## BoQ1
Government eProcurement System Created By: SURESH KUMAR K K Created Date/Time: 12-Dec-2025 12:27 PM Tender Title: Enhancing the illumination level of City Tender ID: 2025_AAI_254589_1
Tender Inviting Authority: Airports Authority of India, Dibrugarh Airport
Name of Work:Enhancing the illumination level of City Side at Dibrugarh Airport..
Contract No: 2025_AAI_ 254589 _1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | D.D.METAL CORPORATION (GSTN-18ACGPD4624F2ZW) BID ID -932872 |  | UNIVERSAL ELECTRICAL AND ELECTRONICS (GSTN-18ABWPD1808N1Z6) BID ID -934350
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of LED Bollard having lumen output not less than 11 Watts with luminaire efficacy of not less than 70 lumens per watt, CCT 3000 K, driver and accessories suitable for outdoor applications complete as per technical specifications. | 60.00 | Each | 1.00 | 3000.00 | 180000.00 | 3360.00 | 201600.00 | 180000.00 | D.D.METAL CORPORATION
2.00 | Supply of LED decorative post top luminaire consisting of a high-pressure powdercoated die-cast aluminium housing suitable for vertical mounting on pole having system lumen output wattage not less than 30 W and system efficacy of not less than 70 lumens per watt, CCT 3000 K, complete with driver and all accessories suitable for outdoor applications complete as per technical specifications. | 15.00 | Each | 1.00 | 7500.00 | 112500.00 | 4440.00 | 66600.00 | 66600.00 | UNIVERSAL ELECTRICAL AND ELECTRONICS
3.00 | ITC of LED Bollard light in ground with required foundation, providing suitable cable entry with HDPE pipe in the foundation, providing end termination of the loop in loop out cable inside the bollard, providing and laying wire if required, interconnections complete as required. | 55.00 | Job | 1.00 | 3900.00 | 214500.00 | 3600.00 | 198000.00 | 198000.00 | UNIVERSAL ELECTRICAL AND ELECTRONICS
4.00 | Supply of 4C x 2.5 Sq.mm XLPE Insulated PVC sheathed Copper Conductor round wire armoured Control Cable of grade 1.1 kV conforming to IS : 7098 with up to date amendents. | 350.00 | Meter | 1.00 | 231.00 | 80850.00 | 228.00 | 79800.00 | 79800.00 | UNIVERSAL ELECTRICAL AND ELECTRONICS
5.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Upto 35 Sq.Mm. | 800.00 | Meter | 1.00 | 60.00 | 48000.00 | 30.00 | 24000.00 | 24000.00 | UNIVERSAL ELECTRICAL AND ELECTRONICS
6.00 | Supplying and laying of following size HDPE pipe ( SDR 11) ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984 complete with fitting and cutting, jointing etc. in the existing trench, complete as required. 25 mm nominal | 300.00 | Meter | 1.00 | 250.00 | 75000.00 | 240.00 | 72000.00 | 72000.00 | UNIVERSAL ELECTRICAL AND ELECTRONICS
7.00 | Excavation of the cable trenches in soft soil not exceeding 30 centimeters in width, and depth upto 50 Centimeters, including getting out the excavated soil and refilling the excavated soil after laying the HDPE pipe in the cable trench, making good the area. | 660.00 | Meter | 1.00 | 200.00 | 132000.00 | 84.00 | 55440.00 | 55440.00 | UNIVERSAL ELECTRICAL AND ELECTRONICS
8.00 | Cutting road/concrete including equipment, labour etc. and disposal of material as directed, within a lead of 50 m. | 5.00 | CUM | 1.00 | 3000.00 | 15000.00 | 4800.00 | 24000.00 | 15000.00 | D.D.METAL CORPORATION
9.00 | Providing and laying in position cement concrete 1:2:4 (1 cement : 2 coarse sand :4 graded stone aggregate 20 mm nominal size) including form work etc. as required. | 5.00 | CUM | 1.00 | 3000.00 | 15000.00 | 8400.00 | 42000.00 | 15000.00 | D.D.METAL CORPORATION
10.00 | Dismantling of Existing 30 Meter High Mast Pole including lights, SS rope, trailing cable from the existing location and shifting the same to a location not more than 100 Meters. The Job includes the lowering of the Mast head Assembly, removing the lights attached to the Mast Head Assembly, removing the foundation bolts, detaching the High Mast Pole from the foundation by providing suitable crane (Crane to be provided by the Agency) without making any damage to the pole and accessories, removing the existing SS rope and trailling cable, Demolishing the RCC structure by mechanical means and the matching it to the ground level complete as required. | 1.00 | Job | 1.00 | 80000.00 | 80000.00 | 72000.00 | 72000.00 | 72000.00 | UNIVERSAL ELECTRICAL AND ELECTRONICS
11.00 | Erection of existing 30 meter High Mast Pole with all accessories by providing reinforced cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation (foundation drawing to be obtained from OEM as per the site conditions and should be approved by AAI) including excavation and refilling including positioning of template & foundation bolts(to be suplied by agency) & providing and fixing of HDPE pipe of size 50 mm dia in the foundation for the cable complete as required and as specified. | 1.00 | Job | 1.00 | 210000.00 | 210000.00 | 108000.00 | 108000.00 | 108000.00 | UNIVERSAL ELECTRICAL AND ELECTRONICS
12.00 | Overhauling, Testing and Commissioning of the existing 30 Meter High Mast Pole by removing the rust, painting the double sided winch, checking the operation of the High Mast head assembly by raising and lower the same, providing grease to the moving parts, making the entire connections for the operation of the High Mast. The Job also includes the fixing of the flood lights, making the connections of the flood light, replacing the cables/wires of the flood light system making good for operation. | 1.00 | Job | 1.00 | 40000.00 | 40000.00 | 48000.00 | 48000.00 | 40000.00 | D.D.METAL CORPORATION
13.00 | Supply and replacement of AISI 316 Grade 6 mm SS steel wire ropes suitable for 30 Meter High Mast Pole installed in Dibrugarh Airport. The job includes the supply and installation of 6 mm rope on the 30 Meter High Mast Pole including replacement of stainless steel thimbles, copper splicing, galvanized turnbuckle eye and bull dog grips including using suitable equipments , tools , safety harness etc. complete as required for replacement of the wire rope complete as required. The job also includes removal of existing wire ropes from the High Mast Pole. The High Mast is equipped with double drum winch and length of the SS steel wire shall compatible for the double drum winch. | 1.00 | Job | 1.00 | 40000.00 | 40000.00 | 36000.00 | 36000.00 | 36000.00 | UNIVERSAL ELECTRICAL AND ELECTRONICS
14.00 | Supply and replacement of EPR Insulated and PCP sheathed trailing cable (8C x 1.5 Sq.mm) suitable for 30 Meter High Mast Pole installed in Dibrugarh Airport. The job including providing and replacing the connectors , the supply and installation of trailing cable on the 30 Meter High Mast Pole including replacement of existing cable using suitable equipments , tools , safety harness etc. complete as required for replacement of the trailing cable complete as required. | 1.00 | Job | 1.00 | 60000.00 | 60000.00 | 18000.00 | 18000.00 | 18000.00 | UNIVERSAL ELECTRICAL AND ELECTRONICS
15.00 | Supply of 4C x 25 Sq.mm XLPE Insulated PVC sheathed Aluminium Conductor armoured Power Cable of grade 1.1 kV conforming to IS : 7098 with up to date amendents. | 100.00 | Meter | 1.00 | 250.00 | 25000.00 | 288.00 | 28800.00 | 25000.00 | D.D.METAL CORPORATION
16.00 | Supply, Installation, Testing and Commissioning of LT Panel, cubicle type, made out of 14 SWG CRCA sheet steel, totally enclosed, IP-54, protection free standing, floor mounting, dust and vermin proof, indoor, compartmentalized, powder coated painting suitable for operation on 3 Phase and neutral, 415V, 50 Hz AC supply system with bus bars extensible on both sides, interconnections with suitable size of copper leads/ solid aluminium strips. INCOMER 1 Nos. 40 Amp, Thermal Magnetic release adjustable type 4 pole Moulded Case Circuit Breaker (Ics = Icu = 25KA) With thermal magnetic release, O/L & S/C Protection with neutral link, 3 Nos.phase indicating LED lamps each with 2 amp back up MCB with each Incomer On & Off Indication lamp with back up Mcb. BUSBARS TPN aluminium bus bars of minimum 100 Amps capacity with heat shrinkable coloured sleeves and i/c, SMC bus bars supports at required intervals complete for cross section, side supports & their spacing etc. for withstanding fault level of 25 KA for 1 sec. OUTGOING 1. Timer Switch along with suitable 3 phase contactor 3 phase MCB for controling lights. 2. Arrangement for raising and lower the High Mast with suitable Amp. rating contactors and raise lower push button, LED indication lamp for ON indication. 3. Spare MCB 4 Pole 10 A. - 2 Sets. | 1.00 | Job | 1.00 | 40000.00 | 40000.00 | 54000.00 | 54000.00 | 40000.00 | D.D.METAL CORPORATION
17.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 6.00 | Job | 1.00 | 7900.00 | 47400.00 | 6000.00 | 36000.00 | 36000.00 | UNIVERSAL ELECTRICAL AND ELECTRONICS
18.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 50.00 | Meter | 1.00 | 540.00 | 27000.00 | 240.00 | 12000.00 | 12000.00 | UNIVERSAL ELECTRICAL AND ELECTRONICS
19.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 360.00 | Meter | 1.00 | 40.00 | 14400.00 | 60.00 | 21600.00 | 14400.00 | D.D.METAL CORPORATION
20.00 | Dismantling of existing pole of height 3 Meter from existing location and shifting to a location not more than 100 meters. The Job includes the removing of bolts, removing the pole by providing suitable arrangement, removing the lights fixed to the pole, demolishing the RCC structure by mechanical means and matching to the ground level, complete as required. | 20.00 | Job | 1.00 | 3000.00 | 60000.00 | 3000.00 | 60000.00 | 60000.00 | D.D.METAL CORPORATION, UNIVERSAL ELECTRICAL AND ELECTRONICS
21.00 | Erection of 3 Mtr.high street light pole with all accessories in reinforced cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation including excavation and refilling including positioning of template & foundation bolts (supplied with pole to match with pole base plate) & providing and fixing of HDPE pipe of size 50 mm dia in the foundation for loop-in-loop-out of the cable to the pole complete as required and as specified | 20.00 | Job | 1.00 | 4000.00 | 80000.00 | 4800.00 | 96000.00 | 80000.00 | D.D.METAL CORPORATION
22.00 | Laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930 complete with fitting and cutting, jointing etc. in the existing trench, complete as required. All pipe size less than 50 mm nominal | 360.00 | Meter | 1.00 | 200.00 | 72000.00 | 120.00 | 43200.00 | 43200.00 | UNIVERSAL ELECTRICAL AND ELECTRONICS
23.00 | ITC of Post top LED light on the Street light Pole of Height 3. meters including making end termination of the loop in loop out cable of size not larger than 4 x 16 sq.mm at syntax box, providing required hole for laying the cable for the light connection, connecting the GI wire for earthing, providing and laying 3 core x 1.5 sq.mm wire for LED light connection, interconnections complete as required for ITC of post top LED light. | 35.00 | Job | 1.00 | 1500.00 | 52500.00 | 960.00 | 33600.00 | 33600.00 | UNIVERSAL ELECTRICAL AND ELECTRONICS
24.00 | Supply and fixing of IP 65 loop in loop out box of inside dimension 155 x 210 x 92 ( equivalent to Hensel make model No.KF 1616 G) including suitable 20 A 4 way DMC connector and din rail etc, including making required interconnections as required. | 35.00 | Job | 1.00 | 1400.00 | 49000.00 | 4200.00 | 147000.00 | 49000.00 | D.D.METAL CORPORATION
| Total in Figures |  |  |  |  | 1770150.00 |  | 1577640.00
Lowest Amount Quoted BY: UNIVERSAL ELECTRICAL AND ELECTRONICS(1577640.00)

## BOQ Summary
BOQ Summary Details Tender Title: Enhancing the illumination level of City Tender ID: 2025_AAI_254589_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | UNIVERSAL ELECTRICAL AND ELECTRONICS (BID ID -934350) | 1577640.00 | L1
| 2 | D.D.METAL CORPORATION (BID ID -932872) | 1770150.00 | L2