## BoQ1
Government eProcurement System Created By: Semreichui Duidang Created Date/Time: 01-Jan-2026 12:04 PM Tender Title: Provision of FDA - Beam Detector, for New Integrated Cargo Terminal Building at Imphal International Airport Tender ID: 2025_AAI_255110_1
Tender Inviting Authority: Sr. Manager (Engg-Elect), AAI, Imphal International Airport.
Name of Work: Provision of FDA (Beam Detector) for New Integrated Cargo Terminal Building at Imphal International Airport.
Contract No: 2025_AAI_255110_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/S TH ROMESH SINGH (GSTN-14BMBPS7319Q2ZF) BID ID -943561 |  | thangtech global infra pvt ltd (GSTN-NA) BID ID -943472
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying, installation, testing & commissioning of addressable beam detector with short circuit isolator inbuilt complete with emitter and receiver including connections with remote test features etc. complete as required. | 10.00 | Each |  | 92400.00 | 924000.00 | 95650.00 | 956500.00 | 924000.00 | M/S TH ROMESH SINGH
2.00 | Supplying, installation, testing & commissioning of following capacity at full load (Unity Power Factor) ONLINE Uninterrupted Power Supply (UPS) system suitable for Single Phase input, Single Phase output AC Supply. The UPS shall include a Rectifier, inverter, battery bank suitable for 30 minutes back up (Battery VAH capacity shall not be less than 1600 VAH per KVA of UPS rating per Hour backup time) on full load (Battery shall be VRLA, SMF in ABS Container) and Static Bypass switch along with provision for manual bypass, suitable isolation transformer for additional protection against neutral faults etc. The UPS systems shall be Microprocessor based Digital Control, using Insulated Gate Bipolar Transistor (IGBT)’s both for the rectifier & inverter with PWM (Pulse Width Modulation) Technology. The quality of design, manufacturing and inspection process should confirm to the relevant Inter-national standards such as IEC/EN/VDE. The operating efficiency of the UPS systems shall be >95% at 100% non-linear loads. Current total harmonic distortion (ITHD)/ total demand distortion (TDD) on the input grid shall be < 5% at 100 %load. (The required LC filters shall be included in UPS cost), extreme power factor kit to be include to limit the input pf to 0.99 and output power factor shall be unity (i.e., kw rating of the UPS shall be KVA rating x 1) however UPS shall be suitable to take load at 0.7 lagging to 0.7 leading power factor loads. UPS shall be suitable for incoming supply AC single phase 160-270V 50 Hz and delivering output AC supply true sine wave single phase 220/230/240 Volt, 50 Hz +/- 0.2Hz, Overload capacity of 120% for 10 mins and 150% for 1 minute.
2.01 | 2 KVA | 1.00 | Each |  | 42000.00 | 42000.00 | 41000.00 | 41000.00 | 41000.00 | thangtech global infra pvt ltd
3.00 | Supply and drawing of 2C x 1.5 Sq.mm FRLS PVC insulated, sheathed copper conductor cable, single core cable in the existing surface /recessed steel/PVC conduit as required. | 90.00 | Mtr |  | 180.00 | 16200.00 | 195.00 | 17550.00 | 16200.00 | M/S TH ROMESH SINGH
4.00 | Supplying and fixing of medium class 20 MM PVC Conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. | 300.00 | Mtr |  | 130.00 | 39000.00 | 165.00 | 49500.00 | 39000.00 | M/S TH ROMESH SINGH
5.00 | Supply and drawing of flexible Twin core 1.5 Sq.mm FRLS PVC insulated, Overall shielded along with PVC outer sheath instrumentation unarmored copper conductor cable, in the existing surface /recessed steel/PVC conduit as required. | 232.00 | Mtr |  | 300.00 | 69600.00 | 350.00 | 81200.00 | 69600.00 | M/S TH ROMESH SINGH
| Total in Figures |  |  |  |  | 1090800.00 |  | 1145750.00
Lowest Amount Quoted BY: M/S TH ROMESH SINGH(1090800.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of FDA - Beam Detector, for New Integrated Cargo Terminal Building at Imphal International Airport Tender ID: 2025_AAI_255110_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/S TH ROMESH SINGH (BID ID -943561) | 1090800.00 | L1
| 2 | thangtech global infra pvt ltd (BID ID -943472) | 1145750.00 | L2