## BoQ1
Government eProcurement System Created By: Sunil Waghmare Created Date/Time: 20-Jan-2026 03:12 PM Tender Title: Provision of LT panel and Miscellaneous works for New Terminal Building and New Office Block at Juhu Airport Mumbai Tender ID: 2025_AAI_255149_1
Tender Inviting Authority: AAI
Name of work: Provision of LT panel and Miscellaneous works for New Terminal Building and New Office Block at Juhu Airport, Mumbai.
Tender ID : 2025_AAI_255149_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO. (GSTN-24AAEFD3355K1ZI) BID ID -945293 |  | Industrial Traders (GSTN-09ACJPC1773F1ZQ) BID ID -945743 |  | SARASWAT ENGINEERING SERVICES (GSTN-27AAZFS6239C1ZO) BID ID -947034 |  | OM POWER SYSTEMS (GSTN-27AADFO2182J1Z5) BID ID -947120 |  | POWER AUTOMATION AND CONTROLS (GSTN-27ABMPA1796L1Z9) BID ID -947256 |  | Virtus Techno (GSTN-NA) BID ID -946694 |  | DAMANI ENTERPRISES (GSTN-NA) BID ID -945861 |  | Kulaswaminee Engineerrs (GSTN-NA) BID ID -936604 |  | Krishsons International Engineers And Consultants (I) Pvt. Ltd (GSTN-NA) BID ID -947255
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.10 | SITC of LT Panel Design,Supply, Installation, Testing and Commissioning of cubicle type LT panel, IP 54 , suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars for high conductivity, SMC bus bar supports, entire panel shall have a common Copper earth bus bar of size as per IS 3043 subject to minimum 50 mm x 6 mm at the rear with 2 Nos. earth stud, solid /flexible connections from main earth bus bar to switchgears with required size of Copper / Aluminium conductors / bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, including provision of SPD's. Surge Protection Devices (SPD’S) shall be provided at main LT Panel incoming feeders (Type 1+2 / Class B+C ) i/c providing following switchgears / accessories as per specifications conforming to IS 8623 / IEC 60439 PTTA type & shall be of Form-3b construction. a) Incomer-1 &2 . 250A FP 36KA MCCB Microprocessor Based Release O/L, S/C & E/F Protection-2 nos, R/Y/B Phase Indication Lamp 230V AC with 6 Amp MCB for controlling-2 sets,R/Y/B Phase Indication Lamp 230V AC with 6 Amp MCB for controlling-2 sets, ON/OFF/TRIP Indication Lamp 230V AC with 6 Amp MCB for controlling-2 set, Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 6 Amp MCB for controlling - 02 set, Spreader Link & Aux. + TAC Contact, Surge Protection Device-1 set, 63A FP 10KA MCB- 1 no.ATS , 1 No. 250 Amps, 4 Pole ATS.3 Nos. Indication Lamps, LED type, for RYB with 6 Amp MCB for controlling, Indication Lamps, LED type for 'ON' , 'OFF' lamps with 6 Amp MCB for controlling -01 Set , Bus Bars, TPN aluminium extensible type main bus bars of minimum 250 Amps. capacity with heat shrinkable coloured sleeves having 100% neutral bus as that of phase i/c SMC bus bar supports at required inetrvals complete for cross section, side supports & their spacing etc for withstanding fault level 36 kA for 1 sec. , Outgoings, 160 Amp ,4 Pole MCCB with 36 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection and terminal spreaders-01 sets Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 6 Amp MCB for controlling - 01 set, Indication Lamps, LED type, R,Y,B Phase indicating lamp with 2 Amp MCB for controlling- 01 Set, Indication Lamps, LED type for MCCB 'ON' , 'OFF' lamps with 2 Amp MCB for controlling -01 Set , All MCCBs shall be provided with Door Interlock with Panel door, 125 Amp ,4 Pole MCCB with 25 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection and terminal spreaders-02 sets | 1.00 | Job |  | 800000.00 | 800000.00 | 835000.00 | 835000.00 | 421356.00 | 421356.00 | 965000.00 | 965000.00 | 1390000.00 | 1390000.00 | 846000.00 | 846000.00 | 990000.00 | 990000.00 | 763688.00 | 763688.00 | 740300.00 | 740300.00 | 421356.00 | SARASWAT ENGINEERING SERVICES
1.20 | Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 6 Amp MCB for controlling - 02 set, Indication Lamps, LED type, R,Y,B Phase indicating lamp with 2 Amp MCB for controlling- 02 Set Indication Lamps, LED type for MCCB 'ON' , 'OFF' lamps with 2 Amp MCB for controlling -02 Set , All MCCBs shall be provided with Door Interlock with Panel door, 100 Amp ,4 Pole MCCB with 25 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection and terminal spreaders-02 sets , Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 6 Amp MCB for controlling - 02 set, Indication Lamps, LED type, R,Y,B Phase indicating lamp with 2 Amp MCB for controlling- 02 Set Indication Lamps, LED type for MCCB 'ON' , 'OFF' lamps with 2 Amp MCB for controlling -02 Set , All MCCBs shall be provided with Door Interlock with Panel door, 63 A 4 pole MCCB with 25 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection and terminal spreader - 2 Sets, Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 6 Amp MCB for controlling - 02 set, Indication Lamps, LED type, R,Y,B Phase indicating lamp with 2 Amp MCB for controlling- 02 Set Indication Lamps, LED type for MCCB 'ON' , 'OFF' lamps with 2 Amp MCB for controlling -02 Set , All MCCBs shall be provided with Door Interlock with Panel door 125 Amp ,Triple Pole MCCB with 25 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection and terminal spreaders-02 sets Indication Lamps, LED type, R,Y,B Phase indicating lamp with 6 Amp MCB for controlling- 01 Set 8 stage APFCR Relay with auxiliary contactor 230 V AC with Add-on block On delay Timer230 V AC Auto manual Selector Switch, 50 KVAr Capacitor bank containing following items: 25 A TP 10 kA MCB-4 sets, Three phase APFC controller 12.5 KVAr Capacitor Duty Contactor 230 V AC with add on block-4 sets, 12.5 KVAr Heavy duty Capacitor bank 440 V AC-4 sets, Indication Lamps, LED type for 'ON' , 'OFF' lamps with 6 Amp MCB for controlling -04 Set Start Push Button (1 NO)-4 Sets, Stop Push Button (2NC)-4 Sets, All MCCBs shall be provided with Door Interlock with Panel door, Note: All incomer breakers shall be electrically and mechaniically interlocked with suitable accessories.
1.30 | Design,Supply, Installation, Testing and Commissioning of cubicle type LT panel, IP 54 , suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars for high conductivity, SMC bus bar supports, entire panel shall have a common Aluminium earth bus bar of size as per IS 3043 subject to minimum 50 mm x 6 mm at the rear with 2 Nos. earth stud, solid /flexible connections from main earth bus bar to switchgears with required size of Cooper / Aluminium conductors / bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, shall be provided a providing following switchgears / accessories as per specifications conforming to IS 8623 / IEC 60439 PTTA type & shall be of Form-3b construction. Incomer 250Amp ,4 Pole MCCB with 36 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protectionand terminal spreaders --- 03 Set Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 2 Amp MCB for controlling - 03 set Indication Lamps, LED type, R,Y,B Phase indicating lamp with 6 Amp MCB for controlling- 03 Set, Indication Lamps, LED type for MCCB 'ON' , 'OFF' lamps with 6 Amp MCB for controlling -03 Set All MCCBs shall be provided with Door Interlock with Panel door ATS , 250 Amps, 4 Pole ATS.-2 nos, 3 Nos. Indication Lamps, LED type, for RYB with 6 Amp MCB for controlling-2 sets, Indication Lamps, LED type for 'ON' , 'OFF' lamps with 6 Amp MCB for controlling -02 Set , Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 6 Amp MCB for controlling - 02 set Bus Bars, TPN aluminium extensible type main bus bars of minimum 250 Amps. capacity with heat shrinkable coloured sleeves having 100% neutral bus as that of phase i/c SMC bus bar supports at required inetrvals complete for cross section, side supports & their spacing etc for withstanding fault level 36 kA for 1 sec. Outgoings, 125 Amp ,4 Pole MCCB with 25 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection and terminal spreaders-01 sets Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 6 Amp MCB for controlling - 01 set Indication Lamps, LED type, R,Y,B Phase indicating lamp with 6 Amp MCB for controlling- 01 Set, Indication Lamps, LED type for MCCB 'ON' , 'OFF' lamps with 6 Amp MCB for controlling -01 Set All MCCBs shall be provided with Door Interlock with Panel door. 100 Amp ,4 Pole MCCB with 25 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection and terminal spreaders-02 sets , Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 6 Amp MCB for controlling - 02 set Indication Lamps, LED type, R,Y,B Phase indicating lamp with 6 Amp MCB for controlling- 02 Set, Indication Lamps, LED type for MCCB 'ON' , 'OFF' lamps with 6 Amp MCB for controlling -02 Set All MCCBs shall be provided with Door Interlock with Panel door, 63 A 4 pole MCCB with 25 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection and terminal spreader - 5 Sets. Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 6 Amp MCB for controlling - 03 set Indication Lamps, LED type, R,Y,B Phase indicating lamp with 6 Amp MCB for controlling- 03 Set, Indication Lamps, LED type for MCCB 'ON' , 'OFF' lamps with 6 Amp MCB for controlling -03 Set , All MCCBs shall be provided with Door Interlock with Panel door | 1.00 | Job |  | 850000.00 | 850000.00 | 890000.00 | 890000.00 | 773448.00 | 773448.00 | 835000.00 | 835000.00 | 1340000.00 | 1340000.00 | 594000.00 | 594000.00 | 1080000.00 | 1080000.00 | 1017258.00 | 1017258.00 | 606750.00 | 606750.00 | 594000.00 | Virtus Techno
1.40 | Design,Supply, Installation, Testing and Commissioning of cubicle type LT panel, IP 54 , suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars for high conductivity, SMC bus bar supports, entire panel shall have a common Aluminium earth bus bar of size as per IS 3043 subject to minimum 50 mm x 6 mm at the rear with 2 Nos. earth stud, solid /flexible connections from main earth bus bar to switchgears with required size of Cooper / Aluminium conductors / bus bars and control wiring with 2.5 sqmm PVC insulated copper conductor cable (FRLS), cable alleys, cable gland plates in two half, shall be provided a providing following switchgears / accessories as per specifications conforming to IS 8623 / IEC 60439 PTTA type & shall be of Form-3b construction. Incomer 1 &2 250Amp ,4 Pole MCCB with 36 kA breaking capacity MCCB with adjustable setting , thermal magnetic release with O/C & S/C protection with addon E/F protection relay and terminal spreaders --- 02 Set Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 6 Amp SP MCB for controlling - 02 set Indication Lamps, LED type, R,Y,B Phase indicating lamp with 6 Amp MCB for controlling- 02 Set Indication Lamps, LED type for MCCB 'ON' , 'OFF' lamps with 6 Amp MCB for controlling -02 Set All MCCBs shall be provided with Door Interlock with Panel door ATS , 250 Amps, 4 Pole ATS.-1 nos 3 Nos. Indication Lamps, LED type, for RYB with 6 Amp MCB for controlling- 1sets Indication Lamps, LED type for 'ON' , 'OFF' lamps with 6 Amp MCB for controlling -01 Set Digital Multi function digital meter to read V,A,kVA, KW, kVAR, PF, Hz etc with LED display with required Nos CTs, control circuit wiring with 6 Amp MCB for controlling - 01 set AMF Feeder, Microprocessor based AMF logic relay 12 V DC-1 no. 20 A battery Charger (24V DC)-1 set, 32A DP 10 KA MCB-1 set DC Voltmeter (0-30V Scale)- 1 no, DC Ammeter (0-20A Scale)-1 no, Hooter 24V DC (96*96mm)-1 no, Hooter Accept Push Button (Black), Reset Push Button (Yellow), Cranking Relay 24V DC-1 no, ON-Delay Timer 230V AC-1 no, 6A Auto/Manual Selector Switch with OFF-1 no, 6A ON/OFF DC Control Selector Switch-1 no, 2 Changeover Auxiliary Relay - 24V DC- 6no, 3 Changeover Auxiliary Relay - 24 DC-1 no, Master trip relay VAJH-13-1set, Digital Reverse Power Relay and Earth fault, Under voltage and over voltage relay-1 set, Alternator voltage monitor relay and main voltage monitor relay-1 set, System ON Indication Lamp 24V DC (Red)-1 no, Low Pressure Indication Lamp 24V DC (Green)-1no, Low Lub Oil Pressure Indication Lamp , 24V DC (Yellow)-1 no, Fail to Start Indication Lamp 24V DC (Yellow)-1 no, Over Speed Indication Lamp 24V DC (Yellow)-1 no, DG Start Push Button (Green)-1 no, DG Stop Push Button (Red)-1 no, Emergency Stop Push Button (Red)-1 no, 6A SP 10KA MCB- 3 no, 12 window Alarm Annunciator-1 set | 2.00 | Job |  | 450000.00 | 900000.00 | 424155.00 | 848310.00 | 409812.00 | 819624.00 | 599900.00 | 1199800.00 | 976000.00 | 1952000.00 | 390000.00 | 780000.00 | 540000.00 | 1080000.00 | 690842.00 | 1381684.00 | 402500.00 | 805000.00 | 780000.00 | Virtus Techno
1.50 | SH-II Supply of Cables
1.60 | Supply of 1.1kV grade, 3.5 Core 400 Sq.mm. XLPE insulated PVC sheathed Aluminium stranded conductor armoured power cable grade conforming to IS-7098 Part-I Part 1 amended upto date etc. complete as required. | 800.00 | Meter |  | 2000.00 | 1600000.00 | 1975.00 | 1580000.00 | 2074.00 | 1659200.00 | 2200.00 | 1760000.00 | 1685.00 | 1348000.00 | 1941.04 | 1552832.00 | 1770.00 | 1416000.00 | 1803.00 | 1442400.00 | 2075.00 | 1660000.00 | 1348000.00 | POWER AUTOMATION AND CONTROLS
1.70 | Supply of 1.1kV grade, 3.5 Core 185 Sq.mm. XLPE insulated PVC sheathed Aluminium stranded conductor armoured power cable grade conforming to IS-7098 Part-I Part 1 amended upto date etc. complete as required. | 250.00 | Meter |  | 1050.00 | 262500.00 | 978.00 | 244500.00 | 1052.00 | 263000.00 | 150.00 | 37500.00 | 845.00 | 211250.00 | 983.34 | 245835.00 | 1170.00 | 292500.00 | 919.00 | 229750.00 | 1080.00 | 270000.00 | 37500.00 | OM POWER SYSTEMS
1.80 | Supply of 1.1kV grade, 3.5 Core 95 Sq.mm. XLPE insulated PVC sheathed Aluminium stranded conductor armoured power cable grade conforming to IS-7098 Part-I Part 1 amended upto date etc. complete as required. | 600.00 | Meter |  | 650.00 | 390000.00 | 525.00 | 315000.00 | 554.00 | 332400.00 | 630.00 | 378000.00 | 435.00 | 261000.00 | 518.40 | 311040.00 | 660.00 | 396000.00 | 488.00 | 292800.00 | 600.00 | 360000.00 | 261000.00 | POWER AUTOMATION AND CONTROLS
1.90 | Supply of 1.1kV grade, 3.5 Core 50 Sq.mm. XLPE insulated PVC sheathed Aluminium stranded conductor armoured power cable grade conforming to IS-7098 Part-I Part 1 amended upto date etc. complete as required. | 800.00 | Meter |  | 450.00 | 360000.00 | 300.00 | 240000.00 | 328.00 | 262400.00 | 350.00 | 280000.00 | 265.00 | 212000.00 | 306.00 | 244800.00 | 390.00 | 312000.00 | 290.00 | 232000.00 | 375.00 | 300000.00 | 212000.00 | POWER AUTOMATION AND CONTROLS
2.00 | Supply of 1.1kV grade, 3.5 Core 35 Sq.mm. XLPE insulated PVC sheathed Aluminium stranded conductor armoured power cable grade conforming to IS-7098 Part-I Part 1 amended upto date etc. complete as required. | 800.00 | Meter |  | 350.00 | 280000.00 | 225.00 | 180000.00 | 242.00 | 193600.00 | 275.00 | 220000.00 | 195.00 | 156000.00 | 226.26 | 181008.00 | 270.00 | 216000.00 | 214.00 | 171200.00 | 295.00 | 236000.00 | 156000.00 | POWER AUTOMATION AND CONTROLS
2.10 | SH-III Supply and Laying of HDPE Pipe
2.20 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc..direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
2.30 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 1400.00 | Meter |  | 200.00 | 280000.00 | 174.00 | 243600.00 | 216.00 | 302400.00 | 75.00 | 105000.00 | 70.00 | 98000.00 | 108.00 | 151200.00 | 180.00 | 252000.00 | 97.00 | 135800.00 | 190.00 | 266000.00 | 98000.00 | POWER AUTOMATION AND CONTROLS
2.40 | 90 mm dia (OD-90 mm & ID-76 mm nominal) | 500.00 | Meter |  | 220.00 | 110000.00 | 220.00 | 110000.00 | 275.00 | 137500.00 | 130.00 | 65000.00 | 130.00 | 65000.00 | 138.00 | 69000.00 | 255.00 | 127500.00 | 122.00 | 61000.00 | 230.00 | 115000.00 | 61000.00 | Kulaswaminee Engineerrs
2.50 | 160mm dia (OD-160 mm & ID-135mm nominal) | 750.00 | Meter |  | 320.00 | 240000.00 | 325.00 | 243750.00 | 419.00 | 314250.00 | 250.00 | 187500.00 | 260.00 | 195000.00 | 240.00 | 180000.00 | 330.00 | 247500.00 | 250.00 | 187500.00 | 375.00 | 281250.00 | 180000.00 | Virtus Techno
2.60 | SH-IV Cable Tray
2.70 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with two numbers G.I. suspenders including base of suitable size GI angle, G.I. bolts & nuts, fastener etc. as required.
2.80 | 375 mm width X 50 mm depth X 2 mm thickness | 150.00 | Meter |  | 1500.00 | 225000.00 | 1519.00 | 227850.00 | 1642.00 | 246300.00 | 500.00 | 75000.00 | 1450.00 | 217500.00 | 1075.20 | 161280.00 | 900.00 | 135000.00 | 1330.00 | 199500.00 | 1900.00 | 285000.00 | 75000.00 | OM POWER SYSTEMS
2.90 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray "bends" (galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with two numbers G.I. suspenders including base of suitable size GI angle, G.I. bolts & nuts, fastener etc. as required.
3.00 | 375 mm width X 50 mm depth X 2 mm thickness | 6.00 | Each |  | 1700.00 | 10200.00 | 2390.00 | 14340.00 | 3593.00 | 21558.00 | 2000.00 | 12000.00 | 2100.00 | 12600.00 | 2390.40 | 14342.40 | 1800.00 | 10800.00 | 578.00 | 3468.00 | 3200.00 | 19200.00 | 3468.00 | Kulaswaminee Engineerrs
3.10 | SH-V Laying of cables:
3.20 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
3.30 | Upto 35 sq. mm (Clamped with 1mm thick saddle) | 100.00 | Meter |  | 80.00 | 8000.00 | 180.00 | 18000.00 | 52.00 | 5200.00 | 20.00 | 2000.00 | 25.00 | 2500.00 | 96.00 | 9600.00 | 45.00 | 4500.00 | 75.00 | 7500.00 | 30.00 | 3000.00 | 2000.00 | OM POWER SYSTEMS
3.40 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 200.00 | Meter |  | 120.00 | 24000.00 | 300.00 | 60000.00 | 87.00 | 17400.00 | 35.00 | 7000.00 | 55.00 | 11000.00 | 96.00 | 19200.00 | 90.00 | 18000.00 | 127.00 | 25400.00 | 90.00 | 18000.00 | 7000.00 | OM POWER SYSTEMS
3.50 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 100.00 | Meter |  | 150.00 | 15000.00 | 360.00 | 36000.00 | 115.00 | 11500.00 | 65.00 | 6500.00 | 75.00 | 7500.00 | 120.00 | 12000.00 | 120.00 | 12000.00 | 173.00 | 17300.00 | 100.00 | 10000.00 | 6500.00 | OM POWER SYSTEMS
3.60 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 30.00 | Meter |  | 200.00 | 6000.00 | 480.00 | 14400.00 | 167.00 | 5010.00 | 98.00 | 2940.00 | 90.00 | 2700.00 | 144.00 | 4320.00 | 180.00 | 5400.00 | 288.00 | 8640.00 | 180.00 | 5400.00 | 2700.00 | POWER AUTOMATION AND CONTROLS
3.70 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
3.80 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 150.00 | Meter |  | 140.00 | 21000.00 | 360.00 | 54000.00 | 115.00 | 17250.00 | 65.00 | 9750.00 | 65.00 | 9750.00 | 120.00 | 18000.00 | 90.00 | 13500.00 | 173.00 | 25950.00 | 105.00 | 15750.00 | 9750.00 | OM POWER SYSTEMS, POWER AUTOMATION AND CONTROLS
3.90 | Above 185 sq. mm and upto 400 sq. mm (clamped with 40x3mm MS flat clamp) | 30.00 | Meter |  | 190.00 | 5700.00 | 420.00 | 12600.00 | 167.00 | 5010.00 | 110.00 | 3300.00 | 80.00 | 2400.00 | 144.00 | 4320.00 | 150.00 | 4500.00 | 288.00 | 8640.00 | 172.00 | 5160.00 | 2400.00 | POWER AUTOMATION AND CONTROLS
4.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC pipe as required.
4.10 | Upto 35 sq. mm | 850.00 | Meter |  | 50.00 | 42500.00 | 96.00 | 81600.00 | 40.00 | 34000.00 | 25.00 | 21250.00 | 18.00 | 15300.00 | 84.00 | 71400.00 | 30.00 | 25500.00 | 63.00 | 53550.00 | 20.00 | 17000.00 | 15300.00 | POWER AUTOMATION AND CONTROLS
4.20 | Above 35 sq. mm and upto 95 sq. mm | 2000.00 | Meter |  | 60.00 | 120000.00 | 120.00 | 240000.00 | 69.00 | 138000.00 | 40.00 | 80000.00 | 22.00 | 44000.00 | 120.00 | 240000.00 | 45.00 | 90000.00 | 92.00 | 184000.00 | 35.00 | 70000.00 | 44000.00 | POWER AUTOMATION AND CONTROLS
4.30 | Above 185 sq. mm and upto 400 sq. mm | 680.00 | Meter |  | 80.00 | 54400.00 | 144.00 | 97920.00 | 139.00 | 94520.00 | 99.00 | 67320.00 | 45.00 | 30600.00 | 120.00 | 81600.00 | 120.00 | 81600.00 | 207.00 | 140760.00 | 70.00 | 47600.00 | 30600.00 | POWER AUTOMATION AND CONTROLS
4.40 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated & PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
4.50 | 3½ X 400 sq. mm (82 mm) | 2.00 | Set |  | 1500.00 | 3000.00 | 3156.00 | 6312.00 | 3077.00 | 6154.00 | 5000.00 | 10000.00 | 1300.00 | 2600.00 | 4754.60 | 9509.20 | 900.00 | 1800.00 | 6485.00 | 12970.00 | 1000.00 | 2000.00 | 1800.00 | DAMANI ENTERPRISES
4.60 | 3½ X 185 sq. mm (57mm) | 8.00 | Set |  | 1200.00 | 9600.00 | 1995.00 | 15960.00 | 1560.00 | 12480.00 | 3500.00 | 28000.00 | 950.00 | 7600.00 | 2820.00 | 22560.00 | 600.00 | 4800.00 | 2792.00 | 22336.00 | 600.00 | 4800.00 | 4800.00 | DAMANI ENTERPRISES, Krishsons International Engineers And Consultants (I) Pvt. Ltd
4.70 | 3½ X 95 sq. mm (45 mm) | 10.00 | Set |  | 800.00 | 8000.00 | 1660.00 | 16600.00 | 798.00 | 7980.00 | 2000.00 | 20000.00 | 500.00 | 5000.00 | 2100.00 | 21000.00 | 450.00 | 4500.00 | 2185.00 | 21850.00 | 400.00 | 4000.00 | 4000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
4.80 | 3½ X 50 sq. mm (35 mm) | 6.00 | Set |  | 700.00 | 4200.00 | 1490.00 | 8940.00 | 611.00 | 3666.00 | 1400.00 | 8400.00 | 475.00 | 2850.00 | 1500.00 | 9000.00 | 360.00 | 2160.00 | 1358.00 | 8148.00 | 300.00 | 1800.00 | 1800.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
4.90 | 3½ X 35 sq. mm (32 mm) | 6.00 | Set |  | 500.00 | 3000.00 | 1440.00 | 8640.00 | 497.00 | 2982.00 | 1000.00 | 6000.00 | 360.00 | 2160.00 | 1380.00 | 8280.00 | 300.00 | 1800.00 | 894.00 | 5364.00 | 250.00 | 1500.00 | 1500.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
5.00 | Construction of inspection chamber along the cable route at various places in brick masonary with bricks of class designation 75 in cement mortar 1:4(1cement : 4fine/coarse sand) of internal size 200 cm (L) x 150 cm width x 120 cm depth, providing and laying in position cement concrete in 1:3:6 (1 cement: 3 coarse sand: 6 graded stone aggregate 20mm nominal size) of 10cm thick on bottom and RCC slab of 20cm thick above the chamber in 1:2:4 (1 cement: 2 coarse sand: 4 gradedstone aggregate 20mm nominal size) with hooks for lifting, plastering all sides of open area in 15mm cement plaster 1:6 (1 cement: 6 fine/coarse sand) including excavation of soil, plastering all sides of open area in 15mm cement plaster 1:6 (1 cement: 6 fine/coarse sand) including excavation of soil complete etc..as reqd. | 4.00 | Job |  | 40000.00 | 160000.00 | 14400.00 | 57600.00 | 55238.00 | 220952.00 | 55000.00 | 220000.00 | 7800.00 | 31200.00 | 6000.00 | 24000.00 | 33000.00 | 132000.00 | 22319.00 | 89276.00 | 17000.00 | 68000.00 | 24000.00 | Virtus Techno
5.10 | Horizontal Drilling of 160 mm bore by mechanical means in horizontal direction in all kinds of soil at least 1 mtr below taxiway surface i/c supply, laying & pushing of 160 mm dia HDPE DWC pipe including all accessories, digging trenches of suitable size on the sides of pavement/runway, making neccessary arrangement for safety of the existing installations and making etc complete as required. | 150.00 | Meter |  | 200.00 | 30000.00 | 1440.00 | 216000.00 | 3175.00 | 476250.00 | 6300.00 | 945000.00 | 800.00 | 120000.00 | 180.00 | 27000.00 | 1800.00 | 270000.00 | 7699.00 | 1154850.00 | 1000.00 | 150000.00 | 27000.00 | Virtus Techno
5.20 | Excavation of the cable trenches in hard rock not exceeding 1.5 meters in width, and lift upto 1.5 meters, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 meters. | 15.00 | cum |  | 500.00 | 7500.00 | 4800.00 | 72000.00 | 1732.00 | 25980.00 | 750.00 | 11250.00 | 850.00 | 12750.00 | 1500.00 | 22500.00 | 1200.00 | 18000.00 | 4025.00 | 60375.00 | 900.00 | 13500.00 | 7500.00 | DOSHI ELECTRIC ENGG. CO.
5.30 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | 15.00 | Job |  | 300.00 | 4500.00 | 2400.00 | 36000.00 | 1294.00 | 19410.00 | 750.00 | 11250.00 | 650.00 | 9750.00 | 1140.00 | 17100.00 | 450.00 | 6750.00 | 3906.00 | 58590.00 | 600.00 | 9000.00 | 4500.00 | DOSHI ELECTRIC ENGG. CO.
5.40 | SH-VI Earthing:
5.50 | Earthing with GI earth pipe 4.5 m long, 40 mm dia including accessories, and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc with charcoal or coke and salt complete as required. | 14.00 | Set |  | 8000.00 | 112000.00 | 12000.00 | 168000.00 | 12194.00 | 170716.00 | 14700.00 | 205800.00 | 3900.00 | 54600.00 | 15000.00 | 210000.00 | 5400.00 | 75600.00 | 21161.00 | 296254.00 | 7500.00 | 105000.00 | 54600.00 | POWER AUTOMATION AND CONTROLS
5.60 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 4.00 | Set |  | 20000.00 | 80000.00 | 24000.00 | 96000.00 | 26636.00 | 106544.00 | 56000.00 | 224000.00 | 14500.00 | 58000.00 | 24000.00 | 96000.00 | 9000.00 | 36000.00 | 48497.00 | 193988.00 | 23000.00 | 92000.00 | 36000.00 | DAMANI ENTERPRISES
5.70 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 25.00 | Meter |  | 2000.00 | 50000.00 | 2160.00 | 54000.00 | 2115.00 | 52875.00 | 2940.00 | 73500.00 | 650.00 | 16250.00 | 1800.00 | 45000.00 | 1200.00 | 30000.00 | 1309.00 | 32725.00 | 2250.00 | 56250.00 | 16250.00 | POWER AUTOMATION AND CONTROLS
5.80 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe From earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 100.00 | Meter |  | 700.00 | 70000.00 | 600.00 | 60000.00 | 746.00 | 74600.00 | 725.00 | 72500.00 | 280.00 | 28000.00 | 228.00 | 22800.00 | 450.00 | 45000.00 | 175.00 | 17500.00 | 400.00 | 40000.00 | 17500.00 | Kulaswaminee Engineerrs
5.90 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 100.00 | Meter |  | 250.00 | 25000.00 | 240.00 | 24000.00 | 185.00 | 18500.00 | 200.00 | 20000.00 | 110.00 | 11000.00 | 228.00 | 22800.00 | 180.00 | 18000.00 | 175.00 | 17500.00 | 192.00 | 19200.00 | 11000.00 | POWER AUTOMATION AND CONTROLS
6.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 25.00 | Meter |  | 1500.00 | 37500.00 | 1680.00 | 42000.00 | 1553.00 | 38825.00 | 1750.00 | 43750.00 | 1055.00 | 26375.00 | 1800.00 | 45000.00 | 1080.00 | 27000.00 | 1309.00 | 32725.00 | 1850.00 | 46250.00 | 26375.00 | POWER AUTOMATION AND CONTROLS
6.10 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 4000.00 | Meter |  | 20.00 | 80000.00 | 34.00 | 136000.00 | 38.00 | 152000.00 | 75.00 | 300000.00 | 20.00 | 80000.00 | 74.40 | 297600.00 | 45.00 | 180000.00 | 34.00 | 136000.00 | 20.00 | 80000.00 | 80000.00 | DOSHI ELECTRIC ENGG. CO., Krishsons International Engineers And Consultants (I) Pvt. Ltd, POWER AUTOMATION AND CONTROLS
6.20 | SH-VII Safety Equipment
6.30 | Providing of set of 4 Nos. 9.5 Litre capacity GI bucket painted in post office red colour with prior coat of red oxide paint and written with white paint ‘FIRE’ and mounted on MS angle iron frame with bracket of appropriate size & capacity i/c filling sand etc. | 2.00 | Set |  | 2000.00 | 4000.00 | 3924.00 | 7848.00 | 5772.00 | 11544.00 | 5500.00 | 11000.00 | 4200.00 | 8400.00 | 5400.00 | 10800.00 | 3600.00 | 7200.00 | 6807.00 | 13614.00 | 850.00 | 1700.00 | 1700.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
6.40 | Supply and fixing of fire retardant electrically insulated synthetic mat of class C 3 mm thick suitable for 11KV AC grade and 240V DC system meeting requirements of IS 15652:2006 tested for breakdown strength, tensile/elongation, aging properties, insulation resistance, effect to acid, alkaline, diesel, transformer oil & leakage current test, fire test etc. having minimum width of 1000 mm ± 20 mm along with all allied materials such as Pu-resin, Chemi bound, special PVC adhesive, liquid primer etc. in what so ever quantity required to complete the job as per site conditions and as per instructions from Engineer-in-Charge. | 50.00 | Sq. Mtr |  | 700.00 | 35000.00 | 1740.00 | 87000.00 | 1386.00 | 69300.00 | 1450.00 | 72500.00 | 1300.00 | 65000.00 | 720.00 | 36000.00 | 2100.00 | 105000.00 | 832.00 | 41600.00 | 900.00 | 45000.00 | 35000.00 | DOSHI ELECTRIC ENGG. CO.
6.50 | Supply & fixing shock treatment chart both in Hindi & English duly mounted on a wooden frame with 3 mm thick glass as reqd. (approximate front area 1.00 sq. meter) | 2.00 | Nos |  | 500.00 | 1000.00 | 1020.00 | 2040.00 | 1154.00 | 2308.00 | 2500.00 | 5000.00 | 450.00 | 900.00 | 2160.00 | 4320.00 | 900.00 | 1800.00 | 2984.00 | 5968.00 | 1800.00 | 3600.00 | 900.00 | POWER AUTOMATION AND CONTROLS
6.60 | Supply and fixing safety instruction chart both in Hindi & English duly framed with 3 mm thick glass as required. (approximate front area 1.00 sq. meter) | 2.00 | Nos |  | 700.00 | 1400.00 | 1020.00 | 2040.00 | 1154.00 | 2308.00 | 2500.00 | 5000.00 | 450.00 | 900.00 | 2160.00 | 4320.00 | 900.00 | 1800.00 | 2984.00 | 5968.00 | 1800.00 | 3600.00 | 900.00 | POWER AUTOMATION AND CONTROLS
6.70 | Supply of First aid box containing material as prescribed by St. John Ambulance brigade (Applicable for medium risk) OR Indian Red Cross conforming to IS 2217-1963 complete as required. | 2.00 | Nos |  | 2000.00 | 4000.00 | 1440.00 | 2880.00 | 1385.00 | 2770.00 | 5500.00 | 11000.00 | 950.00 | 1900.00 | 7560.00 | 15120.00 | 2100.00 | 4200.00 | 7339.00 | 14678.00 | 2000.00 | 4000.00 | 1900.00 | POWER AUTOMATION AND CONTROLS
6.80 | Providing & fixing danger plates made of mild steel at least 2 mm thick & vitreous enamelled white on both sides & with inscriptions in signal red colour on front side as read.
6.90 | Medium Voltage – size 200 mm x 150 mm | 3.00 | Nos |  | 200.00 | 600.00 | 120.00 | 360.00 | 577.00 | 1731.00 | 1000.00 | 3000.00 | 450.00 | 1350.00 | 540.00 | 1620.00 | 600.00 | 1800.00 | 412.00 | 1236.00 | 1000.00 | 3000.00 | 360.00 | Industrial Traders
7.00 | Supplying of Rubber hand gloves suitable for 11KV as per IS Standard. | 10.00 | Pairs |  | 750.00 | 7500.00 | 900.00 | 9000.00 | 1732.00 | 17320.00 | 850.00 | 8500.00 | 625.00 | 6250.00 | 720.00 | 7200.00 | 990.00 | 9900.00 | 2029.00 | 20290.00 | 500.00 | 5000.00 | 5000.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
7.10 | Providing Single Line Diagram on 5mm thick Aluminium sheet in A0 Size duly laminated as per IS Standard. | 2.00 | Nos |  | 2000.00 | 4000.00 | 426.00 | 852.00 | 5772.00 | 11544.00 | 7500.00 | 15000.00 | 4500.00 | 9000.00 | 5400.00 | 10800.00 | 15000.00 | 30000.00 | 6352.00 | 12704.00 | 3500.00 | 7000.00 | 852.00 | Industrial Traders
7.20 | Supply of Resuscitator Bag Reusable Silicone Adult 1600mi with accessories, etc complete as required. | 6.00 | Nos |  | 3000.00 | 18000.00 | 1080.00 | 6480.00 | 947.00 | 5682.00 | 6250.00 | 37500.00 | 1100.00 | 6600.00 | 1800.00 | 10800.00 | 660.00 | 3960.00 | 1654.00 | 9924.00 | 800.00 | 4800.00 | 3960.00 | DAMANI ENTERPRISES
7.30 | SH-VIII LIGHTNING CONDUCTOR
7.40 | Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long G.I. tube, having single prong at top, with 85 mm dia 6 mm thick G.I. base plate including holes etc. complete as required. | 2.00 | Each |  | 2000.00 | 4000.00 | 1200.00 | 2400.00 | 8658.00 | 17316.00 | 2800.00 | 5600.00 | 925.00 | 1850.00 | 5400.00 | 10800.00 | 450.00 | 900.00 | 3734.00 | 7468.00 | 500.00 | 1000.00 | 900.00 | DAMANI ENTERPRISES
7.50 | Jointing copper / G.I. tape (with another copper/ G I tape, base of the finial or anyother metallic object) by riveting / nut bolting/ sweating and soldering etc as required. | 25.00 | Each |  | 200.00 | 5000.00 | 480.00 | 12000.00 | 231.00 | 5775.00 | 280.00 | 7000.00 | 550.00 | 13750.00 | 300.00 | 7500.00 | 90.00 | 2250.00 | 449.00 | 11225.00 | 100.00 | 2500.00 | 2250.00 | DAMANI ENTERPRISES
7.60 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For horizontal run) | 150.00 | Meter |  | 1000.00 | 150000.00 | 168.00 | 25200.00 | 129.00 | 19350.00 | 245.00 | 36750.00 | 115.00 | 17250.00 | 72.00 | 10800.00 | 99.00 | 14850.00 | 90.00 | 13500.00 | 125.00 | 18750.00 | 10800.00 | Virtus Techno
7.70 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor complete as required.(For Vertical run) | 50.00 | Meter |  | 200.00 | 10000.00 | 240.00 | 12000.00 | 198.00 | 9900.00 | 280.00 | 14000.00 | 125.00 | 6250.00 | 72.00 | 3600.00 | 150.00 | 7500.00 | 90.00 | 4500.00 | 200.00 | 10000.00 | 3600.00 | Virtus Techno
7.80 | Providing and fixing testing joint, made of 20 mm X 3 mm thick G.I. strip, 125 mm long, with 4 nos. of G.I. bolts, nuts, chuck nuts and spring washers etc. complete as required. | 2.00 | Each |  | 500.00 | 1000.00 | 600.00 | 1200.00 | 3463.00 | 6926.00 | 490.00 | 980.00 | 145.00 | 290.00 | 300.00 | 600.00 | 90.00 | 180.00 | 90.00 | 180.00 | 115.00 | 230.00 | 180.00 | Kulaswaminee Engineerrs, DAMANI ENTERPRISES
7.90 | Providing and laying G.I. tape 32 mm X 6 mm from earth electrode directly in ground as required. | 50.00 | Meter |  | 400.00 | 20000.00 | 240.00 | 12000.00 | 1021.00 | 51050.00 | 294.00 | 14700.00 | 160.00 | 8000.00 | 164.16 | 8208.00 | 150.00 | 7500.00 | 187.00 | 9350.00 | 185.00 | 9250.00 | 7500.00 | DAMANI ENTERPRISES
8.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 2.00 | Each |  | 10000.00 | 20000.00 | 12000.00 | 24000.00 | 13819.00 | 27638.00 | 13250.00 | 26500.00 | 4000.00 | 8000.00 | 12600.00 | 25200.00 | 6000.00 | 12000.00 | 10028.00 | 20056.00 | 9000.00 | 18000.00 | 8000.00 | POWER AUTOMATION AND CONTROLS
8.10 | SH-IX
8.20 | Revalidation of Greaves make DG Sets of 62.5 Kva capacity from OEM/OEM authorised agency including replacement of Greaves lube oil (10 ltr), Radiator pre mix coolant, lube oil filter, element pre filter, element Air filter, fuel pump calibration, injector calibration, battery, turbo charging repairs including transportation & service charges etc. complete as required. | 2.00 | Job |  | 60000.00 | 120000.00 | 36000.00 | 72000.00 | 70000.00 | 140000.00 | 125000.00 | 250000.00 | 72000.00 | 144000.00 | 84000.00 | 168000.00 | 90000.00 | 180000.00 | 28750.00 | 57500.00 | 11035.00 | 22070.00 | 22070.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
8.30 | SH-X
8.40 | Percentage above or below on the rates of DSR(E&M)2025 (CPWD) items worth totalling 500000- for execution of items on requirement basis(except items mentioned above in this BOQ). The rates quoted shall be without GST. (The payment will be made after deducting GST @18 % from DSR rate). (Rate to be paid = (DSR rate/1.18 x R) ie, if the quoted rate is 1.25 then R = 1.25 and if quoted rate is 0.75, R=0.75 | 1.00 | Nos |  | 1.75 | 1.75 | 600000.00 | 600000.00 | 115440.00 | 115440.00 | 550000.00 | 550000.00 | .90 | .90 | 500000.00 | 500000.00 | 393450.00 | 393450.00 | 90000.00 | 90000.00 | 450000.00 | 450000.00 | .90 | POWER AUTOMATION AND CONTROLS
| Total in Figures |  |  |  |  | 7694101.75 |  | 8484222.00 |  | 7982742.00 |  | 9593340.00 |  | 8351925.90 |  | 7527614.60 |  | 8448000.00 |  | 9090000.00 |  | 7439210.00
Lowest Amount Quoted BY: Krishsons International Engineers And Consultants (I) Pvt. Ltd(7439210.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of LT panel and Miscellaneous works for New Terminal Building and New Office Block at Juhu Airport Mumbai Tender ID: 2025_AAI_255149_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Krishsons International Engineers And Consultants (I) Pvt. Ltd (BID ID -947255) | 7439210.00 | L1
| 2 | Virtus Techno (BID ID -946694) | 7527614.60 | L2
| 3 | DOSHI ELECTRIC ENGG. CO. (BID ID -945293) | 7694101.75 | L3
| 4 | SARASWAT ENGINEERING SERVICES (BID ID -947034) | 7982742.00 | L4
| 5 | POWER AUTOMATION AND CONTROLS (BID ID -947256) | 8351925.90 | L5
| 6 | DAMANI ENTERPRISES (BID ID -945861) | 8448000.00 | L6
| 7 | Industrial Traders (BID ID -945743) | 8484222.00 | L7
| 8 | Kulaswaminee Engineerrs (BID ID -936604) | 9090000.00 | L8
| 9 | OM POWER SYSTEMS (BID ID -947120) | 9593340.00 | L9