## BoQ1
Government eProcurement System Created By: Krishna Kumar Soni Created Date/Time: 22-Dec-2025 03:02 PM Tender Title: Replacement of Cooling Towers of HVAC System at S. V. Airport, Raipur. Tender ID: 2025_AAI_256261_1
Tender Inviting Authority: Asst. Gen. Manager (E-E), Airports Authority of India, S.V. Airport, Raipur
Name of Work: Replacement of Cooling Towers of HVAC system at S. V. Airport, Raipur.
Contract No : 2025_AAI_256261_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SNOWMEX ENGINEERS LIMITED (GSTN-07AAMCS8717P1ZF) BID ID -939609 |  | Virtus Techno (GSTN-NA) BID ID -941428 |  | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD. (GSTN-NA) BID ID -936953
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | H1 Amount | H1 Vendor
1.00 | SH-I: Electrical Works
2.00 | Supply, installation, testing and commissioning of FRP/ GRP (Glass reinforced polystyrene) induced draft based Single cell rectangular shape induced draft counter flow type cooling towers for airconditioning system. Each tower shall be complete with basin, casing distribution system, filling fills, hot deep galvanised (HDG) supportors, GI ladders, motor (IP55 protection) suitable for 415 ± 10% volts, 3 phase power supply, 50 Hz and high efficiency (IE-4) moter, isolators provision at cooling tower enclosed in weather proof panel, Emergency Stop Switch, sump temperature sensors complete as per specification as required. Cooling Towers system shall be selected on the basis of ambient wet bulb 82.94 degree F and actual capacity as follows: Nominal Capacity : 387.8 TR (Heat rejection - 11,61,753 kcal/hr) Water flow rate : 1218 USGPM Water temp. in : 37 °C Water temp. out : 32 °C Note: Selection of Moter shall be as per AAI approval. | 4.00 | Job | 151576.00 | 795000.00 | 3180000.00 | 846000.00 | 3384000.00 | 872025.00 | 3488100.00 | 3488100.00 | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD.
3.00 | Supply, Installation, Testing and Commissioning of Centrifugal Split Casing Pump with bronze and corro coating factory assembled on a common base duly aligned with electric motor (efficiency IE4) for recirculation of water for the central air conditioning system. The pump motor shall be suitable for 415 + 10% volts, 50 Hz, 3 phase power supply including base plate, vibration isolation pad, rubber expanasion bellow, mechanical seals, drain connection remote start stop push buttons etc. complete as required including providing and laying in position cement concrete 1:2:4 (1 Cement : 2 Coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation of pump including form work etc. as required Condenser Water Pump Motor specification as follows : Water flow rate : 1218 USGPM each Head : Minimum 20 Mtr. Pump Efficiency : Minimum 75% Note: Selection of Moter and pumps shall be as per AAI approval. | 4.00 | Job | 78602.00 | 325000.00 | 1300000.00 | 280297.20 | 1121188.80 | 375375.00 | 1501500.00 | 1501500.00 | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD.
4.00 | Supply fixing, testing and commissioning of condenser water pipes of following sizes of MS ‘C’ class along with necessary clamps, vibration isolators and fittings such as bends,tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted/buried in ground excavation and refilling etc. as per specification and as required complete in all respect.
5.00 | 250 mm dia MS pipes ('C' Class) | 18.00 | Mtr. | 212.00 | 5976.00 | 107568.00 | 3180.00 | 57240.00 | 4704.70 | 84684.60 | 107568.00 | SNOWMEX ENGINEERS LIMITED
6.00 | 125 mm dia MS pipes ('C' Class) | 14.00 | Mtr. | 367.00 | 50.00 | 700.00 | 1980.00 | 27720.00 | 2524.67 | 35345.38 | 35345.38 | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD.
7.00 | 100 mm dia MS pipes ('C' Class) | 32.00 | Mtr. | 325.00 | 1428.00 | 45696.00 | 1458.00 | 46656.00 | 1430.90 | 45788.80 | 46656.00 | Virtus Techno
8.00 | 50 mm dia MS pipes ('C' Class) | 15.00 | Mtr. | 261.00 | 980.00 | 14700.00 | 1020.00 | 15300.00 | 754.75 | 11321.25 | 15300.00 | Virtus Techno
9.00 | SITC of Cast Iron BUTTERFLY VALVE (MANUAL) with C I body SS disc nitrile sheet & O - ring & PN 16 pressure rating as specified.
10.00 | 250 mm dia Valves. | 5.00 | Nos. | 1829.00 | 28500.00 | 142500.00 | 17892.00 | 89460.00 | 21469.83 | 107349.15 | 142500.00 | SNOWMEX ENGINEERS LIMITED
11.00 | 125 mm dia Valves. | 2.00 | Nos. | 1307.00 | 50.00 | 100.00 | 3903.60 | 7807.20 | 5781.78 | 11563.56 | 11563.56 | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD.
12.00 | 100 mm dia Valves. | 1.00 | Nos. | 131.00 | 4952.00 | 4952.00 | 3432.00 | 3432.00 | 4466.39 | 4466.39 | 4952.00 | SNOWMEX ENGINEERS LIMITED
13.00 | 50 mm dia Valves. | 1.00 | Nos. | 131.00 | 1580.00 | 1580.00 | 2616.00 | 2616.00 | 2301.92 | 2301.92 | 2616.00 | Virtus Techno
14.00 | BALANCING VALVE WITH BUILT IN MEASURING FACILITY with C I body flanged construction with EPDM coated disc with long pitch with protected out pipe insulation & PN 16 pressure rating for chilled / hot water circulation as specified. 250 mm dia Valves. | 2.00 | Nos. | 131.00 | 75000.00 | 150000.00 | 107310.00 | 214620.00 | 50110.95 | 100221.90 | 214620.00 | Virtus Techno
15.00 | SITC of Y - STRAINER of Ductile CI Body flanged ends with stainless steel strainer for chilled / hot water circulation including insulation as specified. 250 mm dia strainers. | 2.00 | Nos. | 131.00 | 29510.00 | 59020.00 | 32343.60 | 64687.20 | 35236.29 | 70472.58 | 70472.58 | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD.
16.00 | Supply of 3 core X 25 Sq.mm. size of 1.1kv grade multicore aluminium conductor XLPE insulated and PVC sheathed armoured cable as per IS : 7098:1988 with upto date amendments. | 350.00 | Meter | 131.00 | 162.00 | 56700.00 | 191.86 | 67151.00 | 172.21 | 60273.50 | 67151.00 | Virtus Techno
17.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of size Upto 35 sq. mm (clamped with 1mm thick saddle) on wall surface as required. | 350.00 | Meter | 131.00 | 25.00 | 8750.00 | 96.00 | 33600.00 | 115.50 | 40425.00 | 40425.00 | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD.
18.00 | Supplying and making end termination with brass compression gland and aluminum lugs for 3 core, 25 Sq.mm. size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1 KV grade as required. | 8.00 | Sets | 131.00 | 1050.00 | 8400.00 | 720.00 | 5760.00 | 1155.00 | 9240.00 | 9240.00 | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD.
19.00 | Supplying and installing of perforated Hot Dipped Galvanised Iron cable tray "cable tray" of size 150 mm width X 50 mm depth X 1.6 mm thickness with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required. | 100.00 | Meter | 131.00 | 510.00 | 51000.00 | 648.00 | 64800.00 | 669.90 | 66990.00 | 66990.00 | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD.
20.00 | Supplying and installing of perforated Hot Dipped Galvanised Iron cable tray “bends" (galvanisation not less than 50 microns) of 150 mm width X 50 mm depth X 1.6 mm thickness with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required. | 15.00 | Each | 131.00 | 50.00 | 750.00 | 1560.00 | 23400.00 | 606.38 | 9095.70 | 23400.00 | Virtus Techno
21.00 | Supplying and installing of perforated Hot Dipped Galvanised Iron cable tray “Tee” (galvanisation not less than 50 microns) of 150 mm width X 50 mm depth X 1.6 mm thickness size with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required. | 2.00 | Each | 131.00 | 1050.00 | 2100.00 | 2022.00 | 4044.00 | 848.93 | 1697.86 | 4044.00 | Virtus Techno
22.00 | Supplying and installing of perforated Hot Dipped Galvanised Iron cable tray “Cross member” (galvanisation not less than 50 microns) of 150 mm width X 50 mm depth X 1.6 mm thickness with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required. | 2.00 | Each | 131.00 | 1050.00 | 2100.00 | 2880.00 | 5760.00 | 970.20 | 1940.40 | 5760.00 | Virtus Techno
23.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 100.00 | Meter | 131.00 | 55.00 | 5500.00 | 204.00 | 20400.00 | 82.47 | 8247.00 | 20400.00 | Virtus Techno
24.00 | Demolishing HVAC cooling Tower manually/ by mechanical means including stacking of metallic items and disposal of unserviceable material within 50 metres lead as per direction of Engineer - incharge. | 3.00 | Job | 131.00 | 15000.00 | 45000.00 | 24000.00 | 72000.00 | 28875.00 | 86625.00 | 86625.00 | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD.
25.00 | SH-II: Civil Work
26.00 | Centering and shuttering including strutting, propping etc. and removal of form for a) Lintels, beams, plinth beams, girders, bressumers and cantilevers | 190.00 | Sqm | 6969.00 | 800.00 | 152000.00 | 1020.00 | 193800.00 | 597.71 | 113564.90 | 193800.00 | Virtus Techno
27.00 | Centering and shuttering including strutting, propping etc. and removal of form for a) Columns, Pillars, Piers, Abutments, Posts and Struts | 70.00 | Sqm | 3679.00 | 800.00 | 56000.00 | 1020.00 | 71400.00 | 531.30 | 37191.00 | 71400.00 | Virtus Techno
28.00 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete above plinth level. a) Thermo-Mechanically Treated bars (Fe-500D) | 3300.00 | Kg | 4269.00 | 70.00 | 231000.00 | 114.00 | 376200.00 | 106.26 | 350658.00 | 376200.00 | Virtus Techno
29.00 | Providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, Portland Pozzolana /Ordinary Portland /Portland Slag cement, admixtures in recommended proportions as per IS: 9103 to accelerate /retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centering, shuttering, finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete. Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. In case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement. All works above plinth level Upto floor V level. a) Concrete of M25 grade with minimum cement content of 330 kg /cum. | 22.00 | Cum | 6624.00 | 7000.00 | 154000.00 | 7800.00 | 171600.00 | 10626.00 | 233772.00 | 233772.00 | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD.
30.00 | Add for using extra cement in the items of design mix over and above the specified cement content therein. | 5.00 | Quintal | 2408.00 | 1650.00 | 8250.00 | 1800.00 | 9000.00 | 1062.60 | 5313.00 | 9000.00 | Virtus Techno
31.00 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | 240.00 | Kg | 2309.00 | 120.00 | 28800.00 | 114.00 | 27360.00 | 159.39 | 38253.60 | 38253.60 | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD.
32.00 | Drilling suitable holes in reinforced or plain cement concrete with power driven drill machine to a depth as per Drawing/manufacturer's specification in RCC beams, lintels, columns and slabs to introduce steel bars for sunshades/balconies including fixing the steel bars in position using epoxy resin anchor grout of Hilti HIT-HY 200-RV3 Adhesive anchor or equivalent approved make but excluding the cost of reinforcement, all complete as per direction of Engineer-In-Charge. From 12 mm upto and including 25 mm dia | 128.00 | Each | 2001.00 | 210.00 | 26880.00 | 240.00 | 30720.00 | 199.24 | 25502.72 | 30720.00 | Virtus Techno
33.00 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - incharge. | 17.00 | Cum | 9515.00 | 1450.00 | 24650.00 | 1440.00 | 24480.00 | 5977.13 | 101611.21 | 101611.21 | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD.
34.00 | Preparation and submission of structural design/drawing for Base of Cooling Tower along with three copy of drawings, soft copy, hard copy of Design/drawings etc all complete including duly vetting from Govt. Engineering College/NIT/IIT . | 1.00 | Job | 9515.00 | 20000.00 | 20000.00 | 36000.00 | 36000.00 | 69300.00 | 69300.00 | 69300.00 | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD.
| Total in Figures |  |  |  |  | 5888696.00 |  | 6272202.20 |  | 6722816.42
Highest Amount Quoted BY: SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD.(6722816.42)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Cooling Towers of HVAC System at S. V. Airport, Raipur. Tender ID: 2025_AAI_256261_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SHINRYO SUVIDHA ENGINEERS INDIA PVT. LTD. (BID ID -936953) | 6722816.42 | H1
| 2 | Virtus Techno (BID ID -941428) | 6272202.20 | H2
| 3 | SNOWMEX ENGINEERS LIMITED (BID ID -939609) | 5888696.00 | H3