## BoQ1
Government eProcurement System Created By: Bhuwnesh Gupta Created Date/Time: 01-Jan-2026 05:27 PM Tender Title: Construction of Apron at Jammu Airport. SH SITC of Apron Flood Lights and perimeter lights including miscellaneous electrical work at Civil Airport Jammu - Recall Tender ID: 2025_AAI_256312_1
Tender Inviting Authority: Airports Authority of India
Name of Work: Construction of Apron at Jammu Airport. SH: SITC of Apron Flood Lights and perimeter lights including miscellaneous electrical work at Civil Airport, Jammu (Recall).
Contract No: 2025_AAI_256312_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Bajaj Electricals Limited (GSTN-27AAACB2484Q1Z8) BID ID -941128 |  | Instapower Ltd (GSTN-05AAACI9712L1ZG) BID ID -941894 |  | K B CONTRACT (P) LTD (GSTN-07AADCK6091P1ZX) BID ID -942126 |  | ZENITH ASSOCIATES (GSTN-NA) BID ID -941141 |  | Variant Infratech Private Limited (GSTN-NA) BID ID -941589
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I: Provision of Apron Flood Light
2.00 | Design, fabrication & Supply of 25 Mtr height High mast system complete with all accessories, as per the specificaitons. Mast shall be in three sections, hot dip galvanised and suitable for wind velocity as per IS 875 part 3. It shall also include accessories for high mast including head frame, suitable suspension system with steel wire rope 6mm dia (7/19 construction), multicore trailing cable, double drum winch, Galvanised Lantern carriage arrangement suitable for upto 07 luminaries (250 W LED) as per detailed design and lightning finial. The mast shall have an integral electrically operated power tool installed inside the base compartment with raising and lowering mechanism for lantern carraige etc.complete as required as per specifications enclosed. | 9.00 | Each | 525000.00 | 205410.67 | 1848696.03 | 553500.00 | 4981500.00 | 198000.00 | 1782000.00 | 310000.00 | 2790000.00 | 240856.00 | 2167704.00 | 1782000.00 | K B CONTRACT (P) LTD
3.00 | Design, fabrication & Supply of 23 Mtr height High mast system complete with all accessories, as per the specificaitons. Mast shall be in three sections, hot dip galvanised and suitable for wind velocity as per IS 875 part 3. It shall also include accessories for high mast including head frame, suitable suspension system with steel wire rope 6mm dia (7/19 construction), multicore trailing cable, double drum winch, Galvanised Lantern carriage arrangement suitable for upto 07 luminaries (250 W LED) as per detailed design and lightning finial. The mast shall have an integral electrically operated power tool installed inside the base compartment with raising and lowering mechanism for lantern carraige etc.complete as required as per specifications enclosed. | 2.00 | Each | 498000.00 | 211500.00 | 423000.00 | 541200.00 | 1082400.00 | 189000.00 | 378000.00 | 280000.00 | 560000.00 | 233128.00 | 466256.00 | 378000.00 | K B CONTRACT (P) LTD
4.00 | Design, fabrication & Supply of 12 Mtr height High mast system complete with all accessories, as per the specificaitons. Mast shall be in two sections, hot dip galvanised and suitable for wind velocity as per IS 875 part 3. It shall also include accessories for high mast including head frame, suitable suspension system with steel wire rope 6mm dia (7/19 construction), multicore trailing cable, double drum winch, Galvanised Lantern carriage arrangement suitable for upto 07 luminaries (250 W LED) as per detailed design and lightning finial. The mast shall have an integral electrically operated power tool installed inside the base compartment with raising and lowering mechanism for lantern carraige etc.complete as required as per specifications enclosed. | 3.00 | Each | 320000.00 | 143420.33 | 430260.99 | 430500.00 | 1291500.00 | 69300.00 | 207900.00 | 200000.00 | 600000.00 | 128800.00 | 386400.00 | 207900.00 | K B CONTRACT (P) LTD
5.00 | Design and construction of suitable shallow RCC foundation with 1:1.5:3 (1 cement,1.5 coarse sand,3 graded stone aggregate) concrete for the high masts mentioned in item No.1,2 & 3, considering the safe soil bearing capacity at site as 10 T/sq mtr. 2 meters depth, with foundation bolts of suitable size as per approved design and manufactured from special steel alongwith nuts, washers, suitable size anchor plates and templates etc.complete as required.
5.01 | 25 Mtr height in three section | 9.00 | Job | 200000.00 | 66847.33 | 601625.97 | 79950.00 | 719550.00 | 126000.00 | 1134000.00 | 70000.00 | 630000.00 | 150000.00 | 1350000.00 | 601625.97 | Bajaj Electricals Limited
5.02 | 23 Mtr height in three section | 2.00 | Job | 190000.00 | 50048.00 | 100096.00 | 79950.00 | 159900.00 | 126000.00 | 252000.00 | 60000.00 | 120000.00 | 150000.00 | 300000.00 | 100096.00 | Bajaj Electricals Limited
5.03 | 12 Mtr height in two section | 3.00 | Job | 100000.00 | 35189.67 | 105569.01 | 55350.00 | 166050.00 | 60300.00 | 180900.00 | 50000.00 | 150000.00 | 90000.00 | 270000.00 | 105569.01 | Bajaj Electricals Limited
6.00 | Erection, testing and commessioning of following high mast system along with all accessories, flood light fittings, lightning finial and necessary cablings, wirings and junction boxes etc.complete as required on the existing foundation.
6.01 | 25 Mtr height in three section | 9.00 | Job | 78000.00 | 41695.00 | 375255.00 | 32500.00 | 292500.00 | 36000.00 | 324000.00 | 60000.00 | 540000.00 | 23000.00 | 207000.00 | 207000.00 | Variant Infratech Private Limited
6.02 | 23 Mtr height in three section | 2.00 | Job | 70000.00 | 39089.00 | 78178.00 | 32500.00 | 65000.00 | 36000.00 | 72000.00 | 50000.00 | 100000.00 | 23000.00 | 46000.00 | 46000.00 | Variant Infratech Private Limited
6.03 | 12 Mtr height in two section | 3.00 | Job | 30000.00 | 26060.00 | 78180.00 | 19500.00 | 58500.00 | 27000.00 | 81000.00 | 40000.00 | 120000.00 | 17250.00 | 51750.00 | 51750.00 | Variant Infratech Private Limited
7.00 | Supply, installation, testing & commissioning of Nominal 250 W LED luminaries having > 120 Lumen/Watt light output with IP-66 pressure die cast aluminium alloy housing and heat resistant toughened glass cover suitable for High Mast with LED lamp, drivers,connectors, as per design criteria mentioned in technical specifications etc.complete as required. | 84.00 | Job | 11500.00 | 5511.00 | 462924.00 | 8030.00 | 674520.00 | 8100.00 | 680400.00 | 10000.00 | 840000.00 | 6440.00 | 540960.00 | 462924.00 | Bajaj Electricals Limited
8.00 | Supply, installation, testing & commissioning of LED type single dome aviation obstruction light. | 14.00 | Job | 4000.00 | 1798.00 | 25172.00 | 3110.00 | 43540.00 | 10800.00 | 151200.00 | 8000.00 | 112000.00 | 5060.00 | 70840.00 | 25172.00 | Bajaj Electricals Limited
9.00 | Design, Fabrication, Supply, Installation, Testing & Commissioning of floor mounting, totally enclosed , compartmentalized, cubical, vermin proof, outdoor type panel suitable for 415V, 3 phase, 4 wire, 50Hz AC supply system fabricated from CRCA steel sheet of 2mm thick for frame work & 3mm for cable gland plate, entire panel shall have a common GI earth bar of size 25 mm X 5mm at the rear with 2 nos earth stud, finishing complete with power coating in approved shade, bottom base channel of MS section not less than 50mm x 50mm x 5mm thick, solid connections from main bus bar to switch gears with required suitable size of ALu busbars and control wiring with 2.5 sqmm FRLSH PVC insulated copper conductor cable, cable alleys, cable gland plates including providing folling switch gears etc. complete as required. This will include erection of the panel on suiable size MS frame foundation duly grouted in ground with cement and concrete. Complete in all respect as per CPWD specification with following in coming and Outgoings and enclosure protection class IP 65 as required : INCOMER: a) 200A, 4P, 35kA, MCCBs (Ics=100%Icu), with adjustable thermal settings along with incomer bus coupler with extendable ON/OFF rotary handle: 02 nos. b) Bus Coupler 200A, 4P, MCCBs (Ics=100%Icu), 35 kA with extendable ON/OFF rotary handle - 01 No. c) (0-500 V) Digital Voltmeter with selector switch - 2 Set d) (0-200 A) Digital Ammeter with selector switch - 2 Set e) Indication lamp R/Y/B with backup MCB - 2 Set of Three Bus Bar: a) 4-Pole Aluminium Bus bar of 200 A rating of high conductivity with heat shrinkable, coloured sleeves, required intervals complete for cross section, size supports and their spacing etc as per specification. OUTGOING: a) 32A, 4 Pole, 10 kA, C curve, MCBs with all acceessories and internal wiring etc as required: 18 nos. (including spares) (Note : All outgoings should have LED type ON, OFF, trip indicating lamps) | 1.00 | Job | 306800.00 | 220203.00 | 220203.00 | 210500.00 | 210500.00 | 360000.00 | 360000.00 | 350000.00 | 350000.00 | 345550.00 | 345550.00 | 210500.00 | Instapower Ltd
10.00 | Design,manufacturing,supply,installation, testing and commissioning of cubical type totally enclosed free standing, dust free, damp and vermin proof and water proof double door outdoor(IP 65) feeder pillar fabricated out of 2mm thick CRCA sheet duly powder coated and including supply and fixing of the following items and interconnections,wiring with suitable sizes wires/cables and including mounting legs, all civil works like excavation, PCC,brick work pedestal, plastering, refilling etc. and as per specification as required. a) 01 No. 32 Amps, TPN MCCB (Ics=Icu=25 kA) with rotary operating mechanism b) 01 No 32 Amps TP Contactor c) 01 No. Timer (24 hrs) d) 01 No. Auto/mannual selector switch e) 04 Set RYB, ON LED Indication lamp f) 02 Nos 12A (AC 3 rating) Contactor with overload relay for motor g) 02 Nos UP/Down push button h) 02 Nos 16A DP MCB i) 01 No. Digital Voltmeter (0-500 Volts) Class 1 with in built selector switch j) 01 No. Digital Ammeter alongwith suitable range CT's k) Control MCB, Connector strips, Potential free contact for remote operation, Dinbar etc as per requirement. | 14.00 | Job | 76500.00 | 50810.00 | 711340.00 | 13055.00 | 182770.00 | 72000.00 | 1008000.00 | 120000.00 | 1680000.00 | 57500.00 | 805000.00 | 182770.00 | Instapower Ltd
11.00 | Provision of Perimeter Light:
12.00 | Design, Fabrication & Supply of 3 mtrs. high GI OCTAGONAL continuously tapered galvanised street light pole with minimum 500 mm long single arm GI bracket (length and tilt angle of bracket shall be based on design) for installation of LED street light luminaire, suitable for wind velocity as per IS 875 (but not less than 50 m/sec.), fabricated out of 3 mm thick high tensile sheet steel in single piece construction having 130 mm bottom, 70 mm top, suitable for installation on a precast foundation with supply of 4 nos. of foundation bolts & anchor plate, rigid flange plate (200x200x12mm min.) welded with the base of pole for fixing on foundation bolts complete as required for structural stability as specified, weather proof and vandal resistant door flush with the exterior surface containing a terminal plate of 5 mm thick bakelite sheet with 32 Amp heavy duty connector for loop in loop out cable terminations suitable for upto two numbers 4 core 16 Sq.mm cables, including supply of 2A, 10kA, DP, C series, MCB for each fixture connections, earthing bolts for continuous earth connection complete, as required as per technical specifications. | 17.00 | Job | 5500.00 | 5060.00 | 86020.00 | 7380.00 | 125460.00 | 5400.00 | 91800.00 | 6000.00 | 102000.00 | 6698.00 | 113866.00 | 86020.00 | Bajaj Electricals Limited
13.00 | Design, Fabrication & Supply of 3 mtrs. high GI OCTAGONAL continuously tapered galvanised street light pole with minimum 1500 mm long single arm GI bracket (length and tilt angle of bracket shall be based on design) for installation of LED street light luminaire, suitable for wind velocity as per IS 875 (but not less than 50 m/sec.), fabricated out of 3 mm thick high tensile sheet steel in single piece construction having 130 mm bottom, 70 mm top, suitable for installation on a precast foundation with supply of 4 nos. of foundation bolts & anchor plate, rigid flange plate (200x200x12mm min.) welded with the base of pole for fixing on foundation bolts complete as required for structural stability as specified, weather proof and vandal resistant door flush with the exterior surface containing a terminal plate of 5 mm thick bakelite sheet with 32 Amp heavy duty connector for loop in loop out cable terminations suitable for upto two numbers 4 core 16 Sq.mm cables, including supply of 2A, 10kA, DP, C series, MCB for each fixture connections, earthing bolts for continuous earth connection complete, as required as per technical specifications. | 12.00 | Job | 6000.00 | 5500.00 | 66000.00 | 7995.00 | 95940.00 | 6300.00 | 75600.00 | 7000.00 | 84000.00 | 6498.00 | 77976.00 | 66000.00 | Bajaj Electricals Limited
14.00 | Design, Fabrication & Supply of 5 mtrs. high GI OCTAGONAL continuously tapered galvanised street light pole with minimum 1000 mm long single arm GI bracket (length and tilt angle of bracket shall be based on design) for installation of LED street light luminaire, suitable for wind velocity as per IS 875 (but not less than 50 m/sec.), fabricated out of 3 mm thick high tensile sheet steel in single piece construction having 130 mm bottom, 70 mm top, suitable for installation on a precast foundation with supply of 4 nos. of foundation bolts & anchor plate, rigid flange plate (200x200x12mm min.) welded with the base of pole for fixing on foundation bolts complete as required for structural stability as specified, weather proof and vandal resistant door flush with the exterior surface containing a terminal plate of 5 mm thick bakelite sheet with 32 Amp heavy duty connector for loop in loop out cable terminations suitable for upto two numbers 4 core 16 Sq.mm cables, including supply of 2A, 10kA, DP, C series, MCB for each fixture connections, earthing bolts for continuous earth connection complete, as required as per technical specifications. | 36.00 | Job | 7400.00 | 7033.00 | 253188.00 | 9225.00 | 332100.00 | 7200.00 | 259200.00 | 8000.00 | 288000.00 | 8823.00 | 317628.00 | 253188.00 | Bajaj Electricals Limited
15.00 | Design & Supply of GI bracket for installation upto 30 W LED street light luminaire on wall surface with minimum 1000 mm long single arm ( tilt angle of bracket shall be based on design) suitable for wind velocity as per IS 875 (but not less than 50 m/sec.) complete as required. | 20.00 | Each | 2400.00 | 858.00 | 17160.00 | 1107.00 | 22140.00 | 990.00 | 19800.00 | 1500.00 | 30000.00 | 8823.00 | 176460.00 | 17160.00 | Bajaj Electricals Limited
16.00 | Supply of weather proof IP66 thermoplastic cable junction box suitable for termination of 4x16 sqmm armoured cable including one number 6 A, 10 kA, DP MCB, connector kit etc and fixing on existing GI bracket by clamps, bolts, nuts etc complete as required. | 20.00 | Each | 1200.00 | 1173.00 | 23460.00 | 799.50 | 15990.00 | 1350.00 | 27000.00 | 2500.00 | 50000.00 | 1150.00 | 23000.00 | 15990.00 | Instapower Ltd
17.00 | Design and construction of fundation with 1:1.5:3 (1 cement,1.5 coarse sand,3 graded stone aggregate) concrete for the perimeter light pole mentioned in item No.10, 11 & 12 by fixing bolts, nuts, washers, suitable size anchor plates and templates etc.complete as required.
17.01 | Upto 5 Mtr height pole | 65.00 | Job | 7739.00 | 7449.00 | 484185.00 | 5166.00 | 335790.00 | 13500.00 | 877500.00 | 1200.00 | 78000.00 | 5750.00 | 373750.00 | 78000.00 | ZENITH ASSOCIATES
18.00 | Erection, testing and commessioning of following perimeter light pole along with all accessories, LED light fittings and necessary cablings, wirings and junction boxes etc. on the existing foundation and including supplying & drawing of 3core 2.5 sq.mm. FRLSH PVC insulated PVC sheathed flexible copper conductor cable from loop-in-loop-out box upto the individual LED light fitting(s), connection etc. complete as required.
18.01 | 5 Mtr height pole | 36.00 | Job | 2200.00 | 782.00 | 28152.00 | 1300.00 | 46800.00 | 1800.00 | 64800.00 | 600.00 | 21600.00 | 3450.00 | 124200.00 | 21600.00 | ZENITH ASSOCIATES
18.02 | 3 Mtr height pole | 29.00 | Job | 2000.00 | 782.00 | 22678.00 | 1040.00 | 30160.00 | 1350.00 | 39150.00 | 500.00 | 14500.00 | 3450.00 | 100050.00 | 14500.00 | ZENITH ASSOCIATES
19.00 | Erection, testing and commessioning of GI bracket on wall surface with minimum 1000 mm long single arm along with all accessories, LED light fittings and necessary cablings, wirings etc. and including supplying & drawing of 3core 2.5 sq.mm. FRLSH PVC insulated PVC sheathed flexible copper conductor cable from loop-in-loop-out box upto the individual LED light fitting(s), connection etc. complete as required. | 20.00 | Job | 1000.00 | 521.00 | 10420.00 | 845.00 | 16900.00 | 540.00 | 10800.00 | 1000.00 | 20000.00 | 1150.00 | 23000.00 | 10420.00 | Bajaj Electricals Limited
20.00 | Design & Supply of 30 W energy efficient street light LED luminaire with minimum system lumen output of 3300 lm, minimum luman efficacy 110 lm/watt, PF>0.95, CRI>70, CCT from 5700K to 6000K or more, ingress protection should be minimum IP 66, the housing should be of non-corrosive single pice high pressure die-cast aluminium with stand extreme environments. Life of LED not less than of 50K burning hours suitable to operate on 240 V, 50 Hz AC supply with suitable driver complete as required for illumination of perimeter wall as per technical specification. | 55.00 | Each | 1750.00 | 775.00 | 42625.00 | 1107.00 | 60885.00 | 1260.00 | 69300.00 | 1800.00 | 99000.00 | 1095.00 | 60225.00 | 42625.00 | Bajaj Electricals Limited
21.00 | Design & Supply of 25 W energy efficient street light LED luminaire with minimum system lumen output of 2750 lm, minimum luman efficacy 110 lm/watt, PF>0.95, CRI>70, CCT from 5700K to 6000K or more, ingress protection should be minimum IP 66, the housing should be of non-corrosive single pice high pressure die-cast aluminium with stand extreme environments. Life of LED not less than of 50K burning hours suitable to operate on 240 V, 50 Hz AC supply with suitable driver complete as required for illumination of perimeter wall as per technical specification. | 30.00 | Each | 1600.00 | 721.00 | 21630.00 | 799.50 | 23985.00 | 1080.00 | 32400.00 | 1700.00 | 51000.00 | 920.00 | 27600.00 | 21630.00 | Bajaj Electricals Limited
22.00 | Design, Fabrication, Supply, Installation, Testing & Commissioning of outdoor Feeder pillar cubical type, made out of 2.00 mm thick CRCA steel sheet, totally enclosed, IP 65 protection, free standing, floor mounting, powder coated, dust and vermin proof, double door, entire panel shall have a common GI earth bar of size 25 mm X 5mm at the rear with 2 nos earth stud, with proviosion of cable entry from the bottom, all connections from main bus bar to switch gears with required suitable size of ALu busbars and control wiring with 2.5 sqmm FRLSH PVC insulated copper conductor cable, suitable for oeration on 3 phase and neutral, 415 V, 50Hz, AC supply system, including all civil works like excavation, PCC, brick work pedestal, plastering refilling etc. and as per specification as required. INCOMER: a) 63A, 4 Pole, 10 kA, , C curve, MCB : 01 no. b) Indication lamp R/Y/B with backup MCB - 01 Set of Three Bus Bar: a) 4-Pole Aluminium Bus bar of 63 A rating of high conductivity with heat shrinkable, coloured sleeves, required intervals complete for cross section, size supports and their spacing etc as per specification. OUTGOING: a) 40A, 4 Pole, 10 kA, C curve MCBs: 04 nos. (To be control all street light outgoings with programmable digital timer switchs) i) 4 pole surge protection diverter(40kA/pole) - 01 no. ii) Digital Timer Switch with 22 A TP contactor for the automatic switching of luminaries. iii) Interconnection with 2.5 sq.mm copper conductor wire, phase indicating lamps controlled by 03 sets of 2 Amps MCB. (Note : All outgoings should have LED type ON, OFF, trip indicating lamps) | 3.00 | Job | 95000.00 | 77762.00 | 233286.00 | 86450.00 | 259350.00 | 126000.00 | 378000.00 | 150000.00 | 450000.00 | 230000.00 | 690000.00 | 233286.00 | Bajaj Electricals Limited
23.00 | Horizontal Directional Drilling including supply & laying of 50 mm dia (OD-50mm & ID-38 mm nominal) through boring by "No Dig" method using trench-less technology and other associated works along road and under operational area in all type of soil (including soft rock & hard rock) at suitable depth including all civil works and supply of all tested lifting tools and tackling of other required equipments and consumables, labour etc. and making all such necessary arrangements are under agency scope. | 400.00 | Meter | 1200.00 | 1954.00 | 781600.00 | 1105.00 | 442000.00 | 1530.00 | 612000.00 | 1200.00 | 480000.00 | 3450.00 | 1380000.00 | 442000.00 | Instapower Ltd
24.00 | Supply of following sizes of XLPE insulated PVC sheathed, Aluminium conductor armoured electric cable of 1.1 KV grade confirming to IS 7098 PART-I with upto date amended.
24.01 | 4C x 16 Sq.mm | 2500.00 | Meter | 197.00 | 164.00 | 410000.00 | 220.00 | 550000.00 | 144.00 | 360000.00 | 190.00 | 475000.00 | 121.00 | 302500.00 | 302500.00 | Variant Infratech Private Limited
24.02 | 3.5 C x 25 Sq. mm | 4250.00 | Meter | 241.00 | 208.00 | 884000.00 | 276.75 | 1176187.50 | 171.00 | 726750.00 | 220.00 | 935000.00 | 180.00 | 765000.00 | 726750.00 | K B CONTRACT (P) LTD
24.03 | 3.5 C x 300 Sq. mm | 1550.00 | Meter | 1939.00 | 1667.00 | 2583850.00 | 2341.60 | 3629480.00 | 1458.00 | 2259900.00 | 1500.00 | 2325000.00 | 1668.00 | 2585400.00 | 2259900.00 | K B CONTRACT (P) LTD
25.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.
25.01 | 4C x 16 Sq.mm (28mm) | 222.00 | Set | 1939.00 | 208.00 | 46176.00 | 231.05 | 51293.10 | 108.00 | 23976.00 | 650.00 | 144300.00 | 805.00 | 178710.00 | 23976.00 | K B CONTRACT (P) LTD
25.02 | 3.5 C x 25 Sq. mm (28 mm) | 34.00 | Set | 303.00 | 391.00 | 13294.00 | 231.05 | 7855.70 | 225.00 | 7650.00 | 650.00 | 22100.00 | 575.00 | 19550.00 | 7650.00 | K B CONTRACT (P) LTD
25.03 | 3.5 C x 300 Sq. mm (70 mm) | 4.00 | Set | 1135.00 | 3648.00 | 14592.00 | 2043.50 | 8174.00 | 1260.00 | 5040.00 | 1500.00 | 6000.00 | 1725.00 | 6900.00 | 5040.00 | K B CONTRACT (P) LTD
26.00 | Supplying & Installation of following size of performated Hot Dipped Galvainised iron cable tray (Galvainisation thickness not less than 50 micron) with perforation not more than 17.50 %, in convenients sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts etc. as required.
26.01 | 225 mm Width x 50 mm Depth x 1.6 mm Thickness | 200.00 | Meter | 839.00 | 1824.00 | 364800.00 | 565.95 | 113190.00 | 1080.00 | 216000.00 | 800.00 | 160000.00 | 1725.00 | 345000.00 | 113190.00 | Instapower Ltd
27.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. direct in ground (75cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required.
27.01 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 1700.00 | Meter | 246.00 | 133.00 | 226100.00 | 194.15 | 330055.00 | 180.00 | 306000.00 | 250.00 | 425000.00 | 75.00 | 127500.00 | 127500.00 | Variant Infratech Private Limited
27.02 | 90 mm dia (OD-90 mm & ID-76 mm nominal) | 250.00 | Meter | 287.00 | 190.00 | 47500.00 | 244.40 | 61100.00 | 216.00 | 54000.00 | 300.00 | 75000.00 | 230.00 | 57500.00 | 47500.00 | Bajaj Electricals Limited
27.03 | 120 mm dia (OD-120mm & ID-103 mm nominal) | 300.00 | Meter | 358.00 | 262.00 | 78600.00 | 314.85 | 94455.00 | 360.00 | 108000.00 | 350.00 | 105000.00 | 690.00 | 207000.00 | 78600.00 | Bajaj Electricals Limited
28.00 | Laying of one number PVC insulated and PVC Sheathed/ XLPE power cable of 1.1 KV grade of following size direct in ground including excavation and refilling the trench etc. as required but excluding sand cushioning and protective covering.
28.01 | Upto 35 sq. mm | 250.00 | Meter | 384.00 | 46.00 | 11500.00 | 188.00 | 47000.00 | 180.00 | 45000.00 | 90.00 | 22500.00 | 35.00 | 8750.00 | 8750.00 | Variant Infratech Private Limited
28.02 | Above 185 sq. mm and upto 400 sq. mm | 50.00 | Meter | 466.00 | 326.00 | 16300.00 | 188.00 | 9400.00 | 360.00 | 18000.00 | 140.00 | 7000.00 | 58.00 | 2900.00 | 2900.00 | Variant Infratech Private Limited
29.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
29.01 | Upto 35 sq. mm | 5300.00 | Meter | 36.00 | 33.00 | 174900.00 | 45.50 | 241150.00 | 90.00 | 477000.00 | 70.00 | 371000.00 | 35.00 | 185500.00 | 174900.00 | Bajaj Electricals Limited
29.02 | Above 185 sq. mm and upto 400 sq. mm | 1300.00 | Meter | 129.00 | 300.00 | 390000.00 | 117.00 | 152100.00 | 180.00 | 234000.00 | 160.00 | 208000.00 | 93.00 | 120900.00 | 120900.00 | Variant Infratech Private Limited
30.00 | Laying of one number PVC insulated and PVC sheated / XLPE power cable of 1.1 kv Grade of following size on wall surface as required.
30.01 | Upto 35 sq. mm ( clamped with 1mm thick saddle) | 150.00 | Meter | 52.00 | 46.00 | 6900.00 | 104.00 | 15600.00 | 135.00 | 20250.00 | 150.00 | 22500.00 | 35.00 | 5250.00 | 5250.00 | Variant Infratech Private Limited
30.02 | Above 185 sq.mm and upto 400 sq.mm (clamped with 40x3 mm MS flat clamp) | 50.00 | Meter | 215.00 | 365.00 | 18250.00 | 234.00 | 11700.00 | 225.00 | 11250.00 | 300.00 | 15000.00 | 92.00 | 4600.00 | 4600.00 | Variant Infratech Private Limited
31.00 | Laying and fixing of one number PVC insulated and PVC sheated / XLPE power cable of 1.1 kv Grade of following size on cable tray as required.
31.01 | Upto 35 sq. mm ( clamped with 1mm thick saddle) | 100.00 | Meter | 43.00 | 52.00 | 5200.00 | 117.00 | 11700.00 | 135.00 | 13500.00 | 60.00 | 6000.00 | 35.00 | 3500.00 | 3500.00 | Variant Infratech Private Limited
31.02 | Above 185 sq.mm and upto 400 sq.mm (clamped with 40x3 mm MS flat clamp) | 100.00 | Meter | 176.00 | 391.00 | 39100.00 | 234.00 | 23400.00 | 225.00 | 22500.00 | 200.00 | 20000.00 | 92.00 | 9200.00 | 9200.00 | Variant Infratech Private Limited
32.00 | Providing, laying and fixing 100 mm dia G.I pipe (medium class) im ground complete with G.I fittings including trenching (75 cm deep) and re-filling etc complete as required (As per AAI approved make):. | 100.00 | Meter | 1683.00 | 1375.00 | 137500.00 | 1146.50 | 114650.00 | 1620.00 | 162000.00 | 1800.00 | 180000.00 | 1450.00 | 145000.00 | 114650.00 | Instapower Ltd
33.00 | Earthing with G.I pipe 4.5 mm long x 40 mm dia including accessories, and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc. (with charcoal or coke and salt) complete as required. | 34.00 | Each | 6457.00 | 14333.00 | 487322.00 | 5605.00 | 190570.00 | 5400.00 | 183600.00 | 4000.00 | 136000.00 | 3450.00 | 117300.00 | 117300.00 | Variant Infratech Private Limited
34.00 | Earthing with G.I earth plate 600mm x 600mm x 6mm thick including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. (with charcoal or coke and salt) complete as required. | 2.00 | Set | 7033.00 | 18242.00 | 36484.00 | 13705.00 | 27410.00 | 7200.00 | 14400.00 | 6000.00 | 12000.00 | 2300.00 | 4600.00 | 4600.00 | Variant Infratech Private Limited
35.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I wire in 15 mm dia G.I pipe from earth electrode including connection with G.I thimble excavation and refilling as required. | 450.00 | Meter | 269.00 | 279.00 | 125550.00 | 31.10 | 13995.00 | 207.00 | 93150.00 | 380.00 | 171000.00 | 17.00 | 7650.00 | 7650.00 | Variant Infratech Private Limited
36.00 | Providing and fixing of 25 mm x 5 mm GI strip on surface or in recess for connections etc. as required. | 100.00 | Meter | 234.00 | 113.00 | 11300.00 | 70.81 | 7081.00 | 180.00 | 18000.00 | 300.00 | 30000.00 | 138.00 | 13800.00 | 7081.00 | Instapower Ltd
37.00 | Providing and laying 6 SWG dia G.I wire on surface or in recess for loop earthing as required. | 1500.00 | Meter | 68.00 | 22.00 | 33000.00 | 10.62 | 15930.00 | 18.00 | 27000.00 | 60.00 | 90000.00 | 11.00 | 16500.00 | 15930.00 | Instapower Ltd
38.00 | Miscellanous Electrical Works i.e. CISF Morcha etc.
39.00 | Wiring for light point/fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. (Group B) | 60.00 | Point | 1412.00 | 1003.00 | 60180.00 | 1114.00 | 66840.00 | 2160.00 | 129600.00 | 1300.00 | 78000.00 | 1500.00 | 90000.00 | 60180.00 | Bajaj Electricals Limited
40.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit,and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required. (Group B) | 24.00 | Point | 899.00 | 1459.00 | 35016.00 | 1363.50 | 32724.00 | 1440.00 | 34560.00 | 1600.00 | 38400.00 | 1500.00 | 36000.00 | 32724.00 | Instapower Ltd
41.00 | Wiring for circuit/ sub-main wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required. 2x1.5 sq.mm+ 1x 1.5 sq.mm earth wire. | 240.00 | Meter | 311.00 | 104.00 | 24960.00 | 1400.40 | 336096.00 | 342.00 | 82080.00 | 250.00 | 60000.00 | 70.00 | 16800.00 | 16800.00 | Variant Infratech Private Limited
42.00 | Wiring for circuit/ sub-main wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required. 2x2.5 sq.mm+ 1x 2.5 sq.mm earth wire. | 300.00 | Meter | 350.00 | 117.00 | 35100.00 | 1671.00 | 501300.00 | 405.00 | 121500.00 | 250.00 | 75000.00 | 70.00 | 21000.00 | 21000.00 | Variant Infratech Private Limited
43.00 | Wiring for circuit/ sub-main wiring along with earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed Steel conduit as required. 2x4 sq.mm + 1x4 sq.mm earth wire | 90.00 | Meter | 405.00 | 182.00 | 16380.00 | 2286.00 | 205740.00 | 486.00 | 43740.00 | 350.00 | 31500.00 | 120.00 | 10800.00 | 10800.00 | Variant Infratech Private Limited
44.00 | Supply and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 3 pin 5/6 amps modular socket outlet and 5/6 amps modular switch, connection etc. as required. | 10.00 | Each | 454.00 | 208.00 | 2080.00 | 813.50 | 8135.00 | 720.00 | 7200.00 | 500.00 | 5000.00 | 4500.00 | 45000.00 | 2080.00 | Bajaj Electricals Limited
45.00 | Supply and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 16.00 | Each | 555.00 | 208.00 | 3328.00 | 936.50 | 14984.00 | 864.00 | 13824.00 | 700.00 | 11200.00 | 4500.00 | 72000.00 | 3328.00 | Bajaj Electricals Limited
46.00 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
46.01 | 12 Way Double Door | 6.00 | Each | 2166.00 | 4951.00 | 29706.00 | 1801.00 | 10806.00 | 4050.00 | 24300.00 | 5000.00 | 30000.00 | 7000.00 | 42000.00 | 10806.00 | Instapower Ltd
47.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
47.01 | Single Pole | 60.00 | Each | 243.00 | 146.00 | 8760.00 | 167.10 | 10026.00 | 360.00 | 21600.00 | 250.00 | 15000.00 | 100.00 | 6000.00 | 6000.00 | Variant Infratech Private Limited
48.00 | Supplying and fixing following rating, double pole, (single phase and neutral), 240 V, residual current circuit breaker (RCCB), having a sensitivity current 300 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required.
48.01 | 40 Amp | 6.00 | Each | 2997.00 | 2408.00 | 14448.00 | 247.40 | 1484.40 | 3330.00 | 19980.00 | 6000.00 | 36000.00 | 6500.00 | 39000.00 | 1484.40 | Instapower Ltd
49.00 | Supplying and fixing following rating, double pole, 240 V, MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required.
49.01 | 40 Amp | 6.00 | Each | 1224.00 | 756.00 | 4536.00 | 1244.00 | 7464.00 | 1008.00 | 6048.00 | 900.00 | 5400.00 | 250.00 | 1500.00 | 1500.00 | Variant Infratech Private Limited
50.00 | Supply of 20 Watt LED Surface type fitting CCT 6500K suitable to operate 240 Volt 50 HZ Supply, minimum length 120 cm with all standard accessories for proper installation etc complete as required as per Technical specification. | 48.00 | Each | 687.00 | 521.00 | 25008.00 | 461.25 | 22140.00 | 360.00 | 17280.00 | 2700.00 | 129600.00 | 650.00 | 31200.00 | 17280.00 | K B CONTRACT (P) LTD
51.00 | Supply of 10 Watt LED Bulk Head light with IP-66 rating , CCT 5700K or more suitable to operate 240 Volt 50 HZ Supply complete with all standard accessories for installation etc complete as required as per technical specification. | 24.00 | Each | 941.00 | 651.00 | 15624.00 | 1045.50 | 25092.00 | 900.00 | 21600.00 | 500.00 | 12000.00 | 650.00 | 15600.00 | 12000.00 | ZENITH ASSOCIATES
52.00 | Supply of following sizes of celing fan, with double ball bearing, Aluminium pressure die cast body with Aluminium blades, canopies hanging shackle, 30 cm down rod and without speed regulator suitable for 240 V 50 HZ, AC supply Complete as required as per site requirement. 1200 mm sweep. | 12.00 | Each | 2066.00 | 1824.00 | 21888.00 | 1845.00 | 22140.00 | 3600.00 | 43200.00 | 3600.00 | 43200.00 | 3000.00 | 36000.00 | 21888.00 | Bajaj Electricals Limited
53.00 | Supply and fixing stepped type electronic Fan Regulator on the existing modular plate and switch box including connections but excluding modular plate etc. as required. | 12.00 | Each | 334.00 | 339.00 | 4068.00 | 302.75 | 3633.00 | 540.00 | 6480.00 | 500.00 | 6000.00 | 150.00 | 1800.00 | 1800.00 | Variant Infratech Private Limited
54.00 | Supply of following sizes of exhaust fan suitable for single phase 240 volt, 50 HZ AC supply complete with motor, capacitor, louvers/ shutters and all accessories complete as required . 300 mm, Sweep | 6.00 | Each | 2253.00 | 1498.00 | 8988.00 | 2214.00 | 13284.00 | 2700.00 | 16200.00 | 2300.00 | 13800.00 | 1500.00 | 9000.00 | 8988.00 | Bajaj Electricals Limited
55.00 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of standard lenght (upto 30 cm) with 1.5 sq.mm FRLS PVC insulated, copper conductor, single core cable etc. as required. | 12.00 | Each | 210.00 | 365.00 | 4380.00 | 650.00 | 7800.00 | 360.00 | 4320.00 | 150.00 | 1800.00 | 500.00 | 6000.00 | 1800.00 | ZENITH ASSOCIATES
56.00 | Installation, testing and commissioning of pre-wired, fluorescent fitting/ compact fluorescent fitting/LED fitting luminaries etc. of all types (surface/Recessed), complete with all accessories and tube etc. Directly on ceiling/ wall , including connection with 1.5 sq.mm FRLS PVC insulated, stranded, copper conductor single core cable with flexibleconduits and coupler and earthin etc. as required. | 72.00 | Each | 204.00 | 391.00 | 28152.00 | 130.00 | 9360.00 | 360.00 | 25920.00 | 200.00 | 14400.00 | 300.00 | 21600.00 | 9360.00 | Instapower Ltd
57.00 | Inatallation of exhaust fan in the existing opening including fixing of louvers/shutter etc. and making good the damage, connections, testing and commissioning etc. as required. | 6.00 | Each | 251.00 | 391.00 | 2346.00 | 650.00 | 3900.00 | 360.00 | 2160.00 | 100.00 | 600.00 | 200.00 | 1200.00 | 600.00 | ZENITH ASSOCIATES
58.00 | SITC of Busbar chamber on Wall with suitable Fastner,Having rating of 415 Volt 50Hz AC Supply,63 Amp,Four Pole,complete as required as per site requirement. | 6.00 | Job | 6110.00 | 4170.00 | 25020.00 | 12180.00 | 73080.00 | 6300.00 | 37800.00 | 10000.00 | 60000.00 | 1000.00 | 6000.00 | 6000.00 | Variant Infratech Private Limited
59.00 | SITC of Single phase energy Meter on Wall with suitable Fastner, LCD display, Having rating of 240 Volt 50Hz AC Supply 10-60 Amp ,Accuracy class 1.0, with pilfer proof meter box complete as required as per site requirement. | 6.00 | Job | 2100.00 | 2345.00 | 14070.00 | 2720.00 | 16320.00 | 4500.00 | 27000.00 | 5000.00 | 30000.00 | 1500.00 | 9000.00 | 9000.00 | Variant Infratech Private Limited
60.00 | Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/ wooden block including connection etc as required | 18.00 | Job | 84.00 | 42.00 | 756.00 | 437.25 | 7870.50 | 63.00 | 1134.00 | 200.00 | 3600.00 | 1000.00 | 18000.00 | 756.00 | Bajaj Electricals Limited
| Total in Figures |  |  |  |  | 14077916.00 |  | 20039425.20 |  | 15283242.00 |  | 17024000.00 |  | 16271225.00
Lowest Amount Quoted BY: Bajaj Electricals Limited(14077916.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of Apron at Jammu Airport. SH SITC of Apron Flood Lights and perimeter lights including miscellaneous electrical work at Civil Airport Jammu - Recall Tender ID: 2025_AAI_256312_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Bajaj Electricals Limited (BID ID -941128) | 14077916.00 | L1
| 2 | K B CONTRACT (P) LTD (BID ID -942126) | 15283242.00 | L2
| 3 | Variant Infratech Private Limited (BID ID -941589) | 16271225.00 | L3
| 4 | ZENITH ASSOCIATES (BID ID -941141) | 17024000.00 | L4
| 5 | Instapower Ltd (BID ID -941894) | 20039425.20 | L5