## BoQ1
Government eProcurement System Created By: KUMAR RIJENDRA Created Date/Time: 22-Dec-2025 12:58 PM Tender Title: Provision of High Mast and associated electrical work for newly built GSE (Ground Support Equipment) area at B M Airport Ranchi. Tender ID: 2025_AAI_256397_1
Tender Inviting Authority: SM (E-E), AAI, B.M.Airport, Ranchi
Name of Work: Provision of High Mast & associated electrical work for newly built GSE (Ground Support Equipment) area at B M Airport Ranchi.
Contract No: 2025_AAI_256397_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/S AMAR ENTERPRISES (GSTN-20AAMFA2722R1ZE) BID ID -940563 |  | BR Power Control and Automation Services (GSTN-06AREPS4024K1ZP) BID ID -941484 |  | ANU ENGINEERING CORPORATION (GSTN-07AJDPK9181G1Z1) BID ID -941881 |  | SHREE GOURI ELECTRIC ENTERPRISE (GSTN-19ADDPB4683J1ZE) BID ID -941900 |  | VL SERVICES (GSTN-NA) BID ID -935389 |  | waystone engicon private limited (GSTN-NA) BID ID -941929 |  | R1 RADIANCE LIGHTS PRIVATE LIMITED (GSTN-NA) BID ID -941481 |  | M/s G.D. Enterprises (GSTN-NA) BID ID -940378
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design Supply, Fabrication, Installation, Testing and Commissioning of 18 metre height hot dip galvanized high mast shaft in two or three sectioned, hot dip galvanized, suitable for wind velocity as per IS 875 part-3 along with its all accessories : viz head frame, suitable SS wire rope, double or triple drum winch, Galvanized lantern carriage arrangement to install minimum 12 Nos. flood Light luminaries symmetrical arrangement with required cable connection from panel to mast top & fitting cable connection with counter weight (12 Nos.1x200W LED Flood Light luminaries), lightning finial, integral power tool motor installed inside the base compartment for its operation, trailing cable with suitable size, connector, manual handle, junction box, foundation bolts along with nuts, washers, anchor plates and templates etc. as required for a minimum average lux level of 20 lux as per ICAO standards. | 3.00 | Job | 313013.00 | 230000.00 | 690000.00 | 148000.00 | 444000.00 | 185000.00 | 555000.00 | 180000.00 | 540000.00 | 265000.00 | 795000.00 | 230000.00 | 690000.00 | 209002.65 | 627007.95 | 275000.00 | 825000.00 | 444000.00 | BR Power Control and Automation Services
2.00 | Design and casting of suitable shallow foundation with M-20 concrete for the high mast mentioned in item no.-1 considering the safe soil bearing capacity at site as 10T/Sq.Mtr at min. 2 metres depth and as per soil bearing capacity, works also included hard/soft soil excavation & disposal for foundation including erection, testing and commissioning of 18 mtrs high mast system etc. as required and as per specification mentioned in TS & as per direction of EIC. ( Foundation design shall be vetted by the NIT/IITor any Government institution). | 3.00 | Job | 156550.00 | 50000.00 | 150000.00 | 136800.00 | 410400.00 | 80000.00 | 240000.00 | 25000.00 | 75000.00 | 95000.00 | 285000.00 | 60000.00 | 180000.00 | 73433.36 | 220300.08 | 80000.00 | 240000.00 | 75000.00 | SHREE GOURI ELECTRIC ENTERPRISE
3.00 | Supply,Installation,Testing and Commissioning of following type LED Flood light luminaire which should have system efficacy not less than 110 lm/W, toughened glass, secondary lens optic should have should have Narrow beam & SW beam with individual optic lens, IP66 protection, IK08 should have system surge protection upto 20 KV,single piece integral high pressure dicast aluminium housing, complete with electronic power driver, all its accessories,colour temperature should not more than 5700K , suitable to works on 230V+ 10% ,50 Hz AC power suppl etc complete as required following flood light fixtures on the lantern carrier of high mast etc. as required. 200 W LED Flood light | 42.00 | Each | 4546.00 | 3800.00 | 159600.00 | 6967.00 | 292614.00 | 5600.00 | 235200.00 | 5350.00 | 224700.00 | 8500.00 | 357000.00 | 5800.00 | 243600.00 | 3558.69 | 149464.98 | 6000.00 | 252000.00 | 149464.98 | R1 RADIANCE LIGHTS PRIVATE LIMITED
4.00 | Supply,Installation,Testing and Commissioning of LED Type low intensity aviation obstruction light suitable for 220 V , 50 HZ AC supply and as per ICAO standard etc. complete as required. As per list of approved make or equivalent. | 3.00 | Each | 6242.00 | 4000.00 | 12000.00 | 6258.00 | 18774.00 | 6000.00 | 18000.00 | 5000.00 | 15000.00 | 4500.00 | 13500.00 | 4500.00 | 13500.00 | 282.44 | 847.32 | 5000.00 | 15000.00 | 847.32 | R1 RADIANCE LIGHTS PRIVATE LIMITED
5.00 | Design,Supply,Installation,Testing and Commissioning of outdoor type distribution feeder pillar box with 40 A TPN MCB as incommer,totally enclosed,free standing, vermin dust proof,Water proof,front operated, double door made of 2 mm thick ,rubber gasket,powder coating painting with provision for incoming cable connection 35 Sqmm and out going 16 & 2.5 Sqmm terminals for the power tool motor etc. complete as required provisions for earthing, support for switchgears & busbars with suitable angle iron frame base, floor mounting, Al. bus bar,suitable for operation on 3 Phase and 4 wire, 415V, 50 Hz AC supply system including control wiring, necessary connections etc and supply & mountings of following items. (a) 32 A TPN MCB with breaking Capacity of 10 KA -02 No. (b )Suitable TPN Bus bars of Aluminum alloy-1 Set (c )Power Contactor(32A,3P,3Ph,415V,50 Hz) with necessary timer,relay,MCB as required for automatic switching of luminaries,-1 Set. (d )Power Contactor(9A,2P,1Ph,230 V,50Hz) with necessary timer,relay,MCB as required for automatic switching of aviation light, -1Set. (e)RYB Indicating Lamp ( LED Type) - 1 set (f) Rotary switch for auto & manual syastem-1 set (g) Push Button for motor opeartion-1 Set (h) Ammeter with selector switch and suitable C/T etc. -01 set (i) Voltmeter with selector switch - 01 set (j) 16 &2.5 Sqmm terminals/connectors for out going etc - 01 set | 3.00 | Job | 28712.00 | 28000.00 | 84000.00 | 97000.00 | 291000.00 | 48000.00 | 144000.00 | 71000.00 | 213000.00 | 32500.00 | 97500.00 | 28000.00 | 84000.00 | 79082.08 | 237246.24 | 35000.00 | 105000.00 | 84000.00 | M/S AMAR ENTERPRISES, waystone engicon private limited
6.00 | Supply of following sizes XLPE insulated & PVC sheathed,1.1 KV grade, Al conductor, armoured power cable confirming to IS: 7098, Part-1/1988 with upto date amendments. 3.5 x 35 Sq.mm. Aluminium conductor | 495.00 | Meter | 254.00 | 190.00 | 94050.00 | 235.00 | 116325.00 | 270.00 | 133650.00 | 500.00 | 247500.00 | 325.00 | 160875.00 | 240.00 | 118800.00 | 220.30 | 109048.50 | 500.00 | 247500.00 | 94050.00 | M/S AMAR ENTERPRISES
7.00 | Laying of one number PVC insulated and PVC sheathed/XLPE power cable/RC Cable 1.1KV grade of upto size 35 Sq.mm. in the existing RCC/HUME/STONE WARE/Metal /HDPE pipe as reqd. | 495.00 | Meter | 34.00 | 10.00 | 4950.00 | 80.00 | 39600.00 | 20.00 | 9900.00 | 15.00 | 7425.00 | 65.00 | 32175.00 | 25.00 | 12375.00 | 203.35 | 100658.25 | 40.00 | 19800.00 | 4950.00 | M/S AMAR ENTERPRISES
8.00 | Supplying and making end termination with brass compression gland and aluminium/copper lugs for following size of PVC insuated and PVC sheathed/XLPE power cable of 1.1KV grade as reqd. 3.5 x 35 Sq.mm. Al Cable | 6.00 | Each | 413.00 | 400.00 | 2400.00 | 1340.00 | 8040.00 | 200.00 | 1200.00 | 300.00 | 1800.00 | 650.00 | 3900.00 | 250.00 | 1500.00 | 1581.64 | 9489.84 | 410.00 | 2460.00 | 1200.00 | ANU ENGINEERING CORPORATION
9.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 3.00 | Set | 6663.00 | 4000.00 | 12000.00 | 11270.00 | 33810.00 | 7000.00 | 21000.00 | 7000.00 | 21000.00 | 22500.00 | 67500.00 | 6000.00 | 18000.00 | 90379.52 | 271138.56 | 7000.00 | 21000.00 | 12000.00 | M/S AMAR ENTERPRISES
10.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I.pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required | 9.00 | Meter | 622.00 | 300.00 | 2700.00 | 515.00 | 4635.00 | 750.00 | 6750.00 | 100.00 | 900.00 | 265.00 | 2385.00 | 100.00 | 900.00 | 5083.65 | 45752.85 | 650.00 | 5850.00 | 900.00 | SHREE GOURI ELECTRIC ENTERPRISE, waystone engicon private limited
11.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 9.00 | Meter | 130.00 | 100.00 | 900.00 | 273.00 | 2457.00 | 250.00 | 2250.00 | 100.00 | 900.00 | 265.00 | 2385.00 | 100.00 | 900.00 | 3558.69 | 32028.21 | 650.00 | 5850.00 | 900.00 | M/S AMAR ENTERPRISES, SHREE GOURI ELECTRIC ENTERPRISE, waystone engicon private limited
12.00 | Supplying and fixing of 25 mm X 5 mm G.I strip on surface/reccese etc as required. | 30.00 | Meter | 237.00 | 150.00 | 4500.00 | 233.00 | 6990.00 | 250.00 | 7500.00 | 100.00 | 3000.00 | 265.00 | 7950.00 | 100.00 | 3000.00 | 282.44 | 8473.20 | 250.00 | 7500.00 | 3000.00 | SHREE GOURI ELECTRIC ENTERPRISE, waystone engicon private limited
13.00 | Supply of 50 mm dia ISI marked HDPE pipe as per IS 4984:2016 of PE 80 grade and PN 6 rating complete etc. as required. | 480.00 | Meter | 71.00 | 70.00 | 33600.00 | 124.00 | 59520.00 | 135.00 | 64800.00 | 100.00 | 48000.00 | 225.00 | 108000.00 | 80.00 | 38400.00 | 50.84 | 24403.20 | 150.00 | 72000.00 | 24403.20 | R1 RADIANCE LIGHTS PRIVATE LIMITED
14.00 | Providing the HDD upto a depth of approx 2 mtr. Suitable for laying of 50 mm dia HDPE pipe etc. as required. | 480.00 | Meter | 404.00 | 165.00 | 79200.00 | 410.00 | 196800.00 | 650.00 | 312000.00 | 100.00 | 48000.00 | 625.00 | 300000.00 | 250.00 | 120000.00 | 305.03 | 146414.40 | 1250.00 | 600000.00 | 48000.00 | SHREE GOURI ELECTRIC ENTERPRISE
15.00 | Supply of Squar LED illuminated SNI/WGS(Stand number indicator/way guidance signange) sign as per ICAO Annex. 14 Vol.1/CAR DGCA (legends approved by EIC) made out of 2mm thick Aluminium frame with suitable angle support with 2mm thick aluminium backcover and 4mm thick UV stabilized polycarbonate sheet with glare free face with required colouring suitable arrangement for IP 65 protection. Signboard is internally illuminated with required numbers of LED strips/Modules & drivers to achieve required illumination lavel operated on input source 220 VAC, 50HZ supply with mounting clamp suitable to mount on pole. As per CAR/DGCA requirement and guidelines. Size: 1235 x 1500 mm - qty 09 nos. (For Bay no. 01 to 09) | 16.65 | Sq.Meter | 33330.00 | 22000.00 | 366300.00 | 10073.00 | 167715.45 | 42000.00 | 699300.00 | 9000.00 | 149850.00 | 12500.00 | 208125.00 | 3300.00 | 54945.00 | 3248.01 | 54079.37 | 2100.00 | 34965.00 | 34965.00 | M/s G.D. Enterprises
16.00 | ITC of Squar LED illuminated SNI/WGS(Stand number indicator/way guidance signange) sign as per ICAO Annex. 14 Vol.1/CAR DGCA (legends approved by EIC) made out of 2mm thick Aluminium frame with suitable angle support with 2mm thick aluminium backcover and 4mm thick UV stabilized polycarbonate sheet with glare free face with required colouring suitable arrangement for IP 65 protection. Signboard is internally illuminated with required numbers of LED strips/Modules & drivers to achieve required illumination lavel operated on input source 220 VAC, 50HZ supply with mounting clamp suitable to mount on pole. As per CAR/DGCA requirement and guidelines. Size: 1235 x 1500 mm - qty 09 nos. (For Bay no. 01 to 09) | 9.00 | Job | 4040.00 | 4000.00 | 36000.00 | 1596.00 | 14364.00 | 2000.00 | 18000.00 | 3000.00 | 27000.00 | 12500.00 | 112500.00 | 1000.00 | 9000.00 | 1242.72 | 11184.48 | 5000.00 | 45000.00 | 9000.00 | waystone engicon private limited
17.00 | Dismantling, Shifting & re-installation of existing pole( upto 6 mtr height) i/c providing tin plate 6mm for supporting of bottom to the existing pole making necessary excavation & required civil works etc as required. | 4.00 | Job | 5252.00 | 4725.00 | 18900.00 | 8200.00 | 32800.00 | 4000.00 | 16000.00 | 15000.00 | 60000.00 | 6500.00 | 26000.00 | 2000.00 | 8000.00 | 12427.18 | 49708.72 | 2000.00 | 8000.00 | 8000.00 | M/s G.D. Enterprises, waystone engicon private limited
| Total in Figures |  |  |  |  | 1751100.00 |  | 2139844.45 |  | 2484550.00 |  | 1683075.00 |  | 2579795.00 |  | 1596920.00 |  | 2097246.15 |  | 2506925.00
Lowest Amount Quoted BY: waystone engicon private limited(1596920.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of High Mast and associated electrical work for newly built GSE (Ground Support Equipment) area at B M Airport Ranchi. Tender ID: 2025_AAI_256397_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | waystone engicon private limited (BID ID -941929) | 1596920.00 | L1
| 2 | SHREE GOURI ELECTRIC ENTERPRISE (BID ID -941900) | 1683075.00 | L2
| 3 | M/S AMAR ENTERPRISES (BID ID -940563) | 1751100.00 | L3
| 4 | R1 RADIANCE LIGHTS PRIVATE LIMITED (BID ID -941481) | 2097246.15 | L4
| 5 | BR Power Control and Automation Services (BID ID -941484) | 2139844.45 | L5
| 6 | ANU ENGINEERING CORPORATION (BID ID -941881) | 2484550.00 | L6
| 7 | M/s G.D. Enterprises (BID ID -940378) | 2506925.00 | L7
| 8 | VL SERVICES (BID ID -935389) | 2579795.00 | L8