## BoQ1
Government eProcurement System Created By: Debashis Mondal Created Date/Time: 27-Jan-2026 12:44 PM Tender Title: Providing and Installation of Pre Fabricated Pseudo PUF Toilet Block along with providing and sinking of required bore wells at NSCBI Airport Kolkata SH Electrical Works Tender ID: 2025_AAI_256982_1
Tender Inviting Authority: AAI, NSCBI AIRPORT, KOLKATA
Name of Work: Providing and Installation of Pre-Fabricated Pseudo PUF Toilet Block along with providing and sinking of required bore wells at NSCBI Airport, Kolkata. SH: Electrical Works.
Contract No: 2025_AAI_256982_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/s. A S Traders (GSTN-19AKDPR7595N1ZA) BID ID -942212 |  | M/s J.K. Electric Engineering Works (GSTN-19AAHFJ4404E1ZL) BID ID -943676 |  | Youngmen Traders (GSTN-19AEIPB6323B1ZZ) BID ID -945455 |  | MANNA ELECTRONICS AND ELECTRICAL WORKS (GSTN-19AALFM9363P2Z6) BID ID -945843
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of 7.5 HP (5.6 kW), 3 Phase, 415 volts, 50 Hz, rating, vertical Submersible Pump Motor set, discharge capacity minimum 200 LPM, head minimum - 90 mtrs, suitable for DOL operation etc as required as per specification and AAI preferred make list. | 2.00 | Each |  | 60000.00 | 120000.00 | 115000.00 | 230000.00 | 40500.00 | 81000.00 | 57224.00 | 114448.00 | 81000.00 | Youngmen Traders
2.00 | ITC of existing (as per BOQ Item No. 1) 7.5 HP Submersible Pump Motor set, including Supply and Laying of 80 mm dia. C class Gl pipe (flange type joints) with necessary sockets, bends, nut-bolts, washer, gasket etc. upto 60Mtr with reducer compatible to distribution outlet, 10 mm double steel wire rope upto 100 mtr . 4 sq.mm X 3 core copper flat cable upto 60 Mtr. including lowring with U clamp, well cover(as per site requirement). NRV and Gate valve, supporting clamps, flange, pressure gauge etc.required. | 2.00 | Job |  | 330000.00 | 660000.00 | 25000.00 | 50000.00 | 85000.00 | 170000.00 | 180000.00 | 360000.00 | 50000.00 | M/s J.K. Electric Engineering Works
3.00 | Design, Fabrication, supply, installation, Testing and commissioning of outdoor type dust & vermin proof feeder pillar made of not less than 2mm thick MS sheet of suitable size confirning to IP 55 with 4 strip TPN aluminium bus bar suitable for 100 amps capacity & including hinged lockable door on the both side of panel etc, as required. Supply and fixing, of following electrical switchgears including interconnection of switchgears with suitable capacity of aluminium busbar/ cable, required 3 phase ammeter and Volt meter, LED indicators, interconnection, earthing, painting, i/c cleaning and finishing complete with powder coating in approved shade, bottom base of MS channel and Legs (50mmx50mmx6mm) , have a common GI earth bar with 2 nos earth stud, internal connection by suitable aluminium strip/bar or aluminium cable as per specification and control wiring with 2.5 Sq.mm PVC insulated copper conductor cable i/c providing the following switch gears and same should be fixed 2 ft. height (from ground level) on brick foundation, i/c outgoing and incoming electrical connection etc as required. 1. 100 amps, 4 pole, 25 KA MCCB incoming with extended rotary handle-2 No's 2. DOL starter-1 No. ( Pump operation should be capable of both Auto and Manual mode with selector switch and timer switch -suitable for BOQ Item No.01 mentioned above). 3. DP MCB-32A - 3 Nos. 4. ﻿﻿﻿Single phasing preventer-1 No's 5.﻿ Timer switch with suitable power contactor-1No's 6. Thermal Over Load relay-1 No's 7. Digital Voltmetr (0 to 500 volts) with selector switches at both the incomers - 02 nos 8. Digital Ammeter (0 to 150 A ) - 05 nos with necessary CTs and selector switches at all incomers and outgoings, 9. RYB indication lamps & ON/OFF & trip-led indication lamp - ( each incomer)- 02 sets 10.ON/OFF & trip-led indication lamp at all outgoings - 03 sets Note: All the control/ indication wiring should be separate & individual MCB as required | 3.00 | Job |  | 120000.00 | 360000.00 | 310000.00 | 930000.00 | 160000.00 | 480000.00 | 325000.00 | 975000.00 | 360000.00 | M/s. A S Traders
4.00 | Supply of 1.1 kV Power Cable with Aluminium Conductor XLPE Insulated Armoured As Per IS‐7098 (Part 1) 2011 with Up To Date Amendments of following sizes
4.10 | 3.5 core X 95 sq mm | 1950.00 | Mtr |  | 495.00 | 965250.00 | 900.00 | 1755000.00 | 465.00 | 906750.00 | 799.00 | 1558050.00 | 906750.00 | Youngmen Traders
5.00 | Laying of XLPE power cable of 1.1 kV grade of size upto 95 sq.mm in the following
5.10 | Direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. | 400.00 | Mtr |  | 380.00 | 152000.00 | 500.00 | 200000.00 | 315.00 | 126000.00 | 450.00 | 180000.00 | 126000.00 | Youngmen Traders
5.20 | In the existing RCC/ HUME/ METAL/HDPE pipe as required. | 1450.00 | Mtr |  | 50.00 | 72500.00 | 40.00 | 58000.00 | 50.00 | 72500.00 | 20.00 | 29000.00 | 29000.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
5.30 | In the existing masonry open duct as required. | 50.00 | Mtr |  | 30.00 | 1500.00 | 40.00 | 2000.00 | 40.00 | 2000.00 | 20.00 | 1000.00 | 1000.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
5.40 | On wall surface with proper saddling as required. | 50.00 | Mtr |  | 150.00 | 7500.00 | 60.00 | 3000.00 | 75.00 | 3750.00 | 35.00 | 1750.00 | 1750.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
6.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1KV grade as required
6.10 | 3.5 X 95 sq mm | 8.00 | Each |  | 600.00 | 4800.00 | 400.00 | 3200.00 | 1400.00 | 11200.00 | 566.00 | 4528.00 | 3200.00 | M/s J.K. Electric Engineering Works
7.00 | Supplying and making straingt through joint with cast resin compound including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed/XLPE aluminium conductor cable of 1.1 KV grade as required.
7.10 | 3.5 X 95 sq mm | 4.00 | Each |  | 2800.00 | 11200.00 | 2200.00 | 8800.00 | 1800.00 | 7200.00 | 2855.00 | 11420.00 | 7200.00 | Youngmen Traders
8.00 | Supply of nominal 75 mm outer dia, PE - 80 grade, PN 10 rated, SDR 11 HDPE Pipe of minimum wall thickness 14.3 mm HDPE (High Density Polyethylene) pipe, conforming to IS 4984:2016 (along with latest amendments) and as directed by Engineer –in-charge. | 1400.00 | Meter |  | 250.00 | 350000.00 | 190.00 | 266000.00 | 225.00 | 315000.00 | 320.00 | 448000.00 | 266000.00 | M/s J.K. Electric Engineering Works
9.00 | Laying of above mentioned (as per BOQ item no. 8) HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 1400.00 | Meter |  | 520.00 | 728000.00 | 190.00 | 266000.00 | 115.00 | 161000.00 | 155.00 | 217000.00 | 161000.00 | Youngmen Traders
10.00 | Supply of 80 mm dia., Class-B, GI pipe conforming to IS:1239 PART-1 (2004) | 50.00 | Meter |  | 800.00 | 40000.00 | 1300.00 | 65000.00 | 600.00 | 30000.00 | 650.00 | 32500.00 | 30000.00 | Youngmen Traders
11.00 | Laying of 80 mm dia GI pipe (as per BOQ Item No. 10) below the ground (i/c. Road crossing, Cement concrete, Across the Runway / Taxi way/ APRON/ Perimeter Road/ Field) at a depth Not less than 75 cm (For LT Cable) along with all accessories like socket, bend, couplers etc. complete with fitting and cutting, jointing etc.direct in ground including excavation and refilling the trench but excluding sand cushioning and protective covering etc. complete as required | 50.00 | Meter |  | 760.00 | 38000.00 | 450.00 | 22500.00 | 125.00 | 6250.00 | 75.00 | 3750.00 | 3750.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
12.00 | Earthing with Gl earth pipe 4.5 mtr Long, 40mm dia i/c all accessories and providing masonary enclosure with cover plate, having locking arrangement and watering pipe etc, with charcoal/coke and salt as required. | 6.00 | Each |  | 6000.00 | 36000.00 | 4500.00 | 27000.00 | 6000.00 | 36000.00 | 4700.00 | 28200.00 | 27000.00 | M/s J.K. Electric Engineering Works
13.00 | Supplying and laying 25mm X 5 mm G.I. strip at 0.50 meter below ground as strip earth electrode, including connection/terminating with G.I. nut,bolt, spring, washer etc. as required (Joining shall be by overlapping and with 2 sets of G.I nut bolt & spring washer spaced at 50mm) | 40.00 | Meter |  | 120.00 | 4800.00 | 180.00 | 7200.00 | 105.00 | 4200.00 | 120.00 | 4800.00 | 4200.00 | Youngmen Traders
14.00 | Providing & fixing 25 mm. X 5 mm. thick GI strip in 40 mm. dia. G.I. pipe from earth electrode including connection with G.I. nut,bolt, spring, washer excavation and refilling etc. as reqd. | 40.00 | Meter |  | 600.00 | 24000.00 | 450.00 | 18000.00 | 395.00 | 15800.00 | 356.00 | 14240.00 | 14240.00 | MANNA ELECTRONICS AND ELECTRICAL WORKS
15.00 | Providing & laying earth connection from the earth electrode with 6 SWG dia G.I. wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble ex-cavation and re-filling etc. as reqd. | 40.00 | Meter |  | 330.00 | 13200.00 | 215.00 | 8600.00 | 125.00 | 5000.00 | 142.00 | 5680.00 | 5000.00 | Youngmen Traders
16.00 | Providing and making masonary inspection chember of size not less than 2000 mm X 2000 mm X 1200 mm. deep (inside) i/c. excavation of soil, 75 mm. flat brick soiling at the bottom 50 mm. base concrete over brick soiling, 250 mm. brick work with cement morter, cement plaster on brick work bottom (only inside surface), providing removable RCC slabs of suitable size on the top of the chamber with providing suitable lifting arrangement etc. complete as reqd. | 5.00 | Job |  | 17700.00 | 88500.00 | 30000.00 | 150000.00 | 18000.00 | 90000.00 | 25000.00 | 125000.00 | 88500.00 | M/s. A S Traders
17.00 | Supply of vertical Booster Pump Motor sets having Stainless Steel impeller,stainless steel shaft, along with a directly coupled squirrel cage electric induction motor of not less than 3HP, 2900 RPM, suitable for operation of 415Volt +10%V 50Hz, 3 Phase A.C Supply, water lubricated bearings in all respect as required. Discharge- not less than 58.33 LPM Head - not less than 85 Meter (KSB make MOVITEC VF 4/11-8 pumps or equivalent as per AAI preferred make list suitable for boosting operation at reservoirs inside operational area). | 2.00 | Each |  | 75000.00 | 150000.00 | 48000.00 | 96000.00 | 52000.00 | 104000.00 | 76800.00 | 153600.00 | 96000.00 | M/s J.K. Electric Engineering Works
18.00 | ITC of existing (as per BOQ Item No. 17) 3 HP Booster Pump Motor set, including Supply and Laying of 50 mm dia. C class Gl pipe (flange type joints) with necessary sockets, bends, nut-bolts, washer, gasket etc. upto 100 Mtr with reducer compatible to distribution outlet, 4 sq.mm X 3 core armoured copper cable upto 100 Mtr. (as per site requirement), NRV and Gate valve, supporting clamps, flange, pressure gauge etc., DOL starter panel/feeder pillar box for controling as required in complete. | 2.00 | Job |  | 150000.00 | 300000.00 | 9000.00 | 18000.00 | 85000.00 | 170000.00 | 175000.00 | 350000.00 | 18000.00 | M/s J.K. Electric Engineering Works
19.00 | Providing and fixing of 100 amps, 4 pole, 25 KA MCCB at existing LT Panel/ACDB/Pillar Box at required locations including drilling holes in cubicle panel, making connections, etc. as required. | 5.00 | Job |  | 14500.00 | 72500.00 | 10000.00 | 50000.00 | 4800.00 | 24000.00 | 5850.00 | 29250.00 | 24000.00 | Youngmen Traders
| Total in Figures |  |  |  |  | 4199750.00 |  | 4234300.00 |  | 2821650.00 |  | 4647216.00
Lowest Amount Quoted BY: Youngmen Traders(2821650.00)

## BOQ Summary
BOQ Summary Details Tender Title: Providing and Installation of Pre Fabricated Pseudo PUF Toilet Block along with providing and sinking of required bore wells at NSCBI Airport Kolkata SH Electrical Works Tender ID: 2025_AAI_256982_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Youngmen Traders (BID ID -945455) | 2821650.00 | L1
| 2 | M/s. A S Traders (BID ID -942212) | 4199750.00 | L2
| 3 | M/s J.K. Electric Engineering Works (BID ID -943676) | 4234300.00 | L3
| 4 | MANNA ELECTRONICS AND ELECTRICAL WORKS (BID ID -945843) | 4647216.00 | L4