## BoQ1
Government eProcurement System Created By: KUMAR RIJENDRA Created Date/Time: 02-Jan-2026 05:24 PM Tender Title: SITC of LT Panels, High Mast, Street Light alongwith other miscellaneous works at AAI Residential Colony of Ranchi Airport,Ranchi Tender ID: 2025_AAI_257680_1
Tender Inviting Authority: AGM (Engg.-Elect.)
Name of Work: SITC of LT Panels, High Mast, Street Light alongwith other miscellaneous works at AAI Residential Colony of Ranchi Airport,Ranchi.
Tender ID: 2025_AAI_257680_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/s CGPL ELECTROMECH PVT LTD (GSTN-07AAGCC8228F1ZO) BID ID -947690 |  | METRO ENGINEERS SERVICES (GSTN-08AUHPK7216R1ZT) BID ID -947863 |  | M/S AMAR ENTERPRISES (GSTN-20AAMFA2722R1ZE) BID ID -947963 |  | Virtus Techno (GSTN-NA) BID ID -941930
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design,Fabrication,Assembly,Wiring, Supply of cubicle type Outdoor LT panel, IP54 protection with weather proof canopy on top, double door arrangement, suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system,fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, dust and vermin proof , totally enclosed, Form 3b compartmentalised design, floor mounting, free standing having 4P Aluminium alloy bus bars for high conductivity, DMC/SMC bus bar supports, with short circuit withstand capacity of 25 KA for 1 sec , bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common Copper earth bus bar of size 25mm x 5mm at the rear with 2 Nos. earth stud, solid /flexible connections from main busbar to switchgears and from switchgear output to cable termination in cable alley with required size of Busbar / Aluminium Conductor and control wiring with 2.5 sqmm FRLS PVC insulated copper conductor cable, cable alleys, cable gland plates in two half including providing following switchgears /metering instrunments and accessories as per specifications.
1.01 | a) INCOMER 02 Nos. MCCB , 160 Amps, 4 Pole , 25 kA with adjustable setting , thermal magnetic release with O/C & S/C protection (Ics=100% Icu) complete with following accessories: Each Incomer shall have one set of the following items: 1 No. 96 mm x 96 mm digital type Voltmeter of suitable range for 3phase,4 wire operation with LED display and selector switch and backup by 3 Nos of 2Amp MCB. 1 No.96 mm x 96 mm digital type Ammeter for 3 phase 4 wire operation with LED display and selector switch and suitable rating CT's 3 Nos of LED Type Phase indicating lamps (R,Y,B) controlled by 2Amp MCB -1Set 03 Nos LED Type ON/ OFF/ TRIP with 2Amp control MCBs-1set 2 Nos. Four Module Type2 / Class C Surge Protection Device 65kA with suitable rating backup fuse including all necessary accessories. b) BUSCOUPLER (i) 01 Nos. MCCB , 160Amps, 4 Pole , 25 kA with adjustable setting , thermal magnetic release with O/C & S/C protection (Ics=100% Icu) (ii) 03 Nos LED Type ON/ OFF/ TRIP with 2Amp control MCBs-1set (iii)All Incomers & Bus-Couplers shall be interlocked electrically & mechanically (castel key) with suitable accessories. c) BUS BAR Four Pole aluminium extensible type main bus bars of minimum 200 Amps. capacity with heat shrinkable coloured sleeves having 100% neutral bus as that of phase i/c DMC / SMC bus bars supports at required intervals complete for cross section, size supports & having spacing etc. for withstanding fault level of 25kA capacity for 1 sec. d) OUTGOINGS i)4 pole, 125 Amps,25 KA thermal magnetic release type MCCB (Ics=100% Icu) - 02 Nos ii)4 pole, 63 Amps,25 KA thermal magnetic release type MCCB (Ics=100% Icu) - 02 Nos iii)4 pole, 40 Amps,25 KA thermal magnetic release type MCCB (Ics=100% Icu) - 06 Nos Each MCCB outgoings shall have LED type ON/OFF indication lamp with backup of 2 Amp SP MCB iv) 2 Pole, 32 Amps,10 kA, "C" curve MCBs-4 Nos Note: a) 1 Set Rotary operating mechanism and terminal extension spreaders with door interlock shall be provided for all Incomers and Buscouplers b) All accessories such as auxiliary contactors, auxiliary switches, MCBs, phase seperators etc. as required. | 1.00 | Job | 227250.00 | 185700.00 | 185700.00 | 500000.00 | 500000.00 | 150000.00 | 150000.00 | 532537.20 | 532537.20 | 150000.00 | M/S AMAR ENTERPRISES
2.00 | Design,Fabrication,Assembly,Wiring, Supply of cubicle type Outdoor LT panel, IP54 protection with weather proof canopy on top, double door arrangement, suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system,fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, dust and vermin proof , totally enclosed, Form 3b compartmentalised design, floor mounting, free standing having 4P Aluminium alloy bus bars for high conductivity, DMC/SMC bus bar supports, with short circuit withstand capacity of 25 KA for 1 sec , bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common Copper earth bus bar of size 25mm x 5mm at the rear with 2 Nos. earth stud, solid /flexible connections from main busbar to switchgears and from switchgear output to cable termination in cable alley with required size of Busbar / Aluminium Conductor and control wiring with 2.5 sqmm FRLS PVC insulated copper conductor cable, cable alleys, cable gland plates in two half including providing following switchgears /metering instrunments and accessories as per specifications.
2.01 | a) INCOMER 02 Nos. MCCB , 125 Amps, 4 Pole , 25 kA with adjustable setting , thermal magnetic release with O/C & S/C protection (Ics=100% Icu) complete with following accessories: Each Incomer shall have one set of the following items: 1 No. 96 mm x 96 mm digital type Voltmeter of suitable range for 3phase,4 wire operation with LED display and selector switch and backup by 3 Nos of 2Amp MCB. 1 No.96 mm x 96 mm digital type Ammeter for 3 phase 4 wire operation with LED display and selector switch and suitable rating CT's 3 Nos of LED Type Phase indicating lamps (R,Y,B) controlled by 2Amp MCB -1Set 03 Nos LED Type ON/ OFF/ TRIP with 2Amp control MCBs-1set 2 Nos. Four Module Type2 / Class C Surge Protection Device 65kA with suitable rating backup fuse including all necessary accessories. b) BUSCOUPLER (i) 01 Nos. MCCB , 125Amps, 4 Pole , 25 kA with adjustable setting , thermal magnetic release with O/C & S/C protection (Ics=100% Icu) (ii) 03 Nos LED Type ON/ OFF/ TRIP with 2Amp control MCBs-1set (iii)All Incomers & Bus-Couplers shall be interlocked electrically & mechanically (castel key) with suitable accessories. c) BUS BAR Four Pole aluminium extensible type main bus bars of minimum 200 Amps. capacity with heat shrinkable coloured sleeves having 100% neutral bus as that of phase i/c DMC / SMC bus bars supports at required intervals complete for cross section, size supports & having spacing etc. for withstanding fault level of 25kA capacity for 1 sec. d) OUTGOINGS i) 4 pole, 63 Amps,25 KA thermal magnetic release type MCCB (Ics=100% Icu) with suitable 4 pole contactor, 0-24 hours astroniomical timer, auto /manual selector switches , Start/Stop Push Button and necessary wiring etc. -2 set iii)4 pole, 40 Amps,25 KA thermal magnetic release type MCCB (Ics=100% Icu) - 06 Nos Each MCCB outgoings shall have LED type ON/OFF indication lamp with backup of 2 Amp SP MCB iv) 2 Pole, 32 Amps,10 kA, "C" curve MCBs-4 Nos Note: a) 1 Set Rotary operating mechanism and terminal extension spreaders with door interlock shall be provided for all Incomers and Buscouplers b) All accessories such as auxiliary contactors, auxiliary switches, MCBs, phase seperators etc. as required. | 1.00 | Job | 166650.00 | 125000.00 | 125000.00 | 300000.00 | 300000.00 | 100000.00 | 100000.00 | 305355.60 | 305355.60 | 100000.00 | M/S AMAR ENTERPRISES
3.00 | Design,Fabrication,Assembly,Wiring, Supply of cubicle type Outdoor Feeder Pillar, water proof with weather proof canopy on top, double door arrangement, suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system,fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick i/c powder coated painting in approved shade, dust and vermin proof , totally enclosed, floor mounting, free standing having 4P Aluminium alloy bus bars for high conductivity, DMC/SMC bus bar supports , provision for earthing connections , solid /flexible connections from main bus bar to switchgears and from switchgear output to cable termination in cable alley with required size of Busbar / Aluminium Conductor and control wiring with 2.5 sqmm FRLS PVC insulated copper conductor cable, cable alleys including providing following switchgears /metering instrunments and accessories as per specifications. The Feeder Pillar have to be supplied with suitable pedestal (MS angle Iron frame of MS Channel Base for grouting in the PCC & proper gland at the bottom)
3.01 | a) INCOMER 01 Nos. MCCB , 100 Amps, 4 Pole , 25 kA with adjustable setting , thermal magnetic release with O/C & S/C protection (Ics=100% Icu) complete with following accessories: Each Incomer shall have one set of the following items: 1 No. 96 mm x 96 mm digital type Voltmeter of suitable range for 3phase,4 wire operation with LED display and selector switch and backup by 3 Nos of 2Amp MCB. 1 No.96 mm x 96 mm digital type Ammeter for 3 phase 4 wire operation with LED display and selector switch and suitable rating CT's 3 Nos of LED Type Phase indicating lamps (R,Y,B) controlled by 2Amp MCB -1 Set 03 Nos LED Type ON/ OFF/ TRIP with 2Amp control MCBs-1set b) BUS BAR Four Pole aluminium extensible type main bus bars of suitable capacity with heat shrinkable coloured sleeves having 100% neutral bus as that of phase i/c DMC / SMC bus bars supports at required intervals c) OUTGOINGS i)4 pole, 63 Amps,25 KA thermal magnetic release type MCCB (Ics=100% Icu) - 04 Nos ii)4 pole, 40 Amps,25 KA thermal magnetic release type MCCB (Ics=100% Icu) - 02 Nos Each MCCB outgoings shall have LED type ON/OFF indication lamp with backup of 2 Amp SP MCB iii) 2 pole , 40 Amps, , 10 kA, "C" curve MCBs-6 Nos Note: a) 1 Set Rotary operating mechanism and terminal extension spreaders with door interlock shall be provided for all Incomers b) All accessories such as auxiliary contactors, auxiliary switches, MCBs, phase seperators etc. as required. | 1.00 | Job | 129280.00 | 105000.00 | 105000.00 | 160000.00 | 160000.00 | 100000.00 | 100000.00 | 194091.60 | 194091.60 | 100000.00 | M/S AMAR ENTERPRISES
4.00 | Supply of XLPE insulated and PVC sheathed aluminium conductor armoured power cable of 1.1 KV grade conforming to IS 7098 (Part-I) 1988 as amended upto date and of following size as required.
4.01 | a) 3.5C X 35 Sq.mm | 1500.00 | Meter | 245.00 | 255.00 | 382500.00 | 260.00 | 390000.00 | 160.00 | 240000.00 | 226.26 | 339390.00 | 240000.00 | M/S AMAR ENTERPRISES
4.02 | b) 3.5C X 120 Sq.mm | 500.00 | Meter | 997.00 | 1010.00 | 505000.00 | 700.00 | 350000.00 | 600.00 | 300000.00 | 655.56 | 327780.00 | 300000.00 | M/S AMAR ENTERPRISES
4.03 | c) 3.5C X 185 Sq.mm | 900.00 | Meter | 1123.00 | 1120.00 | 1008000.00 | 910.00 | 819000.00 | 850.00 | 765000.00 | 983.34 | 885006.00 | 765000.00 | M/S AMAR ENTERPRISES
5.00 | Supply of following outer dia ISI marked HDPE Pipe as per IS :4984:2016 of PE 80 grade and PN 6 rating complete as required
5.01 | a) 63mm | 650.00 | Meter | 303.00 | 230.00 | 149500.00 | 130.00 | 84500.00 | 100.00 | 65000.00 | 93.60 | 60840.00 | 60840.00 | Virtus Techno
5.02 | b) 110mm | 450.00 | Meter | 404.00 | 340.00 | 153000.00 | 310.00 | 139500.00 | 300.00 | 135000.00 | 283.20 | 127440.00 | 127440.00 | Virtus Techno
6.00 | Installation, Testing and Commissioning of LT Outdoor Panel for Guest House mentioned at Item No.1 including excavation for foundation, providing Civil foundation, suitable masonary pedestal upto 45cm height from Ground Level, fixing of panel with required fasterners etc complete as required. | 1.00 | Job | 18180.00 | 2000.00 | 2000.00 | 1500.00 | 1500.00 | 5000.00 | 5000.00 | 30000.00 | 30000.00 | 1500.00 | METRO ENGINEERS SERVICES
7.00 | Installation, Testing and Commissioning of LT Outdoor Panel for Street Light mentioned at Item No.2 including excavation for foundation, providing Civil foundation, suitable masonary pedestal upto 45cm height from Ground Level, fixing of panel with required fasterners etc complete as required. | 1.00 | Job | 17675.00 | 2000.00 | 2000.00 | 1500.00 | 1500.00 | 5000.00 | 5000.00 | 30000.00 | 30000.00 | 1500.00 | METRO ENGINEERS SERVICES
8.00 | Installation, Testing and Commissioning of LT Outdoor Feeder Pillar mentioned at Item No.3 including excavation for foundation, providing Civil foundation, ,grouting of Panel Pedestal in the Foundation with required fasterners etc complete as required. | 1.00 | Job | 12120.00 | 2000.00 | 2000.00 | 1500.00 | 1500.00 | 5000.00 | 5000.00 | 30000.00 | 30000.00 | 1500.00 | METRO ENGINEERS SERVICES
9.00 | Supply of 08 Mtrs. high GI OCTAGONAL continuously tapered Galvanised Street Light Pole with minimum 1Mtr long single/double arm 32/40NB GI bracket mounted on pole for installation of LED street light luminaire suitable for wind velocity as per IS 875 (but not less than 50 m/sec.), fabricated out of 3 mm thick sheet in single section having top dia 70 mm and bottom dia 135 mm, suitable for installation on a precast foundation with supply of 4 Nos. of foundation bolt (20mm dia of 700 mm long) & anchor plate, rigid flange plate (225x225x16mm min.) welded with the base of pole for fixing on foundation bolts complete as reqd. for structural stability as specified, weather proof and vandal resistant door flush with the exterior surface containing a terminal plate of 5 mm thick bakelite sheet with 32 Amp heavy duty 4pole connector for loop in loop out cable terminations suitable for upto two numbers 4 core 25 Sq.mm cables & 6A DP MCB for each fixture connections, earthing bolts for continuous earth connection with 20mm dia, 1.5 m long MS rod for individual poles earthing etc complete as required & as specified. | 6.00 | Job | 16160.00 | 6500.00 | 39000.00 | 10500.00 | 63000.00 | 7000.00 | 42000.00 | 10578.00 | 63468.00 | 39000.00 | M/s CGPL ELECTROMECH PVT LTD
10.00 | Erection of 08 Mtr.High OCTAGONAL Street light Pole & Bracket with all accessories in reinforced cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) foundation as per OEM design including excavation and refilling including positioning of template & foundation bolts (supplied with pole to match with pole base plate) & providing and fixing of HDPE pipe of size 63 mm dia (2 pieces of min. 0.75 m length) in the foundation for loop-in-loop-out of the cable to the pole, connecting earthing bolt and the earth rod with 6 SWG GI wire of required length complete as required | 6.00 | Job | 10100.00 | 3000.00 | 18000.00 | 1900.00 | 11400.00 | 2000.00 | 12000.00 | 30000.00 | 180000.00 | 11400.00 | METRO ENGINEERS SERVICES
11.00 | Design ,Fabrication,Supply,Erection, Testing and Commissioning of 12.5 (Twelve & half) metre height hot dip galvanised high mast in two section suitable for wind velocity as per IS 875 Part-3 alongwith its all accessories i.e. head frame, suitable SS wire rope, double/triple drum winch,Galvanised lantern carriage arrangement suitable to install minimum 08 Nos. 200 Watts LED Flood Light luminaries & its controlgear boxes (or equivalent such as counter weighted as per design) in symmetrical arrangenment with required cable connection from Panel to mast top & wiring/cabling to each LED fitting and aviation Obstruction Light with counter weight (if required), lightning finial, MCB, suitable electric driven integral power tool motor installed inside the base compartment for its operation and also for manual operation, trailing Copper cable of suitable size,connector,manual handle,junction box, foundation bolts along with Nuts, Bolts, washers, anchor plates and templates etc. as reqiured | 5.00 | Job | 126250.00 | 75000.00 | 375000.00 | 19500.00 | 97500.00 | 125000.00 | 625000.00 | 102000.00 | 510000.00 | 97500.00 | METRO ENGINEERS SERVICES
12.00 | Design and casting of suitable shallow foundation with M-20 grade concrete for the above 12.5 mtr. high mast mentioned in Item No.-11 considering the safe soil bearing capacity at site as 10T/Sq.Mtr at min. 2 metres depth including all materials and Labour. The work also includes hard/soft soil exacavation for foundation & disposal of excavated soil .The Foundation design shall be vetted by the NIT/IIT or any Goverment institution and shall be suitable to withstand wind pressure of 50 m/sec along with desired fitting etc. as required. | 5.00 | Job | 80800.00 | 35000.00 | 175000.00 | 4900.00 | 24500.00 | 35000.00 | 175000.00 | 36000.00 | 180000.00 | 24500.00 | METRO ENGINEERS SERVICES
13.00 | Supply, Installation,Testing and Commissioning of LED Flood Light Luminaire of 200Watts (min) with high power LED's having luminaire efficacy of not less than 110 lm/W (Narrow/Medium beam for meeting LUX levels as per IS) with secondary optic lens and designed with Powder coated Pressure Die Cast aluminium housing, frame, integral driver with Surge protection, heat resistant toughened glass, confirming to IP 66 protection suitable to operate on 140-270V, 50Hz AC supply, CRI>70, CCT from 5700K - 6500K with PF≥0.95 and THD<10% including control gear and all accessories, suitable for outdoor applications for the High mast complete as required. | 40.00 | Each | 6565.00 | 4200.00 | 168000.00 | 4900.00 | 196000.00 | 4500.00 | 180000.00 | 5940.00 | 237600.00 | 168000.00 | M/s CGPL ELECTROMECH PVT LTD
14.00 | Supply,Installation,Testing and Commissioning of LED Type low intensity aviation obstruction light suitable for 220 V , 50 HZ AC supply complete as required. | 5.00 | Each | 3030.00 | 3000.00 | 15000.00 | 500.00 | 2500.00 | 4000.00 | 20000.00 | 3000.00 | 15000.00 | 2500.00 | METRO ENGINEERS SERVICES
15.00 | Design,Supply,Installation,Testing and Commissioning of floor mounted outdoor type distribution feeder pillar of suitable size ,totally enclosed,free standing, dust & vermin proof,Water proof,front operated, double door made of 2 mm thick ,rubber gasket,powder coating painting,weather proof canopy on top with provision for incoming cable connection of 35 Sqmm and outgoing 16 & 2.5 Sqmm terminals for the Luminaries & power tool motor etc. complete with earthing terminals, support for switchgears & busbars with suitable angle iron base frame , cement concrete foundation for Panel and suitable for operation on 3 Phase and 4 wire, 415V, 50 Hz AC supply system including control wiring, necessary connections,interconnections etc and supply & mountings of following items. Incomer: 40Amps,4Pole MCB , C series, 10KA -01 Nos RYB Phase Indicating Lamps ( LED Type) - 1 set Ammeter with selector switch and suitable CT -01 set Voltmeter with selector switch - 01 set Suitable TPN Bus bars of Aluminium alloy-1 Set Outgoings: 32Amps, 4Pole MCB , C series, 10KA -03 Nos (2 Main + 01 Standby) 32Amps , 3Pole Power Contactor with necessary timer & auxiliary contacts for automatic switching of luminaries-1 Set 9Amps ,3Pole Power Contactor with necessary auxiliary contacts for Power Tool motor control - 2Nos Auto & Manual Selector Switch- 1 Nos Raise & Lower Push Button for motor operation-1 Set 16 &2.5 Sqmm terminals/connectors for outgoings - 01 set | 5.00 | Job | 35193.00 | 15500.00 | 77500.00 | 108000.00 | 540000.00 | 20000.00 | 100000.00 | 39000.00 | 195000.00 | 77500.00 | M/s CGPL ELECTROMECH PVT LTD
16.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/GI pipe/DWC/HDPE as required.
16.01 | a) Upto 35 sq. mm | 650.00 | Meter | 45.00 | 10.00 | 6500.00 | 29.00 | 18850.00 | 10.00 | 6500.00 | 72.00 | 46800.00 | 6500.00 | M/s CGPL ELECTROMECH PVT LTD, M/S AMAR ENTERPRISES
16.02 | b) Above 95 sq.mm and upto 185 sq mm | 450.00 | Meter | 91.00 | 15.00 | 6750.00 | 29.00 | 13050.00 | 10.00 | 4500.00 | 120.00 | 54000.00 | 4500.00 | M/S AMAR ENTERPRISES
17.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
17.01 | a) Upto 35 sq. mm | 30.00 | Meter | 30.00 | 10.00 | 300.00 | 29.00 | 870.00 | 10.00 | 300.00 | 72.00 | 2160.00 | 300.00 | M/s CGPL ELECTROMECH PVT LTD, M/S AMAR ENTERPRISES
17.02 | b) Above 95 sq.mm and upto 185 sq mm | 30.00 | Meter | 66.00 | 20.00 | 600.00 | 29.00 | 870.00 | 10.00 | 300.00 | 120.00 | 3600.00 | 300.00 | M/S AMAR ENTERPRISES
18.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
18.01 | a) Upto 35 sq. mm (clamped with 1mm thick saddle) | 650.00 | Meter | 51.00 | 10.00 | 6500.00 | 29.00 | 18850.00 | 10.00 | 6500.00 | 72.00 | 46800.00 | 6500.00 | M/s CGPL ELECTROMECH PVT LTD, M/S AMAR ENTERPRISES
18.02 | b) Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 800.00 | Meter | 167.00 | 20.00 | 16000.00 | 29.00 | 23200.00 | 10.00 | 8000.00 | 120.00 | 96000.00 | 8000.00 | M/S AMAR ENTERPRISES
19.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required
19.01 | a) 3½ X 35 sq. mm (32mm) | 16.00 | Each | 328.00 | 200.00 | 3200.00 | 150.00 | 2400.00 | 200.00 | 3200.00 | 420.00 | 6720.00 | 2400.00 | METRO ENGINEERS SERVICES
19.02 | b) 3½ X 120 sq. mm (45mm) | 6.00 | Each | 505.00 | 300.00 | 1800.00 | 180.00 | 1080.00 | 300.00 | 1800.00 | 600.00 | 3600.00 | 1080.00 | METRO ENGINEERS SERVICES
19.03 | c) 3½ X 185 sq. mm (57mm) | 4.00 | Each | 960.00 | 350.00 | 1400.00 | 300.00 | 1200.00 | 500.00 | 2000.00 | 1020.00 | 4080.00 | 1200.00 | METRO ENGINEERS SERVICES
20.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
20.01 | a) 3½ X 35 sq. mm | 5.00 | Each | 3030.00 | 1200.00 | 6000.00 | 1500.00 | 7500.00 | 1500.00 | 7500.00 | 702.00 | 3510.00 | 3510.00 | Virtus Techno
20.02 | b) 3½ X 120 sq. mm | 2.00 | Each | 5050.00 | 1350.00 | 2700.00 | 1500.00 | 3000.00 | 2500.00 | 5000.00 | 1452.00 | 2904.00 | 2700.00 | M/s CGPL ELECTROMECH PVT LTD
20.03 | c) 3½ X 185 sq. mm | 2.00 | Each | 6060.00 | 1750.00 | 3500.00 | 1500.00 | 3000.00 | 3000.00 | 6000.00 | 1710.00 | 3420.00 | 3000.00 | METRO ENGINEERS SERVICES
21.00 | Laying of following Outer dia HDPE pipe along with all accessories like socket, bend , couplers etc. complete with fitting and cutting, jointing etc. in cement concrete / bitumen surface i/c cutting cement concrete / bitumen surface and finishing with good surface after laying HDPE pipe etc. as required:
21.01 | a) 63mm dia | 60.00 | Meter | 149.00 | 35.00 | 2100.00 | 29.00 | 1740.00 | 50.00 | 3000.00 | 96.00 | 5760.00 | 1740.00 | METRO ENGINEERS SERVICES
21.02 | b) 110mm dia | 40.00 | Meter | 174.00 | 55.00 | 2200.00 | 29.00 | 1160.00 | 50.00 | 2000.00 | 120.00 | 4800.00 | 1160.00 | METRO ENGINEERS SERVICES
22.00 | Laying of following Outer dia HDPE pipe through trenchless technology (HDD) by drilling the bore of suitable dia directly in ground upto the depth of approx 2 meters from the ground level including necessary jointing coupling, splicing etc as required.
22.01 | a) 63mm dia | 450.00 | Meter | 288.00 | 200.00 | 90000.00 | 29.00 | 13050.00 | 100.00 | 45000.00 | 96.00 | 43200.00 | 13050.00 | METRO ENGINEERS SERVICES
22.02 | b) 110mm dia | 260.00 | Meter | 343.00 | 210.00 | 54600.00 | 29.00 | 7540.00 | 100.00 | 26000.00 | 120.00 | 31200.00 | 7540.00 | METRO ENGINEERS SERVICES
23.00 | Laying of following Outer dia HDPE pipe along with all accessories like socket, bend , couplers etc. complete with fitting and cutting, jointing etc. direct in ground(75 cm below level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. complete as required.
23.01 | a) 63mm dia | 200.00 | Meter | 253.00 | 125.00 | 25000.00 | 29.00 | 5800.00 | 100.00 | 20000.00 | 96.00 | 19200.00 | 5800.00 | METRO ENGINEERS SERVICES
23.02 | b) 110mm dia | 160.00 | Meter | 379.00 | 175.00 | 28000.00 | 29.00 | 4640.00 | 100.00 | 16000.00 | 120.00 | 19200.00 | 4640.00 | METRO ENGINEERS SERVICES
24.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 11.00 | Set | 7070.00 | 4000.00 | 44000.00 | 1750.00 | 19250.00 | 3500.00 | 38500.00 | 11400.00 | 125400.00 | 19250.00 | METRO ENGINEERS SERVICES
25.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 60.00 | Meter | 505.00 | 280.00 | 16800.00 | 1750.00 | 105000.00 | 140.00 | 8400.00 | 204.00 | 12240.00 | 8400.00 | M/S AMAR ENTERPRISES
26.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 30.00 | Meter | 354.00 | 220.00 | 6600.00 | 125.00 | 3750.00 | 150.00 | 4500.00 | 204.00 | 6120.00 | 3750.00 | METRO ENGINEERS SERVICES
27.00 | Supply & Installation of 7-10 Watts LED Decorative Type Wall Light suitable for 240V,50Hz AC Power Supply | 20.00 | Each | 1212.00 | 650.00 | 13000.00 | 1050.00 | 21000.00 | 600.00 | 12000.00 | 1440.00 | 28800.00 | 12000.00 | M/S AMAR ENTERPRISES
| Total in Figures |  |  |  |  | 3824750.00 |  | 3959200.00 |  | 3251000.00 |  | 4813022.40
Lowest Amount Quoted BY: M/S AMAR ENTERPRISES(3251000.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of LT Panels, High Mast, Street Light alongwith other miscellaneous works at AAI Residential Colony of Ranchi Airport,Ranchi Tender ID: 2025_AAI_257680_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/S AMAR ENTERPRISES (BID ID -947963) | 3251000.00 | L1
| 2 | M/s CGPL ELECTROMECH PVT LTD (BID ID -947690) | 3824750.00 | L2
| 3 | METRO ENGINEERS SERVICES (BID ID -947863) | 3959200.00 | L3
| 4 | Virtus Techno (BID ID -941930) | 4813022.40 | L4