## BoQ1
Government eProcurement System Created By: md ansari Created Date/Time: 19-Jan-2026 01:17 PM Tender Title: Provision of Gas Based Fire Suppression System for CNS Installations in New ATC Building at Jabalpur Airport Tender ID: 2025_AAI_257896_1
Tender Inviting Authority: Sr. Manager (E-E), Airports Authority of India, Jabalpur Airport, Jabalpur.
Name of Work : Provision of Gas Based Fire Suppression System for CNS Installations in New ATC Building at Jabalpur Airport.
Tender ID - 2025_AAI_257896_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SVS Buildwel Pvt Ltd (GSTN-07AALCS7473H1ZU) BID ID -938827 |  | PYROGUARD ENGINEERS PRIVATE LIMITED (GSTN-07AACCP9466E1Z7) BID ID -948083 |  | CENTRE TAP ENGINEERING (GSTN-24AGPPP8172K1ZP) BID ID -948388 |  | advent electric technologies pvt. ltd. (GSTN-07AAJCA2055K1ZN) BID ID -948804 |  | Swastik Synergy Engineering Pvt. Ltd (GSTN-NA) BID ID -947707
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH: I -Design, Supply, Installation, Testing & Commissioning of Automatic Gas Suppression System comprising PESO approved clean agent cylinder(s) (42 bar or above) complete as per minimum materials and accessories as per SCC page no. 147 & 148 and Technical Specifications with UL/VdS approved valve assembly, supervisory switch for pressure monitoring, pressure gauge with burst disc, electronic/solenoid control head, pressure operated control head, safety cap, flexible hose, NRV, pressure switch and mounting strap; required nos. of UL/VdS listed nozzles, complete piping network and manifold designed with OEM’s UL/VdS approved software for room dimensions and pressure calculations; gas release control panel with abort and manual release stations; smoke detection system, MS pipe; 2C x 1.5 sqmm FRLS cabling, batteries and accessories; filling of clean agent FK-5-1-12 gas (zero ODP, colourless, odourless) at UL/VdS approved filling stations; including submission of OEM-approved cylinder sizing, nozzle layout, piping design and pressure calculations prior to installation – complete as required for protection of rooms of given volumes (including spaces above and below false ceiling wherever applicable). All rooms shall have independent system. 100% reserve cylinders shall be considered for equipment room of ATC building only.
1.10 | IT Server Room (G.F) : Surface Area : 17.40 Sq. Mtr., Height:CV: 1.70 Mtr., RV: 2.60 Mtr., FV:0 Mtr. Total Volume: 74.82 cub Mtr. | 1.00 | Job | 0.00 | 459002.00 | 459002.00 | 304890.00 | 304890.00 | 510000.00 | 510000.00 | 298800.00 | 298800.00 | 398000.00 | 398000.00 | 298800.00 | advent electric technologies pvt. ltd.
1.20 | FTI Room : Surface Area : 15.75 Sq. Mtr., Height:CV: 1.20 Mtr., RV: 2.77 Mtr., FV:0 Mtr. Total Volume: 62.53 cub Mtr. | 1.00 | Job | 0.00 | 451386.00 | 451386.00 | 295690.00 | 295690.00 | 480000.00 | 480000.00 | 286200.00 | 286200.00 | 383600.00 | 383600.00 | 286200.00 | advent electric technologies pvt. ltd.
1.30 | EPBAX Room : Surface Area : 14.50 Sq. Mtr., Height:CV: 1.20 Mtr., RV: 2.57 Mtr., FV:0 Mtr. Total Volume: 54.67 cub Mtr. | 1.00 | Job | 0.00 | 448530.00 | 448530.00 | 295690.00 | 295690.00 | 460000.00 | 460000.00 | 251900.00 | 251900.00 | 381800.00 | 381800.00 | 251900.00 | advent electric technologies pvt. ltd.
1.40 | IT Server Room First Floor (ATC): Surface Area : 18.00 Sq. Mtr., Height:CV: 1.70 Mtr., RV: 2.60 Mtr., FV:0 Mtr. Total Volume: 77.40 cub Mtr. | 1.00 | Job | 0.00 | 459954.00 | 459954.00 | 307190.00 | 307190.00 | 520000.00 | 520000.00 | 301600.00 | 301600.00 | 401600.00 | 401600.00 | 301600.00 | advent electric technologies pvt. ltd.
1.50 | Battery & UPS Room First Floor (ATC): Surface Area : 25.00 Sq. Mtr., Height:CV: 1.70 Mtr., RV: 2.60 Mtr., FV:0 Mtr. Total Volume: 107.50 cub Mtr. | 1.00 | Job | 0.00 | 478994.00 | 478994.00 | 329840.00 | 329840.00 | 600000.00 | 600000.00 | 332400.00 | 332400.00 | 437600.00 | 437600.00 | 329840.00 | PYROGUARD ENGINEERS PRIVATE LIMITED
1.60 | AMSS Room 2nd Floor: Surface Area : 21.60 Sq. Mtr., Height:CV: 1.20 Mtr., RV: 2.50 Mtr., FV:0 Mtr. Total Volume: 79.92 cub Mtr. | 1.00 | Job | 0.00 | 461858.00 | 461858.00 | 310290.00 | 310290.00 | 525000.00 | 525000.00 | 304400.00 | 304400.00 | 405200.00 | 405200.00 | 304400.00 | advent electric technologies pvt. ltd.
1.70 | Equipment Room 3rd Floor (ATC) (with 100% Reserve Cylinder) Surface Area : 100.00 Sq. Mtr., Height:CV: 0.60 Mtr., RV: 3.10 Mtr., FV:0 Mtr. Total Volume: 370.00 cub Mtr. | 1.00 | Job | 0.00 | 1990643.00 | 1990643.00 | 1832500.00 | 1832500.00 | 1720000.00 | 1720000.00 | 1804800.00 | 1804800.00 | 2169000.00 | 2169000.00 | 1720000.00 | CENTRE TAP ENGINEERING
1.80 | Battery Room: Surface Area : 16.20 Sq. Mtr., Height:CV: 1.20 Mtr., RV: 2.60 Mtr., FV:0 Mtr. Total Volume: 61.56 cub Mtr. | 1.00 | Job | 0.00 | 450434.00 | 450434.00 | 295690.00 | 295690.00 | 475000.00 | 475000.00 | 284800.00 | 284800.00 | 383600.00 | 383600.00 | 284800.00 | advent electric technologies pvt. ltd.
| Total in Figures |  |  |  |  | 5200801.00 |  | 3971780.00 |  | 5290000.00 |  | 3864900.00 |  | 4960400.00
Lowest Amount Quoted BY: advent electric technologies pvt. ltd.(3864900.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Gas Based Fire Suppression System for CNS Installations in New ATC Building at Jabalpur Airport Tender ID: 2025_AAI_257896_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | advent electric technologies pvt. ltd. (BID ID -948804) | 3864900.00 | L1
| 2 | PYROGUARD ENGINEERS PRIVATE LIMITED (BID ID -948083) | 3971780.00 | L2
| 3 | Swastik Synergy Engineering Pvt. Ltd (BID ID -947707) | 4960400.00 | L3
| 4 | SVS Buildwel Pvt Ltd (BID ID -938827) | 5200801.00 | L4
| 5 | CENTRE TAP ENGINEERING (BID ID -948388) | 5290000.00 | L5