## BoQ1
Government eProcurement System Created By: Vikas Kumar Tripathi Created Date/Time: 19-Jan-2026 04:43 PM Tender Title: Construction of CCCR Room at D Block, 2nd Floor, Udaan Bhawan, New Delhi. SH- Provision of Gas Based Fire Suppression System Tender ID: 2025_AAI_257916_1
Tender Inviting Authority: Senior Manager, Udaan Bhawan Safdarjung Airport, New Delhi- 110003
Name of Work: Construction of CCCR Room at D Block, 2nd Floor, Udaan Bhawan, New Delhi. SH: Provision of Gas Based Fire Suppression System.
Contract No: AAI/CHQ/SM(E-E)/e-NIT-2/2025-26
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | FIREHUT COMMERCIAL EQUIPMENT PVT LTD (GSTN-07AAACF6139L1ZG) BID ID -945672 |  | Nexus Fire And Security Systems (GSTN-07AAKFN7125K1ZY) BID ID -946341 |  | SVS Buildwel Pvt Ltd (GSTN-07AALCS7473H1ZU) BID ID -948208 |  | advent electric technologies pvt. ltd. (GSTN-07AAJCA2055K1ZN) BID ID -948807 |  | Kalpataru Industries (GSTN-NA) BID ID -948674
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing & Commissioning of Gas Suppression System consisting of Cylinder PESO Approved, complete with UL/VDS/PESO Approved valve assembly and arrangement for supervisory switch connection for monitoring cylinder pressure, a pressure gauge with a safety burst disc, electronic control head/ Solenoid, pressure operated control, head, flexible hose, strap, NRV, Pressure switch and a safety cap, required nos of Nozzles (UL/VDS listed), Piping, Manifold etc. complete as required as per following accessories.
1.01 | Seamless PESO Approved Cylinder with Valve super-pressurized with Nitrogen with capacity of 120 Ltr as per site requirement. | 5.00 | Each |  | 100575.00 | 502875.00 | 105000.00 | 525000.00 | 122939.00 | 614695.00 | 140000.00 | 700000.00 | 106500.00 | 532500.00 | 502875.00 | FIREHUT COMMERCIAL EQUIPMENT PVT LTD
1.02 | FK5-1-12 Gas UL Listed/Inert Gas with Zero ODP(Ozone Depletion Potential) | 441.00 | Kgs. |  | 1575.00 | 694575.00 | 1435.00 | 632835.00 | 2510.00 | 1106910.00 | 1400.00 | 617400.00 | 1575.00 | 694575.00 | 617400.00 | advent electric technologies pvt. ltd.
1.03 | Provision of Master Cylinder Accessories consisting of following (Complete as required) a. Electric Control Head, 24 V DC b. Discharge Hose, 2" x 31" c. Warning Sign - HFC 227ea | 4.00 | Each |  | 36450.00 | 145800.00 | 39000.00 | 156000.00 | 52091.00 | 208364.00 | 18000.00 | 72000.00 | 44450.00 | 177800.00 | 72000.00 | advent electric technologies pvt. ltd.
1.04 | Provision of End Slave Cylinder Accessories consisting of following (Complete as required) a. Pressure Operated Control Head b. Actuation Hose, 30" c. Discharge Hose, 2" x 31" d. Master Cylinder Adaptor Kit e. Male Elbow, 5/16' Flare x 1/8" NPT | 1.00 | Each |  | 26325.00 | 26325.00 | 30000.00 | 30000.00 | 32682.00 | 32682.00 | 12000.00 | 12000.00 | 28410.00 | 28410.00 | 12000.00 | advent electric technologies pvt. ltd.
1.05 | EI Check 2"(Manifold Check Valve) | 2.00 | Each |  | 8775.00 | 17550.00 | 13500.00 | 27000.00 | 22305.00 | 44610.00 | 6000.00 | 12000.00 | 14600.00 | 29200.00 | 12000.00 | advent electric technologies pvt. ltd.
1.06 | Discharge Nozzles of required size/ capacity as per site requirement | 16.00 | Nos. |  | 3645.00 | 58320.00 | 4350.00 | 69600.00 | 8027.00 | 128432.00 | 3200.00 | 51200.00 | 5150.00 | 82400.00 | 51200.00 | advent electric technologies pvt. ltd.
1.07 | Discharge Pressure Switch of required size/ capacity as per site requirement | 4.00 | Nos. |  | 5130.00 | 20520.00 | 10950.00 | 43800.00 | 9621.00 | 38484.00 | 9000.00 | 36000.00 | 10400.00 | 41600.00 | 20520.00 | FIREHUT COMMERCIAL EQUIPMENT PVT LTD
1.08 | Piping : MS seamless SCH 40 ASTM A-106 grade B with fittings & accessories complete as required as per dimensions of rooms as per site conditions. This item includes complete piping and will be measured on per cylinder basis. | 5.00 | Job/ Per Cylinder |  | 25000.00 | 125000.00 | 24200.00 | 121000.00 | 72000.00 | 360000.00 | 48000.00 | 240000.00 | 45398.00 | 226990.00 | 121000.00 | Nexus Fire And Security Systems
1.09 | Gas Inhibit Push Button Unit to shift system from auto to manual. | 4.00 | Each |  | 615.00 | 2460.00 | 1400.00 | 5600.00 | 4320.00 | 17280.00 | 1200.00 | 4800.00 | 4200.00 | 16800.00 | 2460.00 | FIREHUT COMMERCIAL EQUIPMENT PVT LTD
1.10 | Gas Manual Release Button Unit to discharge system from auto to manual. | 4.00 | Each |  | 615.00 | 2460.00 | 1400.00 | 5600.00 | 4320.00 | 17280.00 | 1200.00 | 4800.00 | 4200.00 | 16800.00 | 2460.00 | FIREHUT COMMERCIAL EQUIPMENT PVT LTD
1.11 | Conventional Smoke Detector with base complete as required. | 16.00 | Each |  | 650.00 | 10400.00 | 1300.00 | 20800.00 | 1500.00 | 24000.00 | 900.00 | 14400.00 | 1750.00 | 28000.00 | 10400.00 | FIREHUT COMMERCIAL EQUIPMENT PVT LTD
1.12 | Conventional Heat Detector with base and hardware for mounting. | 16.00 | Each |  | 625.00 | 10000.00 | 1300.00 | 20800.00 | 1500.00 | 24000.00 | 900.00 | 14400.00 | 1850.00 | 29600.00 | 10000.00 | FIREHUT COMMERCIAL EQUIPMENT PVT LTD
1.13 | Conventional hooter | 8.00 | Each |  | 475.00 | 3800.00 | 1700.00 | 13600.00 | 2940.00 | 23520.00 | 600.00 | 4800.00 | 2360.00 | 18880.00 | 3800.00 | FIREHUT COMMERCIAL EQUIPMENT PVT LTD
1.14 | Supply & Laying of 2c x 1.5 SQmm stranded Copper conductor, PVC insulated, armoured, overall PVC sheathed, FRLSH,1.1KV grade, ISI marked complete with glands, lugs, tags, clamps complete as required. | 500.00 | Mtr |  | 125.00 | 62500.00 | 98.00 | 49000.00 | 132.00 | 66000.00 | 140.00 | 70000.00 | 165.00 | 82500.00 | 49000.00 | Nexus Fire And Security Systems
1.15 | Caution sign boards Complete as required | 4.00 | Each |  | 1250.00 | 5000.00 | 2650.00 | 10600.00 | 2160.00 | 8640.00 | 600.00 | 2400.00 | 1350.00 | 5400.00 | 2400.00 | advent electric technologies pvt. ltd.
1.16 | Cylinder mounting bracket complete with clamps bolt nut. | 10.00 | Each |  | 1500.00 | 15000.00 | 1700.00 | 17000.00 | 2003.00 | 20030.00 | 400.00 | 4000.00 | 1450.00 | 14500.00 | 4000.00 | advent electric technologies pvt. ltd.
1.17 | Microprocessor based 2 Zone alarm panel with LCD display with one Area Gas Discharge module with battery charger and standby SMF battery etc complete as required. | 4.00 | Each |  | 11350.00 | 45400.00 | 13200.00 | 52800.00 | 45840.00 | 183360.00 | 18000.00 | 72000.00 | 27500.00 | 110000.00 | 45400.00 | FIREHUT COMMERCIAL EQUIPMENT PVT LTD
1.18 | Service Disconnection Switch for putting system in service mode. | 4.00 | Each |  | 17500.00 | 70000.00 | 5400.00 | 21600.00 | 9600.00 | 38400.00 | 6000.00 | 24000.00 | 15900.00 | 63600.00 | 21600.00 | Nexus Fire And Security Systems
1.19 | Manifold 2 Way | 2.00 | Each |  | 10000.00 | 20000.00 | 9000.00 | 18000.00 | 5400.00 | 10800.00 | 6000.00 | 12000.00 | 12078.00 | 24156.00 | 10800.00 | SVS Buildwel Pvt Ltd
| Total in Figures |  |  |  |  | 1837985.00 |  | 1840635.00 |  | 2967487.00 |  | 1968200.00 |  | 2223711.00
Lowest Amount Quoted BY: FIREHUT COMMERCIAL EQUIPMENT PVT LTD(1837985.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of CCCR Room at D Block, 2nd Floor, Udaan Bhawan, New Delhi. SH- Provision of Gas Based Fire Suppression System Tender ID: 2025_AAI_257916_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | FIREHUT COMMERCIAL EQUIPMENT PVT LTD (BID ID -945672) | 1837985.00 | L1
| 2 | Nexus Fire And Security Systems (BID ID -946341) | 1840635.00 | L2
| 3 | advent electric technologies pvt. ltd. (BID ID -948807) | 1968200.00 | L3
| 4 | Kalpataru Industries (BID ID -948674) | 2223711.00 | L4
| 5 | SVS Buildwel Pvt Ltd (BID ID -948208) | 2967487.00 | L5