## BoQ1
Government eProcurement System Created By: RAVICHANDRAN SEETHARAMAN Created Date/Time: 06-Jan-2026 12:19 PM Tender Title: Replacement of street light poles of approach road, existing parking area, residential colony and allied works at Salem Airport Tender ID: 2025_AAI_257950_1
Tender Inviting Authority: Asst. Gen. Manager (Engg-E). Airports Authority of India, Salem Airport, Salem- 636 309
Name of Work: Replacement of street light poles of approach road, existing parking area, residential colony and allied works at Salem Airport.
Contract No: 2025_AAI_257950_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DEEPAKELECTRICALS (GSTN-33ALUPD3531C1ZI) BID ID -949145 |  | M/s LEESHA ELECTRICALS (GSTN-27ABAPW8550C1ZK) BID ID -949777 |  | RAMESH ELECTRICALS (GSTN-NA) BID ID -946922 |  | Udaya Technologies Private Limited (GSTN-NA) BID ID -949734
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of 7 mtrs height Octagonal Hot Dip GI street light pole upto 1 mtrs long single arm bracket suitable for mounting single street light luminarie complete with base plate, J foundation bolts with template washer nuts, anchor plates, earthing stud including providing suitable RCC (1:3:6) pole foundation including excavation as per standards/OEM specifications, suitable dia heavy duty PVC pipe in foundation for cable entry and exit including providing gland plate, suitable rating MCB, terminal block including 3C x 1.5 sq.mm copper cable for interconnection from light fixture to MCB (street light pole) etc., complete as required. | 50.00 | Each |  | 13000.00 | 650000.00 | 15500.00 | 775000.00 | 13000.00 | 650000.00 | 18150.00 | 907500.00 | 650000.00 | RAMESH ELECTRICALS, DEEPAKELECTRICALS
2.00 | Supply of 45 W Street Light luminaries having, minimum lumen output of 4950 lm , system efficacy not less than 110 lumen/watt, suitable optics for uniform light distribution, integral control driver with provision opening for driver for easy maintenance, minimum 4kV surge suppressor, fitting made up of high pressure die cast aluminium/ standard alloy housing with prismatic polycarbonate secondary lens / optics with IP65 protection, suitable to operate on 230V, 50 Hz, single phase AC supply, with 5 years warrenty inline with tender specifications complete as required. | 50.00 | Each |  | 2800.00 | 140000.00 | 1850.00 | 92500.00 | 1350.00 | 67500.00 | 1791.00 | 89550.00 | 67500.00 | RAMESH ELECTRICALS
3.00 | Supply of 100 W Flood lights luminaries having, minimum lumen output of 11000 lm , system efficacy not less than 110 lumen/watt, suitable optics for uniform light distribution, integral control driver with minimum 4kV surge suppressor, fitting made up of high pressure die cast aluminium/ standard alloy suitable thermal management arrangement, toughened glass / secondary lens / optics with IP65 protection, suitable to operate on 230V, 50 Hz, single phase AC supply, hook/eye bolt for mounting the fixture with 5 years warrenty inline with technical specifications complete as required. | 12.00 | Each |  | 2700.00 | 32400.00 | 3500.00 | 42000.00 | 3550.00 | 42600.00 | 4179.00 | 50148.00 | 32400.00 | DEEPAKELECTRICALS
4.00 | Supply of 300 W Flood lights luminaries having, minimum lumen output of 33000 lm , CCT, system efficacy not less than 110 lumen/watt, suitable optics for uniform light distribution, integral control driver with minimum 4kV surge suppressor, fitting made up of high pressure die cast aluminium/ standard alloy suitable thermal management arrangement, toughened glass / secondary lens / optics with IP65 protection, suitable to operate on 230V, 50 Hz, single phase AC supply, hook/eye bolt for mounting the fixture with 5 years warrenty inline with tender specifications complete as required. | 4.00 | Each |  | 7000.00 | 28000.00 | 11000.00 | 44000.00 | 9000.00 | 36000.00 | 12035.52 | 48142.08 | 28000.00 | DEEPAKELECTRICALS
5.00 | Supply of 30 W well glass LED luminaries having, minimum lumen output of 3300 lm , CCT, system efficacy not less than 110 lumen/watt, suitable optics for uniform light distribution, integral control driver with minimum 4kV surge suppressor, fitting made up of high pressure die cast aluminium/ standard alloy housing with PC diffuser with IP65 protection, suitable to operate on 230V, 50 Hz, single phase AC supply, hook/eye bolt / cradle for mounting the fixture with 5 years warrenty inline with tender specifications complete as required. | 12.00 | Each |  | 2500.00 | 30000.00 | 1250.00 | 15000.00 | 1050.00 | 12600.00 | 1361.16 | 16333.92 | 12600.00 | RAMESH ELECTRICALS
6.00 | Supply of 20 W surface/ wall mounted 4 feet LED Tube Light Fixture with aluminium housing and integrated electronic driver complete with all accesories having minimum lumen output of 2000lm, CCT 5700 k ± 355 k suitable to operate on 230 V single phase, 50Hz AC supply in line with tender specifications with 5 years warrenty complete as required. | 20.00 | Each |  | 600.00 | 12000.00 | 550.00 | 11000.00 | 250.00 | 5000.00 | 167.16 | 3343.20 | 3343.20 | Udaya Technologies Private Limited
7.00 | Supply of hot , cold , normal water dispensor with inbuilt RO System having a total tank capacity of minimum 80 liters (Normal -35 ltrs, Hot-5 ltrs & Cold-40 ltrs), dispensing capacity of minimum 50 liter per hour, made of stainless steel body suitable for operation on single phase, 230V, 50 Hz, AC power supply with stainless steel tank, energy efficient compressor, condensor fan, heat transfer coil, thermostat and discharge of treated water in 3 faucets complete as per specifications at the locations as per the instruction of Engineer In Charge or the authorized representative of the engineering in charge.​ | 2.00 | Each |  | 126000.00 | 252000.00 | 90000.00 | 180000.00 | 95000.00 | 190000.00 | 68058.00 | 136116.00 | 136116.00 | Udaya Technologies Private Limited
8.00 | Supply, installation, testing and commissioning of 5 KVA single phase input voltage 230 V, (180 V - 270 V), 50 Hz and output voltage 230 V AC, single phase, 50 Hz, IGBT based online​ UPS with 16 Nos. 12 V, 26 AH SMF batteries to provide backup of 30 minutes along with battery rack, inter connecting cables, inline with tender specification as required. | 1.00 | Each |  | 110000.00 | 110000.00 | 125001.00 | 125001.00 | 110000.00 | 110000.00 | 97729.00 | 97729.00 | 97729.00 | Udaya Technologies Private Limited
9.00 | Supply of 2 TR capacity wall mounted type Split AC unit (5 star rating Invertor type) fitted with hermetically sealed compressor operating on 220/230 V ± 10% 50 Hz Three phase AC supply with evaporator and condensing unit made of copper tubes with alumnium fins i/c cordless remote control, copper piping for both suction and discharge of 3 metres length, power and control cabling of 3 meters length, metal frame for mounting condensing unit on wall/floor, etc complete as per specificaions complete as required. | 3.00 | Each |  | 45000.00 | 135000.00 | 49500.00 | 148500.00 | 45000.00 | 135000.00 | 44522.00 | 133566.00 | 133566.00 | Udaya Technologies Private Limited
10.00 | Installation, testing and Commissioning of 2 TR capacity wall mounted type Split AC unit inclusding all accessories as per specifications etc., complete as required. | 3.00 | Each |  | 2000.00 | 6000.00 | 1200.00 | 3600.00 | 2500.00 | 7500.00 | 2090.00 | 6270.00 | 3600.00 | M/s LEESHA ELECTRICALS
11.00 | Supply and fixing of voltage stabilisers suitable for 2 TR inverter split AC with Electromagnetic Interference Filter, excellent digital display system ensuring the connected load is always within the voltage range, surge-and-spike-protective mechanism and metal cabinet with voltage range of 170 V - 270 V suitable for single phase, 50 Hz AC supply i/c necessary fixing arrangements, clamps, screws, metal clad top, connecting 3 core cable of suitable length, complete, etc as per specifications complete as required. | 3.00 | Each |  | 1400.00 | 4200.00 | 2800.00 | 8400.00 | 4500.00 | 13500.00 | 2316.36 | 6949.08 | 4200.00 | DEEPAKELECTRICALS
12.00 | Supply and fixing of CPRI tested, ISI marked, Class A Electrical insulation mat having minimum thickness of 2mm for working voltage upto 3.3kV, confirming to IS: 15652:2006, infront of LT panels as per direction of E-I-C | 50.00 | Sq.Mtr |  | 1400.00 | 70000.00 | 550.00 | 27500.00 | 400.00 | 20000.00 | 717.59 | 35879.50 | 20000.00 | RAMESH ELECTRICALS
13.00 | Supplying and fixing of 4 Way (8+12), Double door surface/recess mounting, vertical type 415 volts, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 As tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCB's as required. | 1.00 | Each |  | 12000.00 | 12000.00 | 7500.00 | 7500.00 | 3500.00 | 3500.00 | 7971.14 | 7971.14 | 3500.00 | RAMESH ELECTRICALS
14.00 | Supplying and fixing DP sheet steel enclosure / FRP on surface / recess along with 20/25 A, 230 volts "C" curve DP MCB complete with connections, testing and commissioning etc. as required. | 2.00 | Each |  | 1200.00 | 2400.00 | 850.00 | 1700.00 | 2000.00 | 4000.00 | 1095.00 | 2190.00 | 1700.00 | M/s LEESHA ELECTRICALS
15.00 | Supplying and fixing of 63A, 415 volts, rating Four Pole MCB, "C" curve in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 1.00 | Each |  | 1450.00 | 1450.00 | 1800.00 | 1800.00 | 1850.00 | 1850.00 | 1356.29 | 1356.29 | 1356.29 | Udaya Technologies Private Limited
16.00 | Supplying and fixing of TP MCB 32A rating, 415 Volts, 10kA, "C" curve miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 2.00 | Each |  | 900.00 | 1800.00 | 1000.00 | 2000.00 | 1500.00 | 3000.00 | 2047.26 | 4094.52 | 1800.00 | DEEPAKELECTRICALS
17.00 | SITC of 12 volt, 150 AH @ C10 rating, each Lead Acid Batteries suitable to connect with the 1KWp SPV for power storage including connection, interconnections, earthing, etc., complete as required. | 8.00 | Each |  | 12500.00 | 100000.00 | 13500.00 | 108000.00 | 46500.00 | 372000.00 | 15163.80 | 121310.40 | 100000.00 | DEEPAKELECTRICALS
18.00 | Supply and fixing of outdoor type IP 65 polycarbonate box of size minimum 150 x 200 x 80 having 6 Amps MCB, 10/16 Sq.mm 4 pole connector terminal, din bar, suitable PVC gland for incoming and outgoing cables and earthing connection etc., complete as required. | 14.00 | Each |  | 1890.00 | 26460.00 | 2000.00 | 28000.00 | 500.00 | 7000.00 | 2925.30 | 40954.20 | 7000.00 | RAMESH ELECTRICALS
19.00 | Supplying and fixing of astranomical timer with contactor in the existing panel / cubicle complete as required. | 4.00 | Each |  | 4500.00 | 18000.00 | 7500.00 | 30000.00 | 6000.00 | 24000.00 | 4062.00 | 16248.00 | 16248.00 | Udaya Technologies Private Limited
20.00 | Supply of 1200 mm sweep, minimum BEE 5 star rated ceiling fans suitable for 230 volt 50 HZ Supply, with standard down rod and other accessories with out regulator etc. as required. | 20.00 | Each |  | 2300.00 | 46000.00 | 2200.00 | 44000.00 | 2185.00 | 43700.00 | 2206.00 | 44120.00 | 43700.00 | RAMESH ELECTRICALS
21.00 | Supply of 230 mm sweep, metallic heavyduty exhaust fan, minimum 1300 rpm, suitable for 230 volt 50 HZ Supply including all acessories etc. as required. | 8.00 | Each |  | 2600.00 | 20800.00 | 1600.00 | 12800.00 | 1140.00 | 9120.00 | 2000.00 | 16000.00 | 9120.00 | RAMESH ELECTRICALS
22.00 | Supply of 300 mm sweep, metallic heavyduty exhaust fan, minimum 1300 rpm, suitable for 230 volt 50 HZ Supply including all acessories etc. as required. | 2.00 | Each |  | 2736.00 | 5472.00 | 2000.00 | 4000.00 | 2415.00 | 4830.00 | 4803.00 | 9606.00 | 4000.00 | M/s LEESHA ELECTRICALS
23.00 | Supply of 400 mm sweep slient operation pedastal fan of 1350 RPM and Air delivery of 85 CMM, suitable for 230 volt 50 HZ Supply including all acessories etc. as required. | 5.00 | Each |  | 4500.00 | 22500.00 | 4500.00 | 22500.00 | 2300.00 | 11500.00 | 3310.00 | 16550.00 | 11500.00 | RAMESH ELECTRICALS
24.00 | Supply of 400 mm sweep slient operation wall mounted fan of 1350 RPM and Air delivery of 85 CMM, suitable for 230 volt 50 HZ Supply including all acessories etc. as required. | 9.00 | Each |  | 4300.00 | 38700.00 | 2150.00 | 19350.00 | 1817.00 | 16353.00 | 2582.62 | 23243.58 | 16353.00 | RAMESH ELECTRICALS
25.00 | Wiring for circuit/submain wiring along with earth wire with the following size of FRLS PVC insulated copper conductor, single core cable in surface / recessed medium class PVC conduit as required. 2X2.5 sq.mm + 1X2.5 sq.mm earth wire | 120.00 | Mtrs |  | 230.00 | 27600.00 | 220.00 | 26400.00 | 135.00 | 16200.00 | 147.33 | 17679.60 | 16200.00 | RAMESH ELECTRICALS
26.00 | Wiring for circuit/submain wiring along with earth wire with the following size of FRLS PVC insulated copper conductor, single core cable in surface / recessed medium class PVC conduit as required. 2X4 sq.mm + 1X4 sq.mm earth wire | 100.00 | Mtrs |  | 300.00 | 30000.00 | 250.00 | 25000.00 | 185.00 | 18500.00 | 221.00 | 22100.00 | 18500.00 | RAMESH ELECTRICALS
27.00 | Installation , testing and commissioning of pre-wired LED fittings of all types, complete with all accessories and tube etc., directly on ceilling / wall / Street light pole including connection and earthing etc., as required. | 78.00 | Each |  | 130.00 | 10140.00 | 120.00 | 9360.00 | 330.00 | 25740.00 | 82.31 | 6420.18 | 6420.18 | Udaya Technologies Private Limited
28.00 | Installation, testing and commissioning of ceiling fan, including wiring the down rods of length upto 30 cm with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc. as required.​ | 20.00 | Each |  | 100.00 | 2000.00 | 100.00 | 2000.00 | 300.00 | 6000.00 | 61.42 | 1228.40 | 1228.40 | Udaya Technologies Private Limited
29.00 | Installation of exhaust fan in the existing opening, including making good the damage, connection, testing, commissioning etc. as required. Upto 450 mm sweep | 10.00 | Each |  | 150.00 | 1500.00 | 200.00 | 2000.00 | 400.00 | 4000.00 | 50.15 | 501.50 | 501.50 | Udaya Technologies Private Limited
30.00 | Supply of XLPE insulated and PVC sheathed armoured aluminium conductor UG power cable of 1.1 KV grade of following sizes confirming to IS 7098(Part -1/1988) with upto date amendments etc complete as required. 2C x 16 Sqmm | 800.00 | Mtrs |  | 130.00 | 104000.00 | 160.00 | 128000.00 | 95.00 | 76000.00 | 355.81 | 284648.00 | 76000.00 | RAMESH ELECTRICALS
31.00 | Supply and Laying of 40 mm dia HDPE pipe of PE 80 PN 6 ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984 complete with fittings and cutting, jointing etc, complete as required including laying direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc. , complete as required. | 350.00 | Mtrs |  | 280.00 | 98000.00 | 180.00 | 63000.00 | 270.00 | 94500.00 | 117.85 | 41247.50 | 41247.50 | Udaya Technologies Private Limited
32.00 | Supply and Laying of 40 mm dia HDPE pipe of PE 100 PN 10 ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984 complete with fittings and cutting, jointing etc, in the existing trench/HUME pipe/Metal pipe/Road crossing complete as required. | 50.00 | Mtrs |  | 150.00 | 7500.00 | 120.00 | 6000.00 | 145.00 | 7250.00 | 138.03 | 6901.50 | 6000.00 | M/s LEESHA ELECTRICALS
33.00 | Laying of one number PVC insulated and PVC sheathed /XLPE power cable of 1.1 / 5 kV grade of following size in the existing RCC/ HUME/ DUCT/ METAL/DWC /HDPE pipe / cable trench as required. upto 35 sq.mm | 400.00 | Mtrs |  | 34.00 | 13600.00 | 25.00 | 10000.00 | 45.00 | 18000.00 | 78.80 | 31520.00 | 10000.00 | M/s LEESHA ELECTRICALS
34.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC onsulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 2C x 16 Sq.mm (22 mm) | 126.00 | Each |  | 200.00 | 25200.00 | 250.00 | 31500.00 | 200.00 | 25200.00 | 137.08 | 17272.08 | 17272.08 | Udaya Technologies Private Limited
35.00 | Earthing with G.I earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal / coke and salt as required. | 4.00 | Each |  | 8000.00 | 32000.00 | 8500.00 | 34000.00 | 13500.00 | 54000.00 | 2698.44 | 10793.76 | 10793.76 | Udaya Technologies Private Limited
36.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Mtrs |  | 300.00 | 6000.00 | 450.00 | 9000.00 | 235.00 | 4700.00 | 1219.07 | 24381.40 | 4700.00 | RAMESH ELECTRICALS
37.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or recess for connections etc. as required. | 75.00 | Mtrs |  | 120.00 | 9000.00 | 150.00 | 11250.00 | 130.00 | 9750.00 | 152.83 | 11462.25 | 9000.00 | DEEPAKELECTRICALS
38.00 | Earthing with G.I. earth pipe 4.5 meter long, 40 mm dia including accessories, and providing masonry enclosure with FRP cover plate of mini 2.5 ton capacity, 18x18 mini size and watering pipe etc. with charcoal/ coke and salt as required. | 4.00 | Each |  | 6500.00 | 26000.00 | 9500.00 | 38000.00 | 9000.00 | 36000.00 | 2179.05 | 8716.20 | 8716.20 | Udaya Technologies Private Limited
39.00 | Providing and laying 6 SWG dia G.I. wire on surface or in recess for loop earthing including connection/ termination with GI thimble etc. as required. | 500.00 | Mtrs |  | 45.00 | 22500.00 | 22.00 | 11000.00 | 23.00 | 11500.00 | 58.51 | 29255.00 | 11000.00 | M/s LEESHA ELECTRICALS
40.00 | Dismantaling of existing old street light pole including necessary excavation and disconnecting the cables etc., complete and handing over to AAI store as required. | 42.00 | Each |  | 1000.00 | 42000.00 | 500.00 | 21000.00 | 700.00 | 29400.00 | 1268.63 | 53282.46 | 21000.00 | M/s LEESHA ELECTRICALS
| Total in Figures |  |  |  |  | 2222222.00 |  | 2181661.00 |  | 2227293.00 |  | 2402580.74
Lowest Amount Quoted BY: M/s LEESHA ELECTRICALS(2181661.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of street light poles of approach road, existing parking area, residential colony and allied works at Salem Airport Tender ID: 2025_AAI_257950_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s LEESHA ELECTRICALS (BID ID -949777) | 2181661.00 | L1
| 2 | DEEPAKELECTRICALS (BID ID -949145) | 2222222.00 | L2
| 3 | RAMESH ELECTRICALS (BID ID -946922) | 2227293.00 | L3
| 4 | Udaya Technologies Private Limited (BID ID -949734) | 2402580.74 | L4