## BoQ1
Government eProcurement System Created By: Mukesh Meena Created Date/Time: 28-Jan-2026 06:04 PM Tender Title: Replacement of Precision ACs at ATC Sky Tower, Mumbai Tender ID: 2025_AAI_257985_1
Tender Inviting Authority: Asstt.General Manager (Engg.-Elect.), ATS Complex, Mumbai.
Name of Work: "Replacement of Precision ACs at ATC Sky Tower, Mumbai”
Contract No: MUMBAI/ATS/ENGG-E/eNIT-03/2025-26
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Weartech Engineers Pvt Ltd (GSTN-23AABCW1561C1ZV) BID ID -950093 |  | NETWORK TECHLAB INDIA LIMITED (GSTN-NA) BID ID -945518
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH :- A : S.I.T.C. of P.A.C.
2.00 | Supply of following capacity Floor Mounted, Air Cooled type Precision Air Conditioners. The Indoor units shall comprise of stepless variable capacity Digital/Inverter scroll compressor, Min. Two Sided Double skin side panels, with Class "O" Glasswool insulation, Top discharge type complete with dynamically balanced composite material fan driven by Electronically Commutated (EC) motor, hydrophilic coated slant/flat cooling coil. The unit shall be equipped with high efficiency filters(G4), micro processor based programmable logic controller, Liquid receiver, Expansion Valve, Drivers, suction and discharge piping, Internal power & control wiring, Water leak detector sensor, SS drain tray with nitrile rubber insulation, Stainless steel strip Heater, Infrared steam humidifier, Power and Control contactors and Other Electrical accessories. Provision to communicate with the BMS monitoring system through RS 485 communications protocol. The Outdoor Condenser units shall comprise of Condenser fans & motor, Condenser cooling coil with anti-corrosive coating (Copper coil with aluminium fins), Fan speed controller, Isolater switch The outdoor unit shall be selected at min. 45 Deg C of ambient temperatures with R-410A Refrigerant Gas. The units shall be suitable for operation on 415 Volts, 50 Hz, 3 Phase, 4 Wire AC supply. Each unit should be having individual display panel, which shall display date, time, actual & set values, operating conditions, signal faults, collective faults, limiting values and unit wellness alarm / service alarm to reduce the down time and unit memory shall hold the 400 most recent events with ID number, time and date stamp for each event. Operational & Control Features - Supply Air Set points & Operational Capabilities: 18-20 Deg.C +/- 2 Deg.C, 40% to 70% RH - Return Air Set points & Operational Capabilities: 22 Deg.C to 38 Deg C, 20% to 60% RH - P / PI / PID - All three Control logics for temperature control - Relative / Compensated / Predictive method for humidity control - Temperature & Humidity graphs for the system (Avg. value of all the connected units) & for each single unit - Record of Peak & Low temperature/humidity of the current day - Display shows SET / ACTUAL / SET+ACTUAL Values - Records total run hours for all main components - Team Mode operation for synchronising all machines in room without any external controller - Sequencing & Stand-by rotation - Cascading, Lead-Lag functions - Min. 16 days record of controlled parameters - Unit memory shall hold min. 200 recent alarms with date and time for each alarm - Status report of last 400 event logs - 3 types of access; User, Service & Advanced to protect all settings - Auto restart after a power failure - Graphical display of status of operation of all major components like Compressor, Fan, Heater & Humidifier on screen in an idle mode
3.00 | 11.5 TR Top discharge and back return Total cooling capacity with minimum airflow of 10000 CMH, at minimum 20 Pa ESP, Return Air as temperature at 26 +/-2 Deg C DB & 45% +/-5 RH (Non Condensing). (Note : The Supply of PAC Units followed by its installation are to be carried in the ATC Sky Tower,Vile Parle, Mumbai. Required Tools, Machinary, permissions, Passes, etc. are to be arranged by the Agency) | 3.00 | Each |  | 1544000.00 | 4632000.00 | 1061500.00 | 3184500.00 | 3184500.00 | NETWORK TECHLAB INDIA LIMITED
4.00 | 9.3 TR (or Equivalent) Top discharge and Front return Total cooling capacity with minimum airflow of 8000 CMH, at minimum 20 Pa ESP, Return Air as temperature at 28 +/-2 Deg C DB & 45% +/-5 RH (Non Condensing). (Note : The Supply of PAC Units followed by its installation are to be carried in the ATC Sky Tower,Vile Parle, Mumbai. Required Tools, Machinary, permissions, Passes, etc. are to be arranged by the Agency) | 2.00 | Each |  | 1496000.00 | 2992000.00 | 1028500.00 | 2057000.00 | 2057000.00 | NETWORK TECHLAB INDIA LIMITED
5.00 | Installation, testing, and commissioning of 11.5 TR capacity Floor Mounted, Top discharge and back return type Air Cooled type Precision Air Condtioners including supply & fixing suitable adjutable GI/MS stands with rubber pad for each outdoor unit to dimension as specified / recommendation of O.E.M. (for Indoor and Outdoor units) including wiring, connection & interconnection making suitable for operation complete as required. Provision of Suitable Outdoor stand as per site including civil work if required for fixing of the stand. (Note the Work is to be carried out in ATC Sky Tower of C.S.M.I. Airport, Mumbai with restricted acess and working time) | 3.00 | Each |  | 67113.00 | 201339.00 | 50000.00 | 150000.00 | 150000.00 | NETWORK TECHLAB INDIA LIMITED
6.00 | Installation, testing, and commissioning of 9.3 TR capacity Floor Mounted, Top discharge and front return type Air Cooled type Precision Air Condtioners including supply & fixing suitable adjutable GI/MS stands with rubber pad for each outdoor unit to dimension as specified / recommendation of O.E.M. (for Indoor and Outdoor units) including wiring, connection & interconnection making suitable for operation complete as required. Provision of Suitable Outdoor stand as per site including civil work if required for fixing of the stand. (Note the Work is to be carried out in ATC Sky Tower of C.S.M.I. Airport, Mumbai with restricted acess and working time) | 2.00 | Each |  | 67113.00 | 134226.00 | 50000.00 | 100000.00 | 100000.00 | NETWORK TECHLAB INDIA LIMITED
7.00 | Supply, installation, testing of 18 SWG hard drawn copper refrigerant piping of sizes as per O.E.M. standard with insulation for precision units with proper "U" traps in piping for required length. All refrigerant piping along within conditioned space shall be provided with 9mm Class '0' Nitril Rubber insulation while rest pipework shall be provided with Nitrile Rubber Insulation & Anticorrosive coating and supports, between indoor and outdoor units. Each running meter of one circuit includes one meter of copper pipe (inlet & outlet), necessary supports, fittings, insulation, Thermogaurd coating, etc. and should connect the indoor to the outdoor as per locations. (Including extension kit if required) | 130.00 | Meter |  | 4268.00 | 554840.00 | 3000.00 | 390000.00 | 390000.00 | NETWORK TECHLAB INDIA LIMITED
8.00 | Supply & Installation of Motorized Damper with Actuator (of sufficient torque) & necessary control cablings for ON/OFF operation by interfacing with indoor unit operation and to be installed on indoor machines on Return Air path. | 5.00 | Each |  | 36145.00 | 180725.00 | 21500.00 | 107500.00 | 107500.00 | NETWORK TECHLAB INDIA LIMITED
9.00 | Sequencing & logic control necessary timers and logic control for automatic start-stop of the unit.with necessary timers and logic control for automatic start-stop of the unit.Logic should include orderly restart after power failure | 5.00 | Lot |  | 1813.00 | 9065.00 | 1500.00 | 7500.00 | 7500.00 | NETWORK TECHLAB INDIA LIMITED
10.00 | Supply and fixing Perforated GI trays (With maximum 50% perforation) with necessary support and covertop for Refrigerant Pipes of of following Size in (mm) (Provision of clamp/fixing arrangement are to be provided for the vertical sections)
11.00 | Width 300 mm. x Height 75 mm. x thickness 1.0 mm. | 80.00 | Meter |  | 1835.00 | 146800.00 | 1350.00 | 108000.00 | 108000.00 | NETWORK TECHLAB INDIA LIMITED
12.00 | Width 150 mm. x Height 50 mm. x thickness 0.7 mm. | 20.00 | Meter |  | 969.00 | 19380.00 | 800.00 | 16000.00 | 16000.00 | NETWORK TECHLAB INDIA LIMITED
13.00 | Supply & Installation of following size GI Class "B" Drain Pipe with 9 mm thickness Nitrile rubber insulation with including all accessories complete as required 40 mm. dia. | 20.00 | Meter |  | 1206.00 | 24120.00 | 1000.00 | 20000.00 | 20000.00 | NETWORK TECHLAB INDIA LIMITED
14.00 | Supply and laying of 3C x 2.5 Sq.mm. Cu. Flexible cable (Indoor to outdoor unit) on existing cable tray or surface as directed by EIC | 140.00 | Meter |  | 352.00 | 49280.00 | 350.00 | 49000.00 | 49000.00 | NETWORK TECHLAB INDIA LIMITED
15.00 | Supply & charging of Refrigerant Gas (R-410A / 407C) for the compressor for the 100 % rating and equivalent copper pipe length between Indoor & Outdoor Unit along with required oil for commisioning | 175.00 | Kg |  | 1666.00 | 291550.00 | 1300.00 | 227500.00 | 227500.00 | NETWORK TECHLAB INDIA LIMITED
16.00 | Supply and laying of Size 4C x 16Sqmm. armoured Copper cable from Incoming Isolator Panel to Indoor Unit on existing cable tray or surface as directed by EIC. | 75.00 | Meter |  | 1463.00 | 109725.00 | 1250.00 | 93750.00 | 93750.00 | NETWORK TECHLAB INDIA LIMITED
17.00 | SH :- B : Ducting and dismantling
18.00 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required thick ness 0.8 mm. (22G) | 50.00 | Sq.Mtr. |  | 2703.00 | 135150.00 | 1850.00 | 92500.00 | 92500.00 | NETWORK TECHLAB INDIA LIMITED
19.00 | Dismantling of Existing 11.3 TR floor mounted PAC units (IDU and ODU) from 20/21st Floor and Transporting of the same to ATS Complex (approx. 6km). All Required Tools & plants, Vehicle with driver, Labour for loading and unloading, etc.. | 3.00 | No. |  | 20400.00 | 61200.00 | 12500.00 | 37500.00 | 37500.00 | NETWORK TECHLAB INDIA LIMITED
20.00 | Dismantling of Existing 9.3 TR floor mounted Package Unit from ATC Tower from 19/20th Floor and Transporting of the same to ATS Complex (approx. 6km). All Required Tools & plants, Vehicle with driver, Labour for loading and unloading etc.. | 2.00 | No. |  | 18700.00 | 37400.00 | 11000.00 | 22000.00 | 22000.00 | NETWORK TECHLAB INDIA LIMITED
21.00 | SH-II :- (A.I.C.M.C. - All Inclusive Comprehensive Maintenance Contract)
22.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 5 Nos. (03 nos. 11.5 TR and 02 Nos. 9.3 TR) above work after completion of defect liability period of one year. The scope of work during CMC Period shall be as per technical specifications. For First Year | 12.00 | Month |  | 50385.39 | 604624.68 | 35103.79 | 421245.48 | 421245.48 | NETWORK TECHLAB INDIA LIMITED
23.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 5 Nos. (03 nos. 11.5 TR and 02 Nos. 9.3 TR) above work after completion of defect liability period of one year. The scope of work during CMC Period shall be as per technical specifications. For Second Year | 12.00 | Month |  | 52904.66 | 634855.92 | 36858.98 | 442307.76 | 442307.76 | NETWORK TECHLAB INDIA LIMITED
24.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 5 Nos. (03 nos. 11.5 TR and 02 Nos. 9.3 TR) above work after completion of defect liability period of one year. The scope of work during CMC Period shall be as per technical specifications. For Third Year | 12.00 | Month |  | 55549.89 | 666598.68 | 38701.93 | 464423.16 | 464423.16 | NETWORK TECHLAB INDIA LIMITED
25.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 5 Nos. (03 nos. 11.5 TR and 02 Nos. 9.3 TR) above work after completion of defect liability period of one year. The scope of work during CMC Period shall be as per technical specifications. For Fouth Year | 12.00 | Month |  | 58327.38 | 699928.56 | 40637.03 | 487644.36 | 487644.36 | NETWORK TECHLAB INDIA LIMITED
26.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 5 Nos. (03 nos. 11.5 TR and 02 Nos. 9.3 TR) above work after completion of defect liability period of one year. The scope of work during CMC Period shall be as per technical specifications. For Fifth Year | 12.00 | Month |  | 61243.75 | 734925.00 | 42668.88 | 512026.56 | 512026.56 | NETWORK TECHLAB INDIA LIMITED
| Total in Figures |  |  |  |  | 12919732.84 |  | 8990397.32
Lowest Amount Quoted BY: NETWORK TECHLAB INDIA LIMITED(8990397.32)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Precision ACs at ATC Sky Tower, Mumbai Tender ID: 2025_AAI_257985_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | NETWORK TECHLAB INDIA LIMITED (BID ID -945518) | 8990397.32 | L1
| 2 | Weartech Engineers Pvt Ltd (BID ID -950093) | 12919732.84 | L2