## BoQ1
Government eProcurement System Created By: Ambrish Singh Created Date/Time: 20-Jan-2026 12:44 PM Tender Title: Construction of New Terminal Building at LBSI Airport Varanasi. SH- Interconnection of ESS (Electrical Substation of New Terminal Building) and NPH (New Power House of Existing Terminal Building) Tender ID: 2025_AAI_258358_1
Tender Inviting Authority: Airports Authority of India
Name of work: Construction of New Terminal Building at LBSI Airport Varanasi. SH: Interconnection of ESS (Electrical Substation of New Terminal Building) & NPH (New Power House of Existing Terminal Building).
Contract No: : 2025_AAI_258358_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M/s. CHANDRA REDDY ELECTRICALS (GSTN-37ALMPK9299A1ZM) BID ID -951743 |  | HIMALAYA GENERATORS (GSTN-09AEDPA0988G1ZL) BID ID -952233 |  | ELECTROCONTROL INDIA (GSTN-09AHCPK0197K1Z4) BID ID -952726 |  | Choubay And Co.(Agencies) Pvt.Ltd. (GSTN-09AAACC6073E1ZT) BID ID -953123 |  | K B CONTRACT (P) LTD (GSTN-07AADCK6091P1ZX) BID ID -953447 |  | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -953605 |  | BUDHIRAJA ELECTRICALS (GSTN-NA) BID ID -952003
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of indoor cubicle type floor mounted metal clad 36KV VCB Panel Board with 36 KV, 1500MVA , 630A, HT VCB,totally enclosed & fully interlocked, horizontal draw out, horizontal / vertical Isolation type breaker as per IEC 62271-100 for breaker & 62271-200 for panels and of capacity as mentioned below, single break, trip free mechanism, motor / manually charged and auto / manual closing breaker suitable for use on 33KV, 3 phase 50 Hz AC supply complete with self contained, fully interlocked, rack in and rackout mechanism, air insulated but encapsulated copper bus bars of 800 Amp capacity, Breaker featured with mechanical ON/OFF indication with hand trip device, with DC power pack, spring released coil, shunt trip coil and auxiliary switchs, with Electrical & Mechanical Interlocking between I/Cs and Bus Coupler and equipped with switchgears mentioned below. Panel Board shall be provided with Earthing troley for incoming side / Busbar / outgoing breakers earthing, Panel Board shall be fabricated, made out of 2 mm thick CRCA sheet steel, totally enclosed, IP 4X, free standing, floor mounting, dust and vermin proof ,indoor, compartmentalized, powder coated painting including internally wired / interconnected with suitable provision for end termination with heat shrinkable jointing material etc as required (Note cost of end termination not included in this item) Note: The work shall be done on existing system. All the arrangements need to be considered for commissioning of the Panel with existing Transformers and O/G feeders. VCBs shall be SCADA compatible & shall have feature for control & monitoring by SCADA system/ BMS in future.(Cost of SCADA system not included in this item). Incomer & Bus-Coupler (a) 630A,1500MVA(f), 33KV, 3 phase, 50 Hz Vacuum Circuit Breaker(VCB),Icu=Ics=Icw=100% and withstand capacity of 3 seconds. - Total 3 Nos. (2+1) (b) 3 phase 33 KV/110 Volts PT, class 0.5 accuracy and 100 VA burden with 1 No Voltmeter (0-35 KV), Digital type, selector switch for voltmeter and protection fuses for HT metering upto 35 KV on incomer (Voltmeter shall have communication features for monitoring by BMS) - For each Incomers (c) Dual core 3 CTs 60/30/5+5A of 15 VA burden and accuracy class 0.5 for metering and class 5P10 for protection-For each Incomers (d ) Multi function meter to display F, PF, kW, kVA, kVAR, kWh, kVAh, kVARh, THD, Phase angles, Power demand parameters, suitable for operation on 110V a.c supply, with RS-485 interface for integration to BMS-For each Incomers (e ) Digital Tri Vector Meter/ Energy Meter (Trivector meter shall have communication features for monitoring by BMS)- For each Incomers (f) Microprocessor based numerical relay for Over current and Earth fault protection -For each Incomers (g) 0-50 Amps Ammeter, digital type with selector switch for ammeters. (ammeter shall have communication features for monitoring by BMS) -For each Incomers (h) Phase indicating lamps with HRC fuses/MCB-For each Incomers (i) Indicating lamps to indicate OPEN, CLOSE, TRIP, SPRING CHARGED, TRIP CIRCUIT HEALTHY-For each Incomers and B/C (j) 800 Amps TP Copper Busbar, Hooter located at B/C panel (k) Test terminal block-For each Incomers (l) Trip/Neutral/close and L/R switch- For each Incomers and B/C (m) Copper bus bar of suitable size for earthing (n) Master trip relay & trip circuit healthy supervision relay.-For each Incomers (o) Provision for padlocking the incomer VCBs in 'OFF' position.-For each Incomers and B/C (p) Surge protector of suitable rating- 1 No for each I/C VCBs (q) Mushroom Head Stay Put Type Emergency Push Button- 3 Sets Outgoing (a) 630A,1500MVA, 33KV, 3 phase, 50 Hz Vacuum Circuit Breaker(VCB),Icu=Ics=Icw=100% and withstand capacity of 3 seconds. -5 No.s (4 Tranformer+1 Feeder O/Gs) (b) 3 phase 33 KV/110 Volts PT, class 1.0 accuracy and 100 VA burden with 1 No Voltmeter (0-35 KV), Digital type, selector switch for voltmeter and protection fuses for HT metering upto 35 KV on incomer (Voltmeter shall have communication features for monitoring by BMS) - 1 set for each VCB (c) Dual core 3 CTs 60/30/5+5A of 15 VA burden and accuracy class 1.0 for metering and class 5P10 for protection-1 set for each VCB (d) Multi function meter to display F, PF, kW, kVA, kVAR, kWh, kVAh, kVARh, THD, Phase angles, Power demand parameters, suitable for operation on 110V a.c supply, with RS-485 interface for integration to BMS- 1 No for each VCB (e) Microprocessor based numerical relay for O/C and E/F protection-1 No for each VCB (For all O/G feeders) (f) 0-50 Amp, digital type ammeter with selector switch (ammeter shall have communication features for monitoring by BMS)- 1 No for each VCB (g) Indicating lamps to indicate OPEN, CLOSE, TRIP, SPRING CHARGED, TRIP CIRCUIT HEALTHY- 1 set for each VCB (h) Trip/Neutral/close switch-1 No for each VCB (i) Master trip relay & trip circuit healthy supervision relay-1 Set for each VCB (j) Protection arrangements (87 or 64R) with necessary auxiliary relays for connecting the WTI, OTI, Buchholz Relay and PRV of Existing Transformer- 1set for each transformer O/G feeders only (k) Annunciator (having minimum 8 windows) and alarm bell/ hooter - 1 No. for each VCB (l) Surge protector of suitable rating- 1 No for each Transformer Feeders (m) Mushroom Head Stay Put Type Emergency Push Button- For each panels NOTE:-All metering and protection devices, interconnections, necessary control wiring and all other accessories shall be provided as per SLD or as required as per specifications and technical particulars and as per instruction of E-I-C. | 1.00 | Each |  | 9180176.00 | 9180176.00 | 9752000.00 | 9752000.00 | 7882000.00 | 7882000.00 | 10730000.00 | 10730000.00 | 6750000.00 | 6750000.00 | 6200000.00 | 6200000.00 | 1090000.00 | 1090000.00 | 1090000.00 | BUDHIRAJA ELECTRICALS
2.00 | Supply of Earthed aromured, stranded compacted circular Aluminium Conductor, conductor screen with extruded semi-conducting compound, XLPE insulated, insulation screening with extruded semi conducting compound in combination with copper tape, core laid up, innersheath of PVC, galvanised steel flat strip armoured, & overall PVC sheathed Cable, with FRLS PVC outer sheath for 33kV grade confirming to IS 7908 (Part-II), ammended upto date etc. as required.of following size: 3C X 300 Sq.mm | 1500.00 | Metre |  | 2369.00 | 3553500.00 | 3020.00 | 4530000.00 | 3000.00 | 4500000.00 | 3040.00 | 4560000.00 | 2520.00 | 3780000.00 | 3950.00 | 5925000.00 | 2830.00 | 4245000.00 | 3553500.00 | M/s. CHANDRA REDDY ELECTRICALS
3.00 | Laying of one number XLPE power cable of 33 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required: Above 120 sq. mm and upto 400 sq. mm | 1500.00 | Metre |  | 120.00 | 180000.00 | 30.00 | 45000.00 | 250.00 | 375000.00 | 80.00 | 120000.00 | 135.00 | 202500.00 | 300.00 | 450000.00 | 210.00 | 315000.00 | 45000.00 | HIMALAYA GENERATORS
4.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 Core, XLPE aluminium conductor cable of 33 KV grade as required 3CX300 sqmm | 4.00 | Each |  | 10000.00 | 40000.00 | 7500.00 | 30000.00 | 12000.00 | 48000.00 | 7000.00 | 28000.00 | 9000.00 | 36000.00 | 21000.00 | 84000.00 | 10500.00 | 42000.00 | 28000.00 | Choubay And Co.(Agencies) Pvt.Ltd.
5.00 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 core, XLPE aluminium conductor cable of 33 KV grade as required : 3CX300 sqmm | 2.00 | Each |  | 15000.00 | 30000.00 | 10000.00 | 20000.00 | 31000.00 | 62000.00 | 19000.00 | 38000.00 | 22500.00 | 45000.00 | 35000.00 | 70000.00 | 30100.00 | 60200.00 | 20000.00 | HIMALAYA GENERATORS
6.00 | Supply of XLPE insulated and PVC sheathed aluminium conductor armoured cable of 1.1 KV grade conforming to IS 7098 (Par : -I)/1988 with upto date amendments etc.,as required.of following size: 3.5C X 400 Sq.mm | 3000.00 | Metre |  | 1812.00 | 5436000.00 | 2400.00 | 7200000.00 | 2050.00 | 6150000.00 | 2375.00 | 7125000.00 | 1710.00 | 5130000.00 | 2150.00 | 6450000.00 | 1670.00 | 5010000.00 | 5010000.00 | BUDHIRAJA ELECTRICALS
7.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required: Above 185 sq. mm and upto 400sqmm | 3000.00 | Metre |  | 100.00 | 300000.00 | 30.00 | 90000.00 | 200.00 | 600000.00 | 80.00 | 240000.00 | 135.00 | 405000.00 | 250.00 | 750000.00 | 170.00 | 510000.00 | 90000.00 | HIMALAYA GENERATORS
8.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 400 sq. mm (82 mm) | 8.00 | Each |  | 3000.00 | 24000.00 | 1000.00 | 8000.00 | 2000.00 | 16000.00 | 3000.00 | 24000.00 | 1260.00 | 10080.00 | 1500.00 | 12000.00 | 1600.00 | 12800.00 | 8000.00 | HIMALAYA GENERATORS
9.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 400 sq. mm | 4.00 | Each |  | 7500.00 | 30000.00 | 2500.00 | 10000.00 | 6000.00 | 24000.00 | 5500.00 | 22000.00 | 4500.00 | 18000.00 | 6000.00 | 24000.00 | 6100.00 | 24400.00 | 10000.00 | HIMALAYA GENERATORS
10.00 | Supplying and making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 10cm including inscription duly engraved as required. | 30.00 | Each |  | 650.00 | 19500.00 | 500.00 | 15000.00 | 700.00 | 21000.00 | 1000.00 | 30000.00 | 900.00 | 27000.00 | 550.00 | 16500.00 | 690.00 | 20700.00 | 15000.00 | HIMALAYA GENERATORS
11.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) includingexcavation and refilling the trench but excluding sand cushioning and protective covering etc., complete asrequired. 160 mm dia (OD-160 mm & ID-135 mm nominal) | 750.00 | Metre |  | 316.00 | 237000.00 | 250.00 | 187500.00 | 600.00 | 450000.00 | 400.00 | 300000.00 | 405.00 | 303750.00 | 750.00 | 562500.00 | 375.00 | 281250.00 | 187500.00 | HIMALAYA GENERATORS
12.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. in the existing trench, complete as required. 160 mm dia (OD-160 mm & ID-135 mm nominal) | 2250.00 | Metre |  | 266.00 | 598500.00 | 160.00 | 360000.00 | 400.00 | 900000.00 | 250.00 | 562500.00 | 360.00 | 810000.00 | 550.00 | 1237500.00 | 270.00 | 607500.00 | 360000.00 | HIMALAYA GENERATORS
13.00 | SITC of Cylinderless Clean Agent based ( Zero global warming potential ) Fire Suppression systems, suitable for extinguishing, electrical enclosed panel, fire by automatically triggering the thermo-activated micro capsules of aerosol forming soild compound ( minimum 100 gm aerosol for 1 cum panel space) or equivalent compound with cord minimum 3.5 Mtr for 1 cum panel space activated at 120-175 Degree C temperature(as per requirement of compartment of the panel),in each compartment of the panel conforming to relevant IS and CPWD norms.The system has to be Maintenance free and without any pressurized cylinder,tube, pressure gauge as required.Make and material of Fire Suppression systems required prior approval of EIC. | 50.00 | Cum |  | 14800.00 | 740000.00 | 1000.00 | 50000.00 | 34500.00 | 1725000.00 | 7200.00 | 360000.00 | 23400.00 | 1170000.00 | 11000.00 | 550000.00 | 65000.00 | 3250000.00 | 50000.00 | HIMALAYA GENERATORS
14.00 | Providing of set of 4 Nos. 9.5 Litre capacity GI bucket painted in post office red colour with prior coat of red oxide paint and written with white paint ‘FIRE’ and mounted on MS angle iron frame with bracket of appropriate size & capacity I/c filling sand etc. | 4.00 | Set |  | 4875.00 | 19500.00 | 500.00 | 2000.00 | 310.00 | 1240.00 | 3500.00 | 14000.00 | 6300.00 | 25200.00 | 4500.00 | 18000.00 | 4050.00 | 16200.00 | 1240.00 | ELECTROCONTROL INDIA
15.00 | First aid box as approved by St. John Ambulance Brigade /Indian Red Cross society conforming to IS : 2217 - 1963. | 2.00 | No. |  | 5392.00 | 10784.00 | 300.00 | 600.00 | 1500.00 | 3000.00 | 3000.00 | 6000.00 | 2700.00 | 5400.00 | 4000.00 | 8000.00 | 1700.00 | 3400.00 | 600.00 | HIMALAYA GENERATORS
16.00 | Shock treatment chart duly mounted on a wooden frame with glass on, as required in 2 languages (Hindi & English). | 2.00 | No. |  | 740.00 | 1480.00 | 100.00 | 200.00 | 500.00 | 1000.00 | 1300.00 | 2600.00 | 2700.00 | 5400.00 | 1000.00 | 2000.00 | 1600.00 | 3200.00 | 200.00 | HIMALAYA GENERATORS
17.00 | Providing and fixing M.V. danger notice plate of 200 mm X 150 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 3.00 | No. |  | 700.00 | 2100.00 | 150.00 | 450.00 | 200.00 | 600.00 | 300.00 | 900.00 | 450.00 | 1350.00 | 800.00 | 2400.00 | 280.00 | 840.00 | 450.00 | HIMALAYA GENERATORS
18.00 | Providing and fixing H.T. danger notice plate of 250 mm X 200 mm, made of mild steel, at least 2 mm thick, and vitreous enameled white on both sides, and with inscription in single red colour on front side as required. | 3.00 | No. |  | 700.00 | 2100.00 | 150.00 | 450.00 | 500.00 | 1500.00 | 500.00 | 1500.00 | 540.00 | 1620.00 | 800.00 | 2400.00 | 280.00 | 840.00 | 450.00 | HIMALAYA GENERATORS
19.00 | Supply and fixing of high voltage synthetic insulating mat made of synthetic Elastomer suitable for upto 3.3 KV conforming to IS 15652:2006 with minimum width of 1 metre and thickness of 2.0 mm +/- 10 % (Class-A). Insulating mat should be flexible , anti skid, fire reatrdant, water and moisture proof with no adverse effect of acids,alkalies and transformer oil. Insulating mat should be fixed with suitable adhesive/chemibond , resin,water proofing compound and other sealing materials as per specifications. Insulating mats should be ISI marked alongwith CM/L nos at every meter. | 75.00 | sqm |  | 1105.00 | 82875.00 | 350.00 | 26250.00 | 720.00 | 54000.00 | 1650.00 | 123750.00 | 2250.00 | 168750.00 | 1000.00 | 75000.00 | 1000.00 | 75000.00 | 26250.00 | HIMALAYA GENERATORS
20.00 | Supply and fixing of high voltage synthetic insulating mat made of synthetic Elastomer suitable for upto 11 KV conforming to IS 15652:2006 with minimum width of 1 metre and thickness of 2.5 mm +/- 10 % (Class-B). Insulating mat should be flexible , anti skid, fire reatrdant, water and moisture proof with no adverse effect of acids,alkalies and transformer oil. Insulating mat should be fixed with suitable adhesive/chemibond , resin,water proofing compound and other sealing materials as per specifications. Insulating mats should be ISI marked alongwith CM/L nos at every meter. | 75.00 | sqm |  | 1215.00 | 91125.00 | 400.00 | 30000.00 | 900.00 | 67500.00 | 2075.00 | 155625.00 | 2700.00 | 202500.00 | 1200.00 | 90000.00 | 1200.00 | 90000.00 | 30000.00 | HIMALAYA GENERATORS
21.00 | Supply and fixing of high voltage synthetic insulating mat made of synthetic Elastomer suitable for upto 33 KV conforming to IS 15652:2006 with minimum width of 1 metre and thickness of 3.0 mm +/- 10 % (Class-C). Insulating mat should be flexible , anti skid, fire reatrdant, water and moisture proof with no adverse effect of acids,alkalies and transformer oil. Insulating mat should be fixed with suitable adhesive/chemibond , resin,water proofing compound and other sealing materials as per specifications. Insulating mats should be ISI marked alongwith CM/L nos at every meter. | 50.00 | sqm |  | 1298.00 | 64900.00 | 450.00 | 22500.00 | 1100.00 | 55000.00 | 2450.00 | 122500.00 | 3060.00 | 153000.00 | 1500.00 | 75000.00 | 1350.00 | 67500.00 | 22500.00 | HIMALAYA GENERATORS
22.00 | Supply of Rubber gloves of 33KV grade as per IS 4770-68 etc. complete as required. | 1.00 | Pair |  | 1705.00 | 1705.00 | 500.00 | 500.00 | 2500.00 | 2500.00 | 500.00 | 500.00 | 1260.00 | 1260.00 | 1500.00 | 1500.00 | 1200.00 | 1200.00 | 500.00 | HIMALAYA GENERATORS, Choubay And Co.(Agencies) Pvt.Ltd.
23.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. With charcoal/coke and salt as required. | 2.00 | Each |  | 7000.00 | 14000.00 | 5000.00 | 10000.00 | 3000.00 | 6000.00 | 6500.00 | 13000.00 | 7200.00 | 14400.00 | 10000.00 | 20000.00 | 7000.00 | 14000.00 | 6000.00 | ELECTROCONTROL INDIA
24.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 70.00 | Metre |  | 150.00 | 10500.00 | 70.00 | 4900.00 | 200.00 | 14000.00 | 225.00 | 15750.00 | 180.00 | 12600.00 | 800.00 | 56000.00 | 210.00 | 14700.00 | 4900.00 | HIMALAYA GENERATORS
| Total in Figures |  |  |  |  | 20669745.00 |  | 22395350.00 |  | 22959340.00 |  | 24595625.00 |  | 19278810.00 |  | 22681800.00 |  | 15755730.00
Comparative Chart(eAuction)
Sl.No | Bidder Name | Auction Start Price | Quoted Rate in Figures and Words (Iteration 0)
|  |  | Bidder Price | Amount in Words
1 | Manish Electricals (BID ID -953605) | 15755730.00 | 15676730.00 | One Crore Fifty Six Lakh Seventy Six Thousand Seven Hundred and Thirty
2 | Choubay And Co.(Agencies) Pvt.Ltd. (BID ID -953123) | 15755730.00 | Not Quoted | Not Quoted
3 | K B CONTRACT (P) LTD (BID ID -953447) | 15755730.00 | Not Quoted | Not Quoted
4 | M/s. CHANDRA REDDY ELECTRICALS (BID ID -951743) | 15755730.00 | Not Quoted | Not Quoted
5 | HIMALAYA GENERATORS (BID ID -952233) | 15755730.00 | Not Quoted | Not Quoted
6 | ELECTROCONTROL INDIA (BID ID -952726) | 15755730.00 | Not Quoted | Not Quoted
7 | BUDHIRAJA ELECTRICALS (BID ID -952003) | 15755730.00 | Not Quoted | Not Quoted
Lowest Amount Quoted BY: Manish Electricals(15676730.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of New Terminal Building at LBSI Airport Varanasi. SH- Interconnection of ESS (Electrical Substation of New Terminal Building) and NPH (New Power House of Existing Terminal Building) Tender ID: 2025_AAI_258358_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | BUDHIRAJA ELECTRICALS (BID ID -952003) | 15755730.00 | L1
| 2 | K B CONTRACT (P) LTD (BID ID -953447) | 19278810.00 | L2
| 3 | M/s. CHANDRA REDDY ELECTRICALS (BID ID -951743) | 20669745.00 | L3
| 4 | HIMALAYA GENERATORS (BID ID -952233) | 22395350.00 | L4
| 5 | Manish Electricals (BID ID -953605) | 22681800.00 | L5
| 6 | ELECTROCONTROL INDIA (BID ID -952726) | 22959340.00 | L6
| 7 | Choubay And Co.(Agencies) Pvt.Ltd. (BID ID -953123) | 24595625.00 | L7