## BoQ1
Government eProcurement System Created By: Vikas Kumar Tripathi Created Date/Time: 14-Jan-2026 03:10 PM Tender Title: Electrical works of Parking area. Tender ID: 2025_AAI_259083_1
Tender Inviting Authority: Senior Manager . (Engg. – Elect)- IMU, AAI, CHQ, R.G. Bhawan, New Delhi-110003
Name of Work: Improvement of Parking Area & other miscellaneous works at Old Air India Complex, Safdarjung Airport, New Delhi. SH: Electrical Works.
Contract No: (2025_AAI_259083_1)
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | MEC ENGINEERS (GSTN-09AABFM1296R1ZM) BID ID -950857 |  | ECS ENGINEERING PVT LTD (GSTN-09AABCE5944P1Z1) BID ID -953501 |  | ANU ENGINEERING CORPORATION (GSTN-07AJDPK9181G1Z1) BID ID -954108 |  | NATIONAL SAFETY ENGINEERS (GSTN-07ADCPT3599E3Z6) BID ID -954623 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -954658 |  | M/s HI TECH ELECTRICALS (GSTN-NA) BID ID -953093 |  | O. P. CONSTRUCTIONS (GSTN-NA) BID ID -953792
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of 45W LED Street Light Fitting suitable for operate on 240V, 50Hz, AC Supply housed in pressure Die-Cast/Extruded Aluminium Alloy, Toughened glass with IP66 protection suitable for fixing on pole etc. complete as required. The Fitting shall have separate compartment for LEDs & electronic driver, operating voltage 140-270V with Surge Protection of 4KV. | 30.00 | Each |  | 2090.00 | 62700.00 | 1200.00 | 36000.00 | 1800.00 | 54000.00 | 2200.00 | 66000.00 | 3000.00 | 90000.00 | 2350.00 | 70500.00 | 3000.00 | 90000.00 | 36000.00 | ECS ENGINEERING PVT LTD
2.00 | Supply of 5 mtr.long hot dipped galvanised iron (HDGI) octagonal pole, made of high tensile steel in single section , top dia of pole 70 mm , bottom dia of pole 130 mm , wall thickness of 3 mm , with suitable pole cap & single arm bracket 1 mtr long 40mm dia for mounting the street light fittings and with 500 mm long weatherproof reinforced bottom door opening , 4 Nos. 20M X 600mm long "J" type EN 8 grade foundation bolts along with templet ,base plate size 200 mm x 200 mm x 12mm thick as approved by Engineer-In-Charge) | 30.00 | Each |  | 7250.00 | 217500.00 | 8350.00 | 250500.00 | 9000.00 | 270000.00 | 11000.00 | 330000.00 | 9800.00 | 294000.00 | 12500.00 | 375000.00 | 4500.00 | 135000.00 | 135000.00 | O. P. CONSTRUCTIONS
3.00 | Erection & commissioning of 5 mtr.long hot dipped galvanised iron (HDGI) octagonal pole in shallow foundation at a minimum (600*600*1000)mm with 1:3:6 grade RCC nad top layer finishing with 100 mm concrete layer all arround pole (1 mtr*1 mtr ) by providing & fixing of "J" foundation bolt , hylem sheet for supporting al busbars , 20 Amp rating 4P al bus bar set & 6 Amp SP MCB , mounting the luminaire in the pole making wiring with 3 x 1.5 sq.mm PVC insualted flexiable coper wire from the loop in loop out box to the fitting, as per the Site requirement etc as required. | 30.00 | Job |  | 15000.00 | 450000.00 | 5500.00 | 165000.00 | 6500.00 | 195000.00 | 8500.00 | 255000.00 | 7500.00 | 225000.00 | 5999.00 | 179970.00 | 3500.00 | 105000.00 | 105000.00 | O. P. CONSTRUCTIONS
4.00 | SITC of floor mounted, outdoor type, IP-54 rated factory built sheet steel enclosed construction LT PANEL (PTTA) compartmentalized design and covered with CRCA sheet steel of 2mm thick for doors/covers, 2mm thick for gland plates, cleaning & finishing complete with seven tank process for powder coating in approved shade with short circuit with stand capacity of 25KA for 1sec., bus bar and inter-connection with solid aluminium strips, neutral links. Cable alleys, cable gland plates in two half, danger notice plates, etc. and mounted with the following switch gears as per technical specifications etc. complete as required. Earthing stud and detachable gland plate at bottom and rubber gasket for doors with locking arrangement etc. complete. 1) All MCCBs of current rating 250 Amps and above shall be provided with microprocessor based releases and those of rating below 250 Amps shall be provided with thermal magnetic releases or as specified in BOQ. Breaker Release shall provide protection against O/L, S/C & E/F. 2) All MCCBs shall be having Ics = 100% Icu 3) All MCCBs shall be provided with front rotary handle and spreader links. (A) INCOMER 200Amp FP Moulded Case Circuit Breaker of (25kA Ics Value) complete-1 Nos. 0 to 500 Volt digital voltmeter 96mm x 96mm with selector switch. Suitable Size digital ammeter 96mm x 96mm with selector switch & CT's. of suitable ratio. 1 Set of Phase indicating lamps with Single Pole MCB. 1 Set of ON / OFF indicating lamps with Single Pole MCB. Intelligent digital multi function meter of class 0.5 to read V, A, F, KVA, KW, KVAR, KWH, KVAH, PF, Hz etc. with communication facility (RS 485 port), THD and individual order harmonics upto 31st Order. LED/ LCD display with required Nos CTs of suitable ratio of 15 VA & class 0.5 including control circuit wiring with 2 Amp protection MCB. (B) BUSBARS TPN Aluminium busbars of minimum of 250 Amps capacity having 100% neutral bus as that of phase with heat shrinkable coloured sleeves. (C) OUTGOING 20 Amp FP MCB type-C -15 Nos. 32 Amp FP MCB type-C -01 Nos. 100 Amp FP Moulded Case Circuit Breaker type of (25kA Ics Value) -01 Nos. | 3.00 | Each |  | 126000.00 | 378000.00 | 190000.00 | 570000.00 | 145000.00 | 435000.00 | 85000.00 | 255000.00 | 90000.00 | 270000.00 | 55000.00 | 165000.00 | 175000.00 | 525000.00 | 165000.00 | M/s HI TECH ELECTRICALS
5.00 | Supply of following PVC sheathed, XLPE insulated, Aluminium conductor armoured cable, 1.1 KV grade, as per IS 7098 (Part 1) 1988 with upto date amendments.
5.01 | 4 Core, 16 sqmm. | 300.00 | Mtrs. |  | 178.00 | 53400.00 | 157.00 | 47100.00 | 190.00 | 57000.00 | 250.00 | 75000.00 | 160.00 | 48000.00 | 212.00 | 63600.00 | 400.00 | 120000.00 | 47100.00 | ECS ENGINEERING PVT LTD
5.02 | 4 Core, 50 sqmm. | 150.00 | Mtrs. |  | 405.00 | 60750.00 | 358.00 | 53700.00 | 440.00 | 66000.00 | 510.00 | 76500.00 | 350.00 | 52500.00 | 390.00 | 58500.00 | 600.00 | 90000.00 | 52500.00 | Awasthi Electric Works
6.00 | Supplying and drawing of 4 x 6 sq.mm size of PVC ARMOURED Cables with COPPER Conductor 650/1100 V. Grade confirming to IS:7098 (Pt-1) 1988, in the existing surface/ recessed steel / PVC conduit as required. | 400.00 | Mtrs. |  | 415.00 | 166000.00 | 385.00 | 154000.00 | 470.00 | 188000.00 | 620.00 | 248000.00 | 425.00 | 170000.00 | 490.00 | 196000.00 | 900.00 | 360000.00 | 154000.00 | ECS ENGINEERING PVT LTD
7.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required.
7.01 | 4 x 16 sq.mm (28mm) | 60.00 | Nos. |  | 420.00 | 25200.00 | 600.00 | 36000.00 | 200.00 | 12000.00 | 350.00 | 21000.00 | 300.00 | 18000.00 | 15.00 | 900.00 | 366.00 | 21960.00 | 900.00 | M/s HI TECH ELECTRICALS
7.02 | 4 x 50 sq.mm (35mm) | 6.00 | Nos. |  | 450.00 | 2700.00 | 700.00 | 4200.00 | 250.00 | 1500.00 | 400.00 | 2400.00 | 450.00 | 2700.00 | 20.00 | 120.00 | 489.00 | 2934.00 | 120.00 | M/s HI TECH ELECTRICALS
8.00 | Supplying and making end termination with copper lugs for 4 x 6 sq.mm size of PVC insulated and PVC sheathed copper conductor cable of 1.1 KV grade as required. | 60.00 | Nos. |  | 400.00 | 24000.00 | 300.00 | 18000.00 | 200.00 | 12000.00 | 350.00 | 21000.00 | 400.00 | 24000.00 | 35.00 | 2100.00 | 10.00 | 600.00 | 600.00 | O. P. CONSTRUCTIONS
9.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required.
9.01 | Upto 35 sq. mm | 300.00 | Mtrs. |  | 100.00 | 30000.00 | 60.00 | 18000.00 | 30.00 | 9000.00 | 40.00 | 12000.00 | 25.00 | 7500.00 | 15.00 | 4500.00 | 36.00 | 10800.00 | 4500.00 | M/s HI TECH ELECTRICALS
9.02 | Above 35 sq. mm and upto 95 sq. mm | 150.00 | Mtrs. |  | 120.00 | 18000.00 | 80.00 | 12000.00 | 40.00 | 6000.00 | 60.00 | 9000.00 | 40.00 | 6000.00 | 25.00 | 3750.00 | 58.00 | 8700.00 | 3750.00 | M/s HI TECH ELECTRICALS
10.00 | Supplying and laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. in the existing trench, complete as required.
10.01 | 63 mm dia (OD-63 mm & ID-51 mm nominal) | 600.00 | Mtrs. |  | 160.00 | 96000.00 | 185.00 | 111000.00 | 80.00 | 48000.00 | 120.00 | 72000.00 | 175.00 | 105000.00 | 63.00 | 37800.00 | 136.00 | 81600.00 | 37800.00 | M/s HI TECH ELECTRICALS
10.02 | 90 mm dia (OD-90 mm & ID-76 mm nominal) | 150.00 | Mtrs. |  | 192.00 | 28800.00 | 200.00 | 30000.00 | 115.00 | 17250.00 | 160.00 | 24000.00 | 200.00 | 30000.00 | 120.00 | 18000.00 | 183.00 | 27450.00 | 17250.00 | ANU ENGINEERING CORPORATION
11.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 Meter long etc. with charcoal/ coke and salt as required. | 3.00 | Each |  | 9000.00 | 27000.00 | 10000.00 | 30000.00 | 7500.00 | 22500.00 | 7000.00 | 21000.00 | 18500.00 | 55500.00 | 6500.00 | 19500.00 | 7500.00 | 22500.00 | 19500.00 | M/s HI TECH ELECTRICALS
12.00 | Providing and fixing 6 SWG dia G.I wire on surface or recess for loop earthing as required. | 15.00 | Mtrs. |  | 24.00 | 360.00 | 40.00 | 600.00 | 40.00 | 600.00 | 50.00 | 750.00 | 40.00 | 600.00 | 15.00 | 225.00 | 84.00 | 1260.00 | 225.00 | M/s HI TECH ELECTRICALS
| Total in Figures |  |  |  |  | 1640410.00 |  | 1536100.00 |  | 1393850.00 |  | 1488650.00 |  | 1398800.00 |  | 1195465.00 |  | 1602804.00
Lowest Amount Quoted BY: M/s HI TECH ELECTRICALS(1195465.00)

## BOQ Summary
BOQ Summary Details Tender Title: Electrical works of Parking area. Tender ID: 2025_AAI_259083_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/s HI TECH ELECTRICALS (BID ID -953093) | 1195465.00 | L1
| 2 | ANU ENGINEERING CORPORATION (BID ID -954108) | 1393850.00 | L2
| 3 | Awasthi Electric Works (BID ID -954658) | 1398800.00 | L3
| 4 | NATIONAL SAFETY ENGINEERS (BID ID -954623) | 1488650.00 | L4
| 5 | ECS ENGINEERING PVT LTD (BID ID -953501) | 1536100.00 | L5
| 6 | O. P. CONSTRUCTIONS (BID ID -953792) | 1602804.00 | L6
| 7 | MEC ENGINEERS (BID ID -950857) | 1640410.00 | L7