## BoQ1
Government eProcurement System Created By: Mukesh Meena Created Date/Time: 03-Feb-2026 12:39 PM Tender Title: Improvement of Air-conditioning at ELDIS-I and ELDIS-II at Operational Area at C.S.M.I.Airport, Mumbai. Tender ID: 2025_AAI_259097_1
Tender Inviting Authority: Asstt.General Manager (Engg.-Elect.), ATS Complex, Mumbai.
Name of Work: "Improvement of Air-conditioning at ELDIS-I and ELDIS-II at Operational Area at C.S.M.I.Airport, Mumbai.”
Contract No: MUMBAI/ATS/ENGG-E/eNIT-04/2025-26
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | VOLKS ENERGIE PVT LTD (GSTN-07AADCV9396C1ZZ) BID ID -954597 |  | Weartech Engineers Pvt Ltd (GSTN-23AABCW1561C1ZV) BID ID -957167 |  | GRAVITY INDIA TECHNOLOGIES PRIVATE LIMITED (GSTN-NA) BID ID -956892 |  | NETWORK TECHLAB INDIA LIMITED (GSTN-NA) BID ID -945716
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH :- A : S.I.T.C. of P.A.C.
2.00 | Supply of following capacity Floor Mounted, Top discharge and front return Air Cooled type Precision Air Condtioners . The Indoor units shall comprise of stepless variable capacity Digital/Inverter scroll compressor, Min. Two Sided Double skin side panels, with Class "O" Glasswool insulation, Top discharge type complete with dynamically balanced composite material fan driven by Electronically Commutated (EC) motor, hydrophilic coated slant/flat cooling coil. The unit shall be equipped with high efficiency filters(G4), micro processor based programmable logic controller, Liquid receiver, Expansion Valve, Drivers, suction and discharge piping, Internal power & control wiring, Water leak detector sensor, SS drain tray with nitrile rubber insulation, Stainless steel strip Heater, Infrared steam humidifier, Power and Control contactors and Other Electrical accessories. Provision to communicate with the BMS monitoring system through RS 485 communications protocol. The Outdoor Condenser units shall comprise of Condenser fans & motor, Condenser cooling coil with anti-corrosive coating (Copper coil with aluminium fins), Fan speed controller, Isolater switch The outdoor unit shall be selected at min. 38 Deg C of ambient temperatures with R-410A Refrigerant Gas. The units shall be suitable for operation on 415 Volts, 50 Hz, 3 Phase, 4 Wire AC supply. Each unit should be having individual display panel, which shall display date, time, actual & set values, operating conditions, signal faults, collective faults, limiting values and unit wellness alarm / service alarm to reduce the down time and unit memory shall hold the 400 most recent events with ID number, time and date stamp for each event. Operational & Control Features - Supply Air Set points & Operational Capabilities: 20 Deg.C +/- 2 Deg.C, 40% to 70% RH - Return Air Set points & Operational Capabilities: 22 Deg.C to 38 Deg C, 20% to 60% RH - P / PI / PID - All three Control logics for temperature control - Relative / Compensated / Predictive method for humidity control - Temperature & Humidity graphs for the system (Avg. value of all the connected units) & for each single unit - Record of Peak & Low temperature/humidity of the current day - Display shows SET / ACTUAL / SET+ACTUAL Values - Records total run hours for all main components - Team Mode operation for synchronising all machines in room without any external controller - Sequencing & Stand-by rotation - Cascading, Lead-Lag functions - Min. 16 days record of controlled parameters - Unit memory shall hold min. 200 recent alarms with date and time for each alarm - Status report of last 400 event logs - 3 types of access; User, Service & Advanced to protect all settings - Auto restart after a power failure - Graphical display of status of operation of all major components like Compressor, Fan, Heater & Humidifier on screen in an idle mode
3.00 | i) 15.0 TR Total cooling capacity with minimum airflow of 16000 CMH, at minimum 20 Pa ESP, Return Air as temperature at 28 +/-2 Deg C DB & 45% +/-5 RH (Non Condensing). (Note : The Supply of PAC Units followed by its installation are to be carried in the Operational Area of CSMI Airport, Mumbai. Required Tools, Machinary, permissions, Passes, etc. are to be arranged by the Agency) | 3.00 | Each |  | 1305000.00 | 3915000.00 | 1664662.00 | 4993986.00 | 1605210.48 | 4815631.44 | 877450.00 | 2632350.00 | 2632350.00 | NETWORK TECHLAB INDIA LIMITED
4.00 | ii) 11.0 TR (or Equivalent) Total cooling capacity with minimum airflow of 16000 CMH, at minimum 20 Pa ESP, Return Air as temperature at 28 +/-2 Deg C DB & 45% +/-5 RH (Non Condensing). | 3.00 | Each |  | 1060000.00 | 3180000.00 | 1200755.79 | 3602267.37 | 1157871.66 | 3473614.98 | 970120.00 | 2910360.00 | 2910360.00 | NETWORK TECHLAB INDIA LIMITED
5.00 | SH :- B :Installation, Testing & Commissioning of PAC System
6.00 | Installation, testing, and commissioning of 15.0 TR capacity Floor Mounted, Top discharge and front return type Air Cooled type Precision Air Condtioners including supply & fixing suitable adjutable GI/MS stands with rubber pad for each outdoor unit to dimension as specified / recommendation of O.E.M. (for Indoor and Outdoor units) including wiring, connection & interconnection making suitable for operation complete as required. Provision of Suitable Outdoor stand as per site including civil work if required for fixing of the stand. (Note: The Work is to be carried out in the Operational Area of C.S.M.I. Airport, Mumbai) | 3.00 | Job |  | 30000.00 | 90000.00 | 64349.60 | 193048.80 | 62051.40 | 186154.20 | 52858.60 | 158575.80 | 90000.00 | VOLKS ENERGIE PVT LTD
7.00 | Installation, testing, and commissioning of 11.0 TR capacity Floor Mounted, Top discharge and front return type Air Cooled type Precision Air Condtioners including supply & fixing suitable adjutable GI/MS stands with rubber pad for each outdoor unit to dimension as specified / recommendation of O.E.M. (for Indoor and Outdoor units) including wiring, connection & interconnection making suitable for operation complete as required. Provision of Suitable Outdoor stand as per site including civil work if required for fixing of the stand. (Note :The Work is to be carried out in the Operational Area of C.S.M.I. Airport, Mumbai) | 3.00 | Job |  | 30000.00 | 90000.00 | 57349.60 | 172048.80 | 55301.40 | 165904.20 | 47108.00 | 141324.00 | 90000.00 | VOLKS ENERGIE PVT LTD
8.00 | Supply, installation, testing of 18 SWG hard drawn copper refrigerant piping of sizes as per O.E.M. standard with insulation for precision units with proper "U" traps in piping for required length. All refrigerant piping along within conditioned space shall be provided with 9 mm. Class '0' Nitril Rubber insulation while rest pipework shall be provided with Nitrile Rubber Insulation & Anticorrosive coating and supports, between indoor and outdoor units. Each running meter of one circuit includes one meter of copper pipe (inlet & outlet), necessary supports, fittings, insulation, Thermogaurd coating, etc. and should connect the indoor to the outdoor as per locations. (Including extension kit if required) | 60.00 | Meter |  | 4000.00 | 240000.00 | 4289.60 | 257376.00 | 4136.40 | 248184.00 | 3523.60 | 211416.00 | 211416.00 | NETWORK TECHLAB INDIA LIMITED
9.00 | Supply & Installation of Motorized Damper with Actuator (of sufficient torque) & necessary control cablings for ON/OFF operation by interfacing with indoor unit operation and to be installed on indoor machines on Return Air path. | 6.00 | Each |  | 25000.00 | 150000.00 | 29115.00 | 174690.00 | 28075.00 | 168450.00 | 23916.00 | 143496.00 | 143496.00 | NETWORK TECHLAB INDIA LIMITED
10.00 | Sequencing & logic control necessary timers and logic control for automatic start-stop of the unit.with necessary timers and logic control for automatic start-stop of the unit.Logic should include orderly restart after power failure. | 6.00 | Lot |  | 5000.00 | 30000.00 | 4289.60 | 25737.60 | 4136.40 | 24818.40 | 3523.60 | 21141.60 | 21141.60 | NETWORK TECHLAB INDIA LIMITED
11.00 | Supply and fixing Perforated GI trays (With maximum 50% perforation) with necessary support and covertop for Refrigerant Pipes of of following Size in (mm) (Provision of clamp/fixing arrangement are to be provided for the vertical sections)
12.00 | i) Width 300 mm. x Height 75 mm. x Thickness 1.0 mm. | 40.00 | Meter |  | 1250.00 | 50000.00 | 1492.40 | 59696.00 | 1439.10 | 57564.00 | 1226.00 | 49040.00 | 49040.00 | NETWORK TECHLAB INDIA LIMITED
13.00 | ii) Width 150 mm. x Height 50 mm. x Thickness 0.7 mm. | 30.00 | Meter |  | 900.00 | 27000.00 | 798.00 | 23940.00 | 769.50 | 23085.00 | 655.60 | 19668.00 | 19668.00 | NETWORK TECHLAB INDIA LIMITED
14.00 | Supply & Installation of following size GI Class "B" Drain Pipe with 9 mm. thickness Nitrile rubber insulation with including all accessories complete as required.
15.00 | i) 40 mm. diameter | 30.00 | Meter |  | 300.00 | 9000.00 | 814.80 | 24444.00 | 785.70 | 23571.00 | 669.00 | 20070.00 | 9000.00 | VOLKS ENERGIE PVT LTD
16.00 | Supply and laying of 3C x 2.5 Sq.mm. Cu. Flexible cable (Indoor to outdoor unit) on existing cable tray or surface as directed by EIC. | 75.00 | Meter |  | 130.00 | 9750.00 | 329.50 | 24712.50 | 317.74 | 23830.50 | 270.60 | 20295.00 | 9750.00 | VOLKS ENERGIE PVT LTD
17.00 | Supply & charging of Refrigerant Gas (R-410A) for the compressor for the 100 % rating and equivalent copper pipe length between Indoor & Outdoor Unit along with required oil for commisioning. | 150.00 | Kg |  | 900.00 | 135000.00 | 1372.00 | 205800.00 | 1323.00 | 198450.00 | 1127.00 | 169050.00 | 135000.00 | VOLKS ENERGIE PVT LTD
18.00 | Supply and laying of Size 4C x 16 Sq.mm. armoured Copper cable from Incoming Isolator Panel to Indoor Unit on existing cable tray or surface as directed by EIC. | 60.00 | Meter |  | 900.00 | 54000.00 | 1205.40 | 72324.00 | 1162.35 | 69741.00 | 990.10 | 59406.00 | 54000.00 | VOLKS ENERGIE PVT LTD
19.00 | SH :- C : Supply and Fixing of G.I. duct i/c insulation and New Diffusers/ Grills.
20.00 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports, etc. as per approved drawings and specifications of following sheet thickness complete as required.
21.00 | i) Thickness 0.63 mm. sheet (24 Gauge) | 20.00 | Sq.Mtr. |  | 1500.00 | 30000.00 | 2310.00 | 46200.00 | 2227.50 | 44550.00 | 1897.50 | 37950.00 | 30000.00 | VOLKS ENERGIE PVT LTD
22.00 | Dismantling of Existing 15 TR floor mounted PAC units (IDU and ODU) from ELDIS -II and Transporting of the same to ATS Complex. All Required Tools & plants, Vehicle with driver, Labous for loading and unloading, etc.. | 3.00 | No. |  | 130000.00 | 390000.00 | 26783.40 | 80350.20 | 25826.85 | 77480.55 | 22000.65 | 66001.95 | 66001.95 | NETWORK TECHLAB INDIA LIMITED
23.00 | Dismantling of Existing 15 TR floor mounted Package Unit from ELDIS -I and Transporting of the same to ATS Complex. All Required Tools & plants, Vehicle with driver, Labous for loading and unloading, etc.. | 3.00 | No. |  | 120000.00 | 360000.00 | 26783.40 | 80350.20 | 25826.85 | 77480.55 | 22000.65 | 66001.95 | 66001.95 | NETWORK TECHLAB INDIA LIMITED
24.00 | SH-D :- (A.I.C.M.C. - Annual Comprehensive Maintenance Contract of PAC)
25.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 6 Nos. (03 nos. 15 TR and 03 Nos. 11 TR) above work after completion of defect liability period of one year. The scope of work during C.M.C. Period shall be as per technical specifications. For First Year | 12.00 | Month |  | 38835.00 | 466020.00 | 47840.00 | 574080.00 | 46131.00 | 553572.00 | 31907.00 | 382884.00 | 382884.00 | NETWORK TECHLAB INDIA LIMITED
26.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 6 Nos. (03 nos. 15 TR and 03 Nos. 11 TR) above work after completion of defect liability period of one year. The scope of work during C.M.C. Period shall be as per technical specifications. For Second Year | 12.00 | Month |  | 40777.00 | 489324.00 | 50232.00 | 602784.00 | 48438.00 | 581256.00 | 33502.00 | 402024.00 | 402024.00 | NETWORK TECHLAB INDIA LIMITED
27.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 6 Nos. (03 nos. 15 TR and 03 Nos. 11 TR) above work after completion of defect liability period of one year. The scope of work during C.M.C. Period shall be as per technical specifications. For Third Year | 12.00 | Month |  | 42816.00 | 513792.00 | 52744.00 | 632928.00 | 50860.00 | 610320.00 | 35177.00 | 422124.00 | 422124.00 | NETWORK TECHLAB INDIA LIMITED
28.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 6 Nos. (03 nos. 15 TR and 03 Nos. 11 TR) above work after completion of defect liability period of one year. The scope of work during C.M.C. Period shall be as per technical specifications. For Forth Year | 12.00 | Month |  | 44957.00 | 539484.00 | 55381.00 | 664572.00 | 53403.00 | 640836.00 | 36936.00 | 443232.00 | 443232.00 | NETWORK TECHLAB INDIA LIMITED
29.00 | Annual Comprehensive Maintenance Contract of above Floor mounted PAC i.e 6 Nos. (03 nos. 15 TR and 03 Nos. 11 TR) above work after completion of defect liability period of one year. The scope of work during C.M.C. Period shall be as per technical specifications. For Fifth Year | 12.00 | Month |  | 47205.00 | 566460.00 | 58150.00 | 697800.00 | 56073.00 | 672876.00 | 38783.00 | 465396.00 | 465396.00 | NETWORK TECHLAB INDIA LIMITED
| Total in Figures |  |  |  |  | 11334830.00 |  | 13209135.47 |  | 12737369.82 |  | 8841806.30
Lowest Amount Quoted BY: NETWORK TECHLAB INDIA LIMITED(8841806.30)

## BOQ Summary
BOQ Summary Details Tender Title: Improvement of Air-conditioning at ELDIS-I and ELDIS-II at Operational Area at C.S.M.I.Airport, Mumbai. Tender ID: 2025_AAI_259097_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | NETWORK TECHLAB INDIA LIMITED (BID ID -945716) | 8841806.30 | L1
| 2 | VOLKS ENERGIE PVT LTD (BID ID -954597) | 11334830.00 | L2
| 3 | GRAVITY INDIA TECHNOLOGIES PRIVATE LIMITED (BID ID -956892) | 12737369.82 | L3
| 4 | Weartech Engineers Pvt Ltd (BID ID -957167) | 13209135.47 | L4