## BoQ1
Government eProcurement System Created By: MD Sadrul Huda Created Date/Time: 13-Feb-2026 05:00 PM Tender Title: Replacement of Essential and Non-Essential Panels at C.A. Porbandar Tender ID: 2025_AAI_259328_1
Tender Inviting Authority: Asst. General Manager (E-E)
Name of Work: Replacement of Essential and Non-Essential Panels at C.A. Porbandar
Contract No: 2025_AAI_259328_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO. (GSTN-24AAEFD3355K1ZI) BID ID -969044
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of UV resistance indoor wall mounted LT Distribution Panel of Thermoplastic polycarbonate enclosure in accordance with IEC 61439-1 of appropriate dimension, IP 54 (EN 60 529), RAL 7035, mounting frame RAL 7016 suitable for system Voltage 415V, 50 HZ, 4WIRE+E with following details - Copper Busbar Rating - 400A Incomer- 400A 4P 36kA MCCB - 1 Nos. R Y B LED Indication Lamps - 1 Each 2/32A Control Fuse Terminal with link - 6 Nos. Current Transformer 400A /5A , 5 VA CL - 3 No Digital Voltmeter - 1 No. Digital Ammeter - 1 No. Multifunction Meter with 3 line LCD Display - 1 No Outgoing - 125 A 4P 25kA MCCB - 5 Nos Indication Lamp R & G (LED type) - 5 Set 50 sqmm Terminal Block - 20Nos. (Design and other materials as per attached drawing no. HEN MI DB - 1015 - 25 - 1) | 1.00 | Each | 0.00 | 330000.00 | 330000.00 | 330000.00 | DOSHI ELECTRIC ENGG. CO.
2.00 | SITC of UV resistance indoor wall mounted LT Distribution Panel of Thermoplastic polycarbonate enclosure in accordance with IEC 61439-1 of appropriate dimension, IP 54 (EN 60 529), RAL 7035, mounting frame RAL 7016 suitable for system Voltage 415V, 50 HZ, 4WIRE+E with following details - Copper Busbar Rating - 400A Incomer- 400A 4P 36kA MCCB - 1 Nos. R Y B LED Indication Lamps - 1 Each 2/32A Control Fuse Terminal with link - 6 Nos. Current Transformer 400A /5A , 5 VA CL - 3 No Digital Voltmeter - 1 No. Digital Ammeter - 1 No. Multifunction Meter - 1 No Outgoing - 125 A 4P 25kA MCCB - 4 Nos Indication Lamp R & G (LED type) - 4 Set 50 sqmm Terminal Block - 12Nos. (Design and other materials as per attached drawing no. HEN MI DB - 1015 - 25 - 2) | 1.00 | Each |  | 312000.00 | 312000.00 | 312000.00 | DOSHI ELECTRIC ENGG. CO.
3.00 | SITC of UV resistance indoor wall mounted LT Distribution Panel of Thermoplastic polycarbonate enclosure in accordance with IEC 61439-1 of appropriate dimension, IP 54 (EN 60 529), RAL 7035, mounting frame RAL 7016 suitable for system Voltage 415V, 50 HZ, 4WIRE+E with following details - Copper Busbar Rating - 250A Incomer- 250A 4P 36kA MCCB - 1 Nos. R Y B LED Indication Lamps - 1 Each 2/32A Control Fuse Terminal with link - 6 Nos. Current Transformer 250A /5A , 5 VA CL - 3 No Digital Voltmeter - 1 No. Digital Ammeter - 1 No. Multifunction Meter - 1 No Outgoing - 125 A 4P 25kA MCB - 3 Nos 50 A 4P 25kA MCB - 3 Nos Indication Lamp R & G (LED type) - 6 Set 50 sqmm Terminal Block - 12Nos. 16 sqmm Terminal Block - 12Nos. (Design and other materials as per attached drawing no. HEN MI DB - 1015 - 25 - 3) | 1.00 | Each |  | 293000.00 | 293000.00 | 293000.00 | DOSHI ELECTRIC ENGG. CO.
4.00 | SITC of UV resistance indoor wall mounted LT Distribution Panel of Thermoplastic polycarbonate enclosure in accordance with IEC 61439-1 of appropriate dimension, IP 54 (EN 60 529), RAL 7035, mounting frame RAL 7016 suitable for system Voltage 415V, 50 HZ, 4WIRE+E with following details - Copper Busbar Rating - 250A Incomer- 250A 4P 36kA MCCB - 1 Nos. R Y B LED Indication Lamps - 1 Each 2/32A Control Fuse Terminal with link - 6 Nos. Current Transformer 250A /5A , 5 VA CL - 3 No Digital Voltmeter - 1 No. Digital Ammeter - 1 No. Multifunction Meter - 1 No Outgoing - 63 A 4P 10kA MCB - 20 Nos 16 sqmm Terminal Block - 80Nos. (Design and other materials as per attached drawing no. HEN MI DB - 1015 - 25 - 4) | 1.00 | Each |  | 338000.00 | 338000.00 | 338000.00 | DOSHI ELECTRIC ENGG. CO.
5.00 | SITC of UV resistance indoor wall mounted LT Distribution Panel of Thermoplastic polycarbonate enclosure in accordance with IEC 61439-1 of appropriate dimension, IP 54 (EN 60 529), RAL 7035, mounting frame RAL 7016 suitable for system Voltage 415V, 50 HZ, 4WIRE+E with following details - Copper Busbar Rating - 250A Incomer- 250A 4P 36kA MCCB - 1 Nos. R Y B LED Indication Lamps - 1 Each 2/32A Control Fuse Terminal with link - 6 Nos. Current Transformer 250A /5A , 5 VA CL - 3 No Digital Voltmeter - 1 No. Digital Ammeter - 1 No. Multifunction Meter - 1 No Outgoing - 63 A 4P 10kA MCB - 15 Nos 16 sqmm Terminal Block - 60Nos. (Design and other materials as per attached drawing no. HEN MI DB - 1015 - 25 - 5) | 1.00 | Each |  | 274000.00 | 274000.00 | 274000.00 | DOSHI ELECTRIC ENGG. CO.
6.00 | SITC of UV resistance indoor wall mounted LT Distribution Panel of Thermoplastic polycarbonate enclosure in accordance with IEC 61439-1 of appropriate dimension, IP 54 (EN 60 529), RAL 7035, mounting frame RAL 7016 suitable for system Voltage 415V, 50 HZ, 4WIRE+E with following details - Copper Busbar Rating - 250A Incomer- 250A 4P 36kA MCCB - 1 Nos. R Y B LED Indication Lamps - 1 Each 2/32A Control Fuse Terminal with link - 6 Nos. Current Transformer 250A /5A , 5 VA CL - 3 No Digital Voltmeter - 1 No. Digital Ammeter - 1 No. Multifunction Meter - 1 No Outgoing - 63 A 4P 10kA MCB - 6 Nos 40 A 4P 10kA MCB - 6 Nos 16 sqmm Terminal Block - 24Nos. 10 sqmm Terminal Block - 24Nos. (Design and other materials as per attached drawing no. HEN MI DB - 1015 - 25 - 6) | 1.00 | Each |  | 245000.00 | 245000.00 | 245000.00 | DOSHI ELECTRIC ENGG. CO.
7.00 | SITC of UV resistance outdoor floor stand mounted LT Distribution Panel of Thermoplastic polycarbonate enclosure in accordance with IEC 61439-1 of appropriate dimension, IP 65 (EN 60 529), RAL 7035, mounting frame RAL 7016 suitable for system Voltage 415V, 50 HZ, 4WIRE+E with following details - Copper Busbar Rating - 250A Incomer- 250A 4P 25kA MCCB - 1 Nos. R Y B LED Indication Lamps - 1 Each Control Fuse Terminal - 6 Nos. Current Transformer 250A /5A , 5 VA CL - 3 No Multifunction Meter - 1 No Outgoing - 63 A 4P 10kA MCB - 4 Nos 70A TP Contactor - 3 Nos Control Fuse Terminal - 3 Nos 24 Hour Timer - 3 Nos A/O/M Selector Switch - 3 Nos Stop Push Button with 1 NC Contact - 3 Nos Start Push Button with 1 NO contact - 3 Nos 32 A DP 10kA MCB - 20Nos 16 A DP 10KA MCB - 1 No 63 A, IP 67, 5Pin Plug and Socket - 1 No 32 A, IP 67, 3 Pin Plug and Socket - 1 No (Design and other materials as per attached drawing no. HEN MI DB - 1092 - 2025) | 1.00 | Each |  | 340000.00 | 340000.00 | 340000.00 | DOSHI ELECTRIC ENGG. CO.
8.00 | SITC of UV resistance indoor floor stand mounted LT Distribution Panel of Thermoplastic polycarbonate enclosure in accordance with IEC 61439-1 of appropriate dimension, IP 54 (EN 60 529), RAL 7035, mounting frame RAL 7016 suitable for system Voltage 415V, 50 HZ, 4WIRE+E with following details - Copper Busbar Rating - 250A Incomers - Incomer 1 - 160A 4P 25kA MCCB - 1 Nos. Incomer 2 - 160A 4P 25kA MCCB - 1 Nos. R Y B LED Indication Lamps - 1 Each for Each Incomer Control Fuse Terminal with link - 6 Nos. Current Transformer 160A /5A , 5 VA CL - 6 No Digital Voltmeter - 1 No. for Each Incomer Digital Ammeter - 1 No. for Each Incomer Multifunction Meter - 1 No for Each Incomer Manual Changeover Switch: 125 A 4P Changeover Switch - 1 No. Outgoing - 32 A FP 10kA MCB - 5 Nos 16 A SP 10kA MCB - 12 Nos 16A DP 10kA MCB, 18A DP Contactor, 24Hours digital timer, Start/Stop Push Button (1 each), A/O/M Selector Switch and 2 A Fuse terminal block - 1 Set 50 sqmm Terminal Block - 12Nos. 50 sqmm Terminal Block - 20Nos. 4 sqmm Terminal Block - 32Nos. (Design and other materials as per attached drawing no. HEN MI DB-08-24-2) | 1.00 | Each |  | 290000.00 | 290000.00 | 290000.00 | DOSHI ELECTRIC ENGG. CO.
9.00 | Supply of Cable reel with central, interlocking mechanism, Solid carrying rack with ergonomic handle Central Plate with thermal overload protection and a) 1 unit CEE flanged socket straight 16/5 6h (315-6f7) Rated operating voltage: 400V and b) 3 unit of safety machine sockets national version with self-closing hinged lids and sealing edge (105-0bsw) Rated operating voltage: 400V, Rated current: 16A, Protection rating: IP54. Cable: 33m Black cable H07RN-F 5C2.5sqmm (Make- PCE electric, Article no- 9350042-p or Equivalent) | 3.00 | Each |  | 65000.00 | 195000.00 | 195000.00 | DOSHI ELECTRIC ENGG. CO.
10.00 | Supply of 280mm X 190mm X 130mm Weatherproof Junction Box of material Polycarbonate, Cover screws material- Polyamide, Gasket material- PU, IP 66/67, IK 10, having 4 pole connectors of 63A rating, DIN Rail for mounting of MCB in the terminal box, alongwith 5A-32A DP Curve C MCB, PVC gland for 4C x 25 sqmm cable entry, clamp for fixing on pole/wall as per site requirement. (JB Make- Trinity Touch, Article no- 011702288, Model-HE-PC 2819 17G or Equivalent from preferred Make) | 150.00 | Each |  | 1300.00 | 195000.00 | 195000.00 | DOSHI ELECTRIC ENGG. CO.
11.00 | Supply of 3.5 Core X 70 Sq.mm size. XLPE insulated, PVC sheathed Aluminum conductor armoured power cable of 1.1 KV grade conforming to IS:7098 Part-I with upto date amendment etc. complete as required. | 300.00 | Meter |  | 400.00 | 120000.00 | 120000.00 | DOSHI ELECTRIC ENGG. CO.
12.00 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable of 1.1 KV grade of following size on wall surface as required i) Above 35 sq. mm and upto 95sq. mm (clamped with 25x3mm MS flat clamp) | 300.00 | Meter |  | 100.00 | 30000.00 | 30000.00 | DOSHI ELECTRIC ENGG. CO.
13.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 3 ½X 70 sq. mm (38 mm) size of PVC insulated and PVC sheathed/XLPE aluminium conductor cable of 1.1 grade as required. | 2.00 | Each |  | 1000.00 | 2000.00 | 2000.00 | DOSHI ELECTRIC ENGG. CO.
14.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray cable tray with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders / supported from ground with L angle including G.I. bolts & nuts, etc as required. 450 mm width X 50 mm depth X 2 mm | 10.00 | Meter |  | 1750.00 | 17500.00 | 17500.00 | DOSHI ELECTRIC ENGG. CO.
15.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray “bends “ ( galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders / supported from ground with L angle including G.I. bolts & nuts, etc as required. 450 mm width X 50 mm depth X 2 mm | 2.00 | Each |  | 2000.00 | 4000.00 | 4000.00 | DOSHI ELECTRIC ENGG. CO.
16.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray cable tray with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders / supported from ground with L angle including G.I. bolts & nuts, etc as required. 100 mm width X 50 mm depth X 1.6 mm | 12.00 | Meter |  | 700.00 | 8400.00 | 8400.00 | DOSHI ELECTRIC ENGG. CO.
17.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray “Cross member” ( galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required 450 mm width X 50 mm depth X 2 mm | 3.00 | Each |  | 10.00 | 30.00 | 30.00 | DOSHI ELECTRIC ENGG. CO.
18.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray “Reducer” ( galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required. 450 mm width X 50 mm depth X 2 mm | 6.00 | Each |  | 1750.00 | 10500.00 | 10500.00 | DOSHI ELECTRIC ENGG. CO.
19.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray “bends “ ( galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders / supported from ground with L angle including G.I. bolts & nuts, etc as required. 100 mm width X 50 mm depth X 1.6 mm | 6.00 | Each |  | 900.00 | 5400.00 | 5400.00 | DOSHI ELECTRIC ENGG. CO.
20.00 | PU Expanding foam of 750ml spray bottle for sealing upto 3 inch gaps | 10.00 | Each |  | 600.00 | 6000.00 | 6000.00 | DOSHI ELECTRIC ENGG. CO.
21.00 | Cable Duct Sealing Compound | 20.00 | lb (pound) |  | 500.00 | 10000.00 | 10000.00 | DOSHI ELECTRIC ENGG. CO.
22.00 | Supply of Heavy duty professional 230V Electric Rotary Hammer Drill machine with SDS of minimum 900W and rated speed of 800 rpm and Impact rate upto 3600 impact/minute at the rated speed, suitable for hole of upto 32mm in Concrete along with auxiliary handle and set of drill bits (1 bit of 28mm dia, 400mm working length and 2 nos. of Flat Chisel of 20mm dia and minimum 250mm working length) suitable for the drill machine. Bosch GBH 4-32 DFR Professional or equivalent | 1.00 | Set |  | 35000.00 | 35000.00 | 35000.00 | DOSHI ELECTRIC ENGG. CO.
23.00 | Supply of Heavy duty professional portable 230V Electric Demolition Hammer of minimum 1500W and Impact rate upto 1800 impact/minute at the rated speed, impact energy shall be atleast 16J, suitable for Concrete along with auxiliary handle and 1 nos. of Flat Chisel suitable for the hammer. Bosch GSH 11E Professional or equivalent | 1.00 | Set |  | 40000.00 | 40000.00 | 40000.00 | DOSHI ELECTRIC ENGG. CO.
24.00 | SITC of 3 phase 100 KVA Air Cooled Servo controlled voltage stabilizer With MCCB, BYPASS, Contactor Input voltage range: 340 V to 480 V Output voltage range: 415 V ±1% at MSSR Porbandar | 2.00 | Each |  | 200000.00 | 400000.00 | 400000.00 | DOSHI ELECTRIC ENGG. CO.
25.00 | SITC of 3 phase, 15 KVA, unbalanced Air Cooled Servo controlled voltage stabilizer having Microcontroller based DVM Display, Control type: digital micro controller based With MCCB, BYPASS, Contactor Input voltage range: 340 V to 480 V Output voltage range: 415 V ±1% , Input frequency: 47 to 53 Hz at ADS-B at Mithapur site | 1.00 | Each |  | 50000.00 | 50000.00 | 50000.00 | DOSHI ELECTRIC ENGG. CO.
26.00 | Supply and installation of 250 Amp Changeover switch at MSSR Porbandar with following - Enclosure Type- Thermoplastic polycarbonate Degree of Protection: IP 54 System Voltage: 3 Phase 50Hz 415V 4W+E Incomer- 2 nos of incomer of 3.5X185 sqmm (direct termination) Outgoing-1 no outgoing of 3.5X185 sqmm (direct termination) Mimimum Panel Size: 600X1400X400mm (minimum) | 1.00 | Each |  | 26400.00 | 26400.00 | 26400.00 | DOSHI ELECTRIC ENGG. CO.
27.00 | Supply and installation of 63 Amp Changeover switch at Mithapur site with following - Enclosure Type- Thermoplastic polycarbonate Degree of Protection: IP 54 System Voltage: 3 Phase 50Hz 415V 4W+E Incomer- 2 nos of incomer of 3.5X50 sqmm (direct termination) Outgoing-1 no outgoing of 3.5X50 sqmm (direct termination) Mimimum Panel Size: 350X490X270mm (minimum) | 1.00 | Each |  | 15000.00 | 15000.00 | 15000.00 | DOSHI ELECTRIC ENGG. CO.
28.00 | Supply, fabrication and installation of stainless steel chequered plates of 6mm thickness in compliance with ASTM A240/480, work includes cutting, chamfering and fabricating in desired size and shape, fixing handles, fabricating and installing support channels as per site requirement to make aesthetic appearance. | 8.00 | sqm |  | 14000.00 | 112000.00 | 112000.00 | DOSHI ELECTRIC ENGG. CO.
| Total in Figures |  |  |  |  | 3704230.00
Lowest Amount Quoted BY: DOSHI ELECTRIC ENGG. CO.(3704230.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Essential and Non-Essential Panels at C.A. Porbandar Tender ID: 2025_AAI_259328_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | DOSHI ELECTRIC ENGG. CO. (BID ID -969044) | 3704230.00 | L1