## BoQ1
Government eProcurement System Created By: Sateesh Kr Kanaujiya Created Date/Time: 22-Jan-2026 04:58 PM Tender Title: Replacement of existing APFC capacitor panel in power house at the Chh. Sambhaji Nagar Airport Tender ID: 2025_AAI_260489_1
Tender Inviting Authority: Senior Manager (Engg.-Electrical), Airports Authority of India, Chh. Sambhaji Nagar Airport - 431007.
Name of Work: Replacement of existing APFC capacitor Panel in power house at the Chh. Sambhaji Nagar Airport.
Contract No: 2025_AAI_ 260489_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | GK ELECTRICALS AND ENGINEERS (GSTN-27CEZPK9541R1Z3) BID ID -952701 |  | ECS ENGINEERING PVT LTD (GSTN-09AABCE5944P1Z1) BID ID -957613 |  | DOSHI ELECTRIC ENGG. CO. (GSTN-24AAEFD3355K1ZI) BID ID -957653 |  | POWER AUTOMATION AND CONTROLS (GSTN-27ABMPA1796L1Z9) BID ID -959696 |  | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -960025 |  | RISHA CONTROL ENGINEERS PRIVATE LIMITED (GSTN-NA) BID ID -959626 |  | Shiva Enterprises (GSTN-NA) BID ID -959550
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, installation, testing and commissioning of 550 KVAR @ 440 V AC Automatic Power Factor Correction (APFC) Panel totally enclosed type with self-standing floor mounting dust with minimum 7 tank process, and vermin proof fully compartmentalized indoor type cubical fabricated from 1.6 mm. thick CRCA sheet, front doors hinged type with properly fitted gasket. Panel shall have separate compartment for busbar, and cable alley. Suitable MS channel shall be provided at the bottom, painting and complete with inter connection between busbar, switch gears, caps bank along with APFC relay etc. with suitable size Copper strip/bars, and having following component, instrument etc. with earthing the body as per the technical specification. APFC Panel consisting of 5KVAR to 100 KVAR Capacitors totaling to 550 KVAR suitable for operation on 03 Phase, 440 V AC/525V AC, delta connected, ultra-Heavy Duty Cylindrical MDXL TYPE, with discharge resistors, insulation level – 3 KV RMS, Tolerance ± 10 %, Frequency- 50 HZ, Temp.Catog.-10⁰C +85⁰C Harmonic elimination upto 35%, voltage withstand -20-30% as per IS. Inbuilt with: 550 KVAR, 3-phase, 50Hz dry type indoor line side 14% or 7% detuned Copper Wound Series Reactor. INCOMER 1600 A TPN, Micro processor base ACB 50 KA, - 01 No., CT, 1600/5A, 15VA, Class – 1 - 3-Nos., Digital Ammeter, 0-1600A, 96 x 96mm -1-no., Digital Voltmeter, 0-500V, 96 x 96mm - 1-no.,Indicating Lamp ,ON, OFF & Trip - 3-nos. , 6A SP MCB - 7 -No., APFC Relay, 13 Stages with P.F. Meter- 1-no., 15A, 2P 2way with off, Auto / Manual Selector Switch- 1-no., Phase indication lamp (R/Y/B) - 3-nos., Suitable size Fan, 200mm Sweep & Suitable Neutral Link. The technical specification sheet for the selection of the capacitor bank and details of MCB & MCCB, indicationlamp, Push button, details in mention in the Technical specfication sheet.The details of 550 KVAR is 5 KVAR - 2No., 7.5KVAR - 02 No. 12.5 KVAR - 02 No., 25 KVAR - 02 No., 50 KVAR - 01 No. & 100 KVAR - 04 No. The details of APFC panel mentioned in Technical specification sheet. | 3.00 | Set |  | 1580000.00 | 4740000.00 | 2012000.00 | 6036000.00 | 1585000.00 | 4755000.00 | 1530000.00 | 4590000.00 | 1480000.00 | 4440000.00 | 1366666.00 | 4099998.00 | 1350000.00 | 4050000.00 | 4050000.00 | Shiva Enterprises
2.00 | Dismantling of existing APFC panel of capacity 540 kVAR and shifting to AAI electrical store within 50 metre premises complete as required as per the direction of Engineer-In-Charge. | 2.00 | Job |  | 4609.00 | 9218.00 | 10000.00 | 20000.00 | 5000.00 | 10000.00 | 20000.00 | 40000.00 | 45000.00 | 90000.00 | 10000.00 | 20000.00 | 12500.00 | 25000.00 | 9218.00 | GK ELECTRICALS AND ENGINEERS
3.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 300 sq. mm (70mm) | 12.00 | Each |  | 380.00 | 4560.00 | 1500.00 | 18000.00 | 1400.00 | 16800.00 | 3800.00 | 45600.00 | 2000.00 | 24000.00 | 3050.00 | 36600.00 | 1250.00 | 15000.00 | 4560.00 | GK ELECTRICALS AND ENGINEERS
| Total in Figures |  |  |  |  | 4753778.00 |  | 6074000.00 |  | 4781800.00 |  | 4675600.00 |  | 4554000.00 |  | 4156598.00 |  | 4090000.00
Lowest Amount Quoted BY: Shiva Enterprises(4090000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of existing APFC capacitor panel in power house at the Chh. Sambhaji Nagar Airport Tender ID: 2025_AAI_260489_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Shiva Enterprises (BID ID -959550) | 4090000.00 | L1
| 2 | RISHA CONTROL ENGINEERS PRIVATE LIMITED (BID ID -959626) | 4156598.00 | L2
| 3 | Manish Electricals (BID ID -960025) | 4554000.00 | L3
| 4 | POWER AUTOMATION AND CONTROLS (BID ID -959696) | 4675600.00 | L4
| 5 | GK ELECTRICALS AND ENGINEERS (BID ID -952701) | 4753778.00 | L5
| 6 | DOSHI ELECTRIC ENGG. CO. (BID ID -957653) | 4781800.00 | L6
| 7 | ECS ENGINEERING PVT LTD (BID ID -957613) | 6074000.00 | L7