## BoQ1
Government eProcurement System Created By: Chandan Kumar Created Date/Time: 25-Feb-2026 04:41 PM Tender Title: Development of New Civil Enclave at Bihta. SH SITC of GLF system Electrical works for Apron and taxiway at Civil Enclave Bihta Airport Tender ID: 2025_AAI_261207_1
Tender Inviting Authority: Airports Authority of India, Civil Enclave Bihta Airport.
Name of Work: Development of New Civil Enclave at Bihta. SH:SITC of GLF system Electrical works for Apron and taxiway at Civil Enclave Bihta Airport.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | REWINDER TECHNO ELECTRICALS (GSTN-18AAFFR7457K1ZL) BID ID -971438 |  | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED (GSTN-NA) BID ID -963493
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-IA : Supply of GLF system & associated electrical works Supply of FAA/ICAO/DGCA-CAR Compliant Inset type LED Uni directional Stop Bar (RED) light fitting suitable for aviation visual aids requirements complete with shallow base and matching body of the fitting, inner body and outer cover made of die cast aluminium complete with LED lamp with integral driver and electronics suitable for 6.6 amps current with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, hardware, red prism / lenses and all standard accessories and ready for site installation complete as required as per sepcifications. | 18.00 | Each |  | 51000.00 | 918000.00 | 54000.00 | 972000.00 | 918000.00 | REWINDER TECHNO ELECTRICALS
2.00 | Supply of FAA/ICAO/DGCA-CAR Compliant high intensity Elevated LED Runway guard light (yellow) with two flashing light fixtures with black independent visors, 6.6A Current driven input power supply, LED lamps/module, flashing rates 45-50 Per Minute, frangible support, high strength base plate for runway guard light to resist wind speed (300 mph), gaskets etc complete as required as per specifications. | 5.00 | Set |  | 210000.00 | 1050000.00 | 188000.00 | 940000.00 | 940000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
3.00 | Supply of FAA/ICAO/DGCA-CAR Compliant elevated type omni-directional (Blue), medium intensity LED type Taxiway Edge Light fitting for aviation visual aid complete with LED suitable for operation at 6.6 Amps, Lens clamping mechanism, breakable coupling, gasket, two pin secondary leads, base plate and other accessories including integrated encapsulated electronic module complete as required as per sepcifications. | 296.00 | Each |  | 7000.00 | 2072000.00 | 10730.00 | 3176080.00 | 2072000.00 | REWINDER TECHNO ELECTRICALS
4.00 | Supply of FAA/ICAO/DGCA-CAR Compliant inset type omni-directional (Blue), medium intensity LED type taxiway Edge Light fitting for aviation visual aid complete with LED and integral driver and electronics suitable for 6.6 Amps and provided with lenses / prism, filters, lens protection ring, shallow base, matching body, single plug, inner & outer cover, two pin secondary leads complete with other accessories as required as per specifications. | 15.00 | Each |  | 51000.00 | 765000.00 | 51000.00 | 765000.00 | 765000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
5.00 | Supply of 2C x 2.5 sqmm 600 V grade, copper conductor, EPR insulated, PCP/CPE/TCP sheathed, unscreened, non-shielded, unarmoured anti-termite and anti-rodent treated underground secondary cable conforming to IS:9968-1 as amended up to date and as per technical specifications etc. complete as required. | 600.00 | Mtrs. |  | 270.00 | 162000.00 | 270.00 | 162000.00 | 162000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
6.00 | Supply of 1 X 6 sqmm, 5 KV grade copper conductor, XLPE insulated, PVC sheathed, single core, unscreened, non-shielded, unarmoured anti-termite and anti-rodent treated underground Airfield Lighting cable conforming to IS:7098 part-II as amended up to date and as per technical specifications etc. complete as required. | 23419.00 | Mtrs. |  | 220.00 | 5152180.00 | 209.00 | 4894571.00 | 4894571.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
7.00 | Supply of 6 sqmm, 5 kV grade Plug and Receptacle,Type-I, Class 'B' connector kit suitable for field attachment with 5 kV grade 1 x 6 sqmm primary cable as per FAA/ICAO/DGCA CAR and conforming to technical specifications etc. complete as required. | 354.00 | Set |  | 900.00 | 318600.00 | 900.00 | 318600.00 | 318600.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
8.00 | Supply of Indoor type air cooled constant current regulator of micro processor controlled, thyristor type suitable for remote as well as local control operations on input voltage 230/415 volts, 50Hz AC supply with 6.6A output having 5 steps brightness control with variation of current output and able to communicate with PC or PLC controlled system, with suitable rating Microprocessor based release (Ics = Icu = 25kA) incomer 3 Pole 63 Amp. MCCB, digital output ammeter (0-10A), overcurrent, overvoltage, open circuit and earth fault protection and digital earth leakage meter, two stage earth leakage detector, positive back indication equipments, LED/LCD display, suitable for connection and communication with ALCMS for operation of LED type AGL Circuits etc complete as required confirming to technical specifications for the following rating. a) 2.5 Kw | 7.00 | Each |  | 210000.00 | 1470000.00 | 182000.00 | 1274000.00 | 1274000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
9.00 | Supply of Indoor type air cooled constant current regulator of micro processor controlled, thyristor type suitable for remote as well as local control operations on input voltage 230/415 volts, 50Hz AC supply with 6.6A output having 5 steps brightness control with variation of current output and able to communicate with PC or PLC controlled system, with suitable rating Microprocessor based release (Ics = Icu = 25kA) incomer 3 Pole 63 Amp. MCCB, digital output ammeter (0-10A), overcurrent, overvoltage, open circuit and earth fault protection and digital earth leakage meter, two stage earth leakage detector, positive back indication equipments, LED/LCD display, suitable for connection and communication with ALCMS for operation of LED type AGL Circuits etc complete as required confirming to technical specifications for the following rating. a) 7.5 Kw | 3.00 | Each |  | 250000.00 | 750000.00 | 238000.00 | 714000.00 | 714000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
10.00 | Supply of 15 Watt, 6.6/6.6 Amp rating completely enclosed rubber covered isolating transformer for use of 6.6 amps series airport lighting circuits having nominal voltage rating of 5KV rated for operation on 50 Hz. The transformer shall be water tight and shall be designed for direct burial in the earth or installation in a Housing Box in conformity with ICAO/DGCA-CAR, complete as required as per specifications. | 329.00 | Each |  | 3000.00 | 987000.00 | 2700.00 | 888300.00 | 888300.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
11.00 | Supply of 45 Watt, 6.6/6.6 Amp rating completely enclosed rubber covered isolating transformer for use of 6.6 amps series airport lighting circuits having nominal voltage rating of 5KV rated for operation on 50 Hz. The transformer shall be water tight and shall be designed for direct burial in the earth or installation in a Housing Box in conformity with ICAO/DGCA-CAR, complete as required as per specifications. | 25.00 | Each |  | 3500.00 | 87500.00 | 3500.00 | 87500.00 | 87500.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
12.00 | Supply of 1 x 16 Sq.mm PVC insulated copper conductor single core un-armoured flexible cable of 1.1 KV grade confirming to IS 694 for earth connection etc complete as required. | 100.00 | Mtrs. |  | 200.00 | 20000.00 | 250.00 | 25000.00 | 20000.00 | REWINDER TECHNO ELECTRICALS
13.00 | Supply of LED Guidance signage board of various sizes made out of 2 mm thick anodized aluminium frame with suitable angle support, 1.5 mm thick aluminium back symbols of sign should be screen printed on inside of sign face made of self-adhesive 3M film applied on the inside face with required coloring as approved by E-I-C. Sign board shall be uniformly internally illuminated with required LED's i/c all other accessories to achieve uniform illumination level and with suitable driver and electronics to operate on 2.8 Amp to 6.6 Amp AC, made for water tightness and locking arrangements, mounting legs with frangible coupling & base frame etc. meeting the latest ICAO/DGCA-CAR standards complete as per specifications etc. as required. The LED signage board shall be provided with an electronic LED driver having dual input capability and capable of operating from two independent isolating transformers, connected to separate series circuits. Note- The rate shall be quoted considering Wastages. | 30.00 | Sq.Mtrs |  | 35000.00 | 1050000.00 | 35000.00 | 1050000.00 | 1050000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
14.00 | Supply of 3C x 16 Sq. mm.size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Copper conductor power cable conforming to IS 7098 (Part-I) as amended upto date. | 150.00 | Mtrs. |  | 800.00 | 120000.00 | 800.00 | 120000.00 | 120000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
15.00 | Supply of 4C x 16 Sq. mm.size 1.1 KV grade XLPE insulated, PVC sheathed, armoured Copper conductor power cable conforming to IS 7098 (Part-I) as amended upto date. | 200.00 | Mtrs. |  | 900.00 | 180000.00 | 900.00 | 180000.00 | 180000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
16.00 | Supply of 1 X 2.5 sq.mm FRLSH PVC insulated copper conductor single core wire for end to end termination for earthing, preferably green colour conforming to conforming to IS:694 as amended up to date and technical specifications etc. complete as required. | 350.00 | Mtrs. |  | 120.00 | 42000.00 | 120.00 | 42000.00 | 42000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
17.00 | Supply of 1.1 KV grade, Aluminium Conductor, XLPE insulated, galvanised steel strip armoured & overall PVC sheathed armoured power cable as per IS: 7098 (Part-I) upto latest amendments complete as required. a) 3.5C X 120 Sq.mm | 200.00 | Mtrs. |  | 1200.00 | 240000.00 | 1200.00 | 240000.00 | 240000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
18.00 | Supply of 50 mm outer dia. lSI marked HDPE pipe as per 1S:4984:2016, of rating PE 80, PN 10 with 4 mm nylon rope etc. complete as required. | 8037.00 | Mtrs. |  | 170.00 | 1366290.00 | 170.00 | 1366290.00 | 1366290.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
19.00 | SH-IB:Installation, Testing & Commissioning of GLF system & associated electrical works Installation, testing and Commissioning of inset type fitting with deep core cutting for fixing shallow base, aligning and setting i/c providing sealing material and installation of Isolating Transformer, Crimping / Jointing of secondary lead connectors & other accessories required for commissioning i/c supply of all materials except isolating transformer etc. as per specification complete as required. a) Fitting size up to 8 " / 12 " | 30.00 | Job |  | 5000.00 | 150000.00 | 6200.00 | 186000.00 | 150000.00 | REWINDER TECHNO ELECTRICALS
20.00 | Installation, testing & commissioning of Elevated type taxiway light fixtures/ Runway Guard light on existing transformer housing boxes and Crimping / Jointing of secondary lead connectors, installation of isolating transformers, i/c supply of all materials except isolating transformer etc.as per specificaiton complete as required. | 274.00 | Job |  | 150.00 | 41100.00 | 150.00 | 41100.00 | 41100.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
21.00 | Installation, Testing, Commissioning of CCR including termination of incoming and outgoing power and control cables, inter connection, making foundation/ suitable size of MS channel for fixing of CCR base, earthing connection etc. complete as required | 10.00 | Job |  | 5000.00 | 50000.00 | 5000.00 | 50000.00 | 50000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
22.00 | Installation, Testing and Commissioning of guidance signboards of various sizes (upto 2 m length) i/c installation of isolating transformer of suitable rating and providing secondary leads etc. i/c pedestal of 1m all around the signage board with 1:2:4 (cement, concrete, coarse) of thickness 100mm with neat cement finish plaster, testing and commissioning etc. as required as per specification. | 30.00 | Sq.Mtrs |  | 5000.00 | 150000.00 | 5000.00 | 150000.00 | 150000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
23.00 | Laying of 50 mm dia size HDPE pipe with accessories like couplers, bends, tee etc including excavation of the soil upto a depth of approx. 750 mm, back filling & making good the same as per site requirement as per the direction of engineer in charge. | 8037.00 | Mtrs. |  | 100.00 | 803700.00 | 100.00 | 803700.00 | 803700.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
24.00 | Laying of 50mm outer dia. HDPE pipe with accessories like socket, couplers, bends etc. complete with fitting, cuttings, jointing wherever applicable to connect the consecutive transformer housing boxes and transformer housing box to other fitting / location. The laying shall be in Apron/Taxiway shoulder at suitable depth along the civil construction works etc complete as required as directed by EIC. | 100.00 | Mtrs. |  | 30.00 | 3000.00 | 40.00 | 4000.00 | 3000.00 | REWINDER TECHNO ELECTRICALS
25.00 | Laying of one number PVC / XLPE / AFL/ EPR insulated & PVC / PE / PCP sheathed copper conductor power cable of grade exceeding 0.4 KV but not exceeding 11 KV of size not exceeding 25 sq. mm. in the existing cable duct / RCC/HUME/METAL/HDPE/DWC pipes etc. as required. | 22940.00 | Mtrs. |  | 10.00 | 229400.00 | 25.00 | 573500.00 | 229400.00 | REWINDER TECHNO ELECTRICALS
26.00 | Laying of one number PVC / XLPE / AFL/ EPR insulated & PVC / PE / PCP sheathed copper conductor power cable of grade exceeding 0.4 KV but not exceeding 11 KV of size not exceeding 25 sq. mm in the existing masonary open duct/trench/open surface as required. | 750.00 | Mtrs. |  | 10.00 | 7500.00 | 25.00 | 18750.00 | 7500.00 | REWINDER TECHNO ELECTRICALS
27.00 | Laying of 1 x 2.5 Sq.mm PVC insulated FRLSH copper conductor single core flexible cable of 1.1 KV grade in duct / masonary trench / RCC / HUME / METAL / GI / HDPE / DWC pipe etc. as required. | 350.00 | Mtrs. |  | 10.00 | 3500.00 | 15.00 | 5250.00 | 3500.00 | REWINDER TECHNO ELECTRICALS
28.00 | Earthing with 'B' class G. I. earth pipe 4.5 mtrs. long x 40 mm dia i/c accessories and providing masonry enclosures with cover plate having locking arrangement & watering pipe etc. i/c charcoal/ coke and salt complete as required as per specification. | 35.00 | Each |  | 6000.00 | 210000.00 | 6500.00 | 227500.00 | 210000.00 | REWINDER TECHNO ELECTRICALS
29.00 | Earthing with copper earth plate 600mm x 600mm x 3.0mm thick including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc. Including charcoal and salt complete as required. | 14.00 | Set |  | 14000.00 | 196000.00 | 16000.00 | 224000.00 | 196000.00 | REWINDER TECHNO ELECTRICALS
30.00 | Earthing with GI earth plate 600mm x 600mm x 6.0mm thick including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc. Including charcoal and salt complete as required. | 2.00 | Set |  | 6000.00 | 12000.00 | 7000.00 | 14000.00 | 12000.00 | REWINDER TECHNO ELECTRICALS
31.00 | Cutting kerf of suitable size in taxiway/runway/apron of PQC/bituminous surface i/c chipping, hammering, cleaning & drying etc. & refilling the kerf with sealant material including primer etc. as reqd. in bitumin/PQC area & laying following numbers of secondary leads:- a) 01 No. Secondary lead of size 2C x 2.5 sq.mm. | 164.00 | Mtrs. |  | 300.00 | 49200.00 | 385.00 | 63140.00 | 49200.00 | REWINDER TECHNO ELECTRICALS
32.00 | Cutting kerf of suitable size in taxiway/runway/apron of PQC/bituminous surface i/c chipping, hammering, cleaning & drying etc. & refilling the kerf with sealant material including primer etc. as reqd. in bitumin/PQC area & laying following numbers of secondary leads:- a) 2 No. Secondary lead of size 2C x 2.5 sq.mm. | 92.00 | Mtrs. |  | 350.00 | 32200.00 | 350.00 | 32200.00 | 32200.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
33.00 | Providing and fixing 25mm x 5mm copper strip in 40mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 70.00 | Mtrs. |  | 1500.00 | 105000.00 | 1670.00 | 116900.00 | 105000.00 | REWINDER TECHNO ELECTRICALS
34.00 | Providing and fixing 25mm x 5 mm G.I. strip in 40mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 10.00 | Mtrs. |  | 700.00 | 7000.00 | 1000.00 | 10000.00 | 7000.00 | REWINDER TECHNO ELECTRICALS
35.00 | Providing and fixing 25mm x 5mm copper strip on surface/in recess/existing pipe for connections etc. as required. | 168.00 | Mtrs. |  | 900.00 | 151200.00 | 1250.00 | 210000.00 | 151200.00 | REWINDER TECHNO ELECTRICALS
36.00 | Providing and fixing 25mm x 5mm G.I. strip on surface/in recess/existing pipes etc. for connections etc. as required. | 30.00 | Mtrs. |  | 300.00 | 9000.00 | 400.00 | 12000.00 | 9000.00 | REWINDER TECHNO ELECTRICALS
37.00 | Providing and fixing 6 SWG G. I. wire on surface or in recess or with HDPE pipe for loop earthing as required. | 8037.00 | Mtrs. |  | 35.00 | 281295.00 | 35.00 | 281295.00 | 281295.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
38.00 | Making connection of 5 KV grade, 1 x 6 Sq.mm Copper conductor primary cable with plug & receptacle (but excluding cost of plug & receptacles) including filling the gap with water sealed material applying HT tape of reputed make etc. complete as required at site. | 354.00 | Job |  | 50.00 | 17700.00 | 150.00 | 53100.00 | 17700.00 | REWINDER TECHNO ELECTRICALS
39.00 | Supply and Fixing of 600 V grade Plug & Receptacle, Type-II, Class 'B' connector kit for field attachment with 2C x 2.5 Sq.mm secondary lead cable. | 30.00 | Job |  | 900.00 | 27000.00 | 900.00 | 27000.00 | 27000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
40.00 | LT Panel (GLF PANEL) Supply, Installation, Testing and Commissioning of indoor cubicle LT panel as per IEC 61439, IP42, suitable for 415V+/-10%, 3 Phase, 4 wire 50 Hz AC supply system, fabricated in compartmentalized modular design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having TPN Aluminium alloy bus bars with 100% size neutral bus as that of phase bus, supported with SMC bus bar supports, with short circuit withstand capacity as per design subject to minimum 25 kA for 1 sec, bottom base channel of MS section not less than 75 mm x 40 mm, fabrication shall be done in transportable sections, entire panel shall have a common Copper earth bus bar of size as per IS 3043 subject to minimum 32 mm x 5 mm at the rear with 2 Nos. earth stud, solid/ flexible copper connections from main earth bus bar to switchgears with required size of Cooper conductors/ bus bars and control wiring with 2.5 sqmm FRLSH PVC insulated copper conductor cable, cable alleys, cable gland plates in two halves, including control and interlocking of incomers, bus coupler and providing following switchgears/ accessories as per specifications. Incomer 2 Nos. 100A, 4P MCCB, Microprocessor based release (Ics = Icu = 25kA) with inbuilt O/L , S/C & E/F protection as per specification and each incommer shall be provided with following accessories.1 Set of phase indicating LED lamps with 2 amp back up MCB.1 No. 96 x 96 sqmm Digital MFM meter and 3 nos. Cast resin CTs of ratio 100/5A , Class 0.5 accuracy and 10 VA burden, suitable to measure voltage, Ampere, Frequency, Power Factor, KVA, KW, KVAH, KWH, MDI with RS-485 port.1 Set of ON/ OFF/TRIP Indicating LED Lamps With 2 Amp MCB.Buscoupler 4P aluminium bus bars of 100A capacity with heat shrinkable coloured sleeves including SMC bus bars supports at required intervals complete for cross section, size supports & their spacing etc. for withstanding fault level of 25 KA for 1 sec. Outgoings.6 Nos. 63A 4P MCCB with built in thermal magnetic release with adjustable setting (Ics = Icu = minimum 25 KA)For each busbar section-1 Set Surge protection device Type 2 ( Class C), 4 Module, MOV type suitable for 8/ 20µs surge,Voltage Protection level Up < 1.5kV. SPD shall be with built in fuse and plugable type. For connecting SPD minimum 10sqmm copper wire must be used. The SPD shall be complient and tested from KEMA KEUR / VDE / NABL tested as per relevant IEC. | 1.00 | Job |  | 450000.00 | 450000.00 | 350000.00 | 350000.00 | 350000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
41.00 | Supply Installation ,Testing and Commissioning of IGBT, Three level PWM Design based, modular type, true online double conversion type 2 X 20 KVA UPS System in parallel configuration with harmonic filter suitable to drive constant current regulators(CCR) with 100% unbalanced load at output at full load condition, working on 3 phase, 4 Wire, 415 Volt, 50 Hz and delivering output 3 phase, 4 Wire, 415 Volt, 50 Hz , High Efficiency , having SMF Barreries to support minimum 30 minutes back up with each UPS, THD less than 3% , Power Factor not less than 0.90, having transfer time of 0 m sec, up along with all accessories i.e.breakers,DC cables, cabinets,battery racks, interconnecting links and related items etc as per site requirement for making the UPS Operational and meeting the standard of IEC and as per specification complete as required. | 1.00 | Job |  | 1100000.00 | 1100000.00 | 1100000.00 | 1100000.00 | 1100000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
42.00 | Laying of one number PVC insulated & PVC sheathed XLPE power cable of 1.1 KV grade of following size in the existing masonary open duct/surface/pipe/raceway as per specification as required a) Above 95 sqmm and upto 185 sqmm | 200.00 | Mtrs. |  | 10.00 | 2000.00 | 50.00 | 10000.00 | 2000.00 | REWINDER TECHNO ELECTRICALS
43.00 | Supplying and making end termination with brass compression gland and Aluminimum lugs for following size of PVC insulated and PVC sheathed / XLPE Aluminium conductor cable of 1.1 KV grade as required. a) 3.5 X 120 Sq.mm | 4.00 | Set |  | 500.00 | 2000.00 | 1500.00 | 6000.00 | 2000.00 | REWINDER TECHNO ELECTRICALS
44.00 | Supplying and making end termination with brass compression gland and Copper lugs for following size of PVC insulated and PVC sheathed / XLPE Copper conductor cable of 1.1 KV grade as required. a) 3C x 16 Sq. mm. | 12.00 | Set |  | 400.00 | 4800.00 | 740.00 | 8880.00 | 4800.00 | REWINDER TECHNO ELECTRICALS
45.00 | Supplying and making end termination with brass compression gland and Copper lugs for following size of PVC insulated and PVC sheathed / XLPE Copper conductor cable of 1.1 KV grade as required. a) 4C x 16 Sq. mm. | 8.00 | Set |  | 300.00 | 2400.00 | 750.00 | 6000.00 | 2400.00 | REWINDER TECHNO ELECTRICALS
46.00 | Supply and fixing of fire retardant electrically insulated synthetic mat of class A, 2.5 mm thick suitable for all voltages not exceeding 11 KV AC and 240V DC system meeting requirements of IS 15652:2006 tested for breakdown strength, tensile/elongation, aging properties, insulation resistance, effect to acid, alkaline, diesel, transformer oil & leakage current test, fire test etc. having minimum width of 1000 mm ±20 mm along with all allied materials such as Pu-resin, Chemi bound, special PVC adhesive, liquid primer etc. in what so ever quantity required to complete the job as per site conditions and as per instructions from Engineer-in-Charge. | 30.00 | Sq.Mtrs |  | 2200.00 | 66000.00 | 2200.00 | 66000.00 | 66000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED, REWINDER TECHNO ELECTRICALS
47.00 | Constructing 23cm thick brick wall masonry chamber in cement mortar 1:4 ( 1 cement : 4 coarse sand ) R.C.C top slab 10 mm thick with 1:2:4 mix ( 1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size), foundation concrete 1:4:8 mix ( 1 cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size) inside plastering 12mm thick with cement mortar 1:3 ( 1 cement : 3 coarse sand ) finished with floating coat of neat cement complete as per standard design: Inside size 1000 mm X 1000 mm x 1200 mm (LXWXD) including RCC Cover is to be provided along with hook for lifting purpose etc complete as required as per the direction of Engineer-In-Charge. | 12.00 | Job |  | 19000.00 | 228000.00 | 15000.00 | 180000.00 | 180000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
| Total in Figures |  |  |  |  | 21141565.00 |  | 22045656.00
Lowest Amount Quoted BY: REWINDER TECHNO ELECTRICALS(21141565.00)

## BOQ Summary
BOQ Summary Details Tender Title: Development of New Civil Enclave at Bihta. SH SITC of GLF system Electrical works for Apron and taxiway at Civil Enclave Bihta Airport Tender ID: 2025_AAI_261207_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | REWINDER TECHNO ELECTRICALS (BID ID -971438) | 21141565.00 | L1
| 2 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED (BID ID -963493) | 22045656.00 | L2