## BoQ1
Government eProcurement System Created By: Debdeep Dutta Created Date/Time: 06-Feb-2026 05:12 PM Tender Title: Construction of DVOR at Katihar station. SH- Provision of Electrical and Fire protection system of DVOR Katihar station. Tender ID: 2025_AAI_261218_1
Tender Inviting Authority: Dy. GM (E-E)
Name of Work: Construction of DVOR at Katihar station. SH:- Provision of Electrical and Fire protection system of DVOR Katihar station.
Contract No: 2025_AAI_261218_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Vrinda Nano Technologies Pvt Ltd (GSTN-06AABCV6699N1ZG) BID ID -964433 |  | Nexpo Power Solutions Private Limited (GSTN-NA) BID ID -958826
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | A. SH-I IP based Fire Alarm and Fire Extinguisher Supplying, installation,testing & commissioning of IP based Addressable fire alarm panel,LCD display, having minumum 01 loop card, complying relevant national fire alarm code for local fire alarm system with mimic diagram for all area / zone covered,complete with all connections. The panel shall have single mode networkcard having on board single mode fiber connectivity port, RS485 port & TCP/IP port with redundancy.The panel shall have input of 240 volts AC power supply,inbuilt automatic battery charger, 24volts, 2X12volts, 7Ah sealed lead acid maintenance free batteries sufficient for 24 hours normal power backup & working, interconnections. The panel shall be UL / EN / FM listed and along with GSM auto dialer facility (20 Nos min.) etc. as required. | 1.00 | Job | 450000.00 | 65250.00 | 65250.00 | 62000.00 | 62000.00 | 62000.00 | Nexpo Power Solutions Private Limited
2.00 | Supply, Installation, Testing & commissioning of UL / EN listed (latest version) addressable multi sensor Heat cum smoke detector base and with unique optical sensing chamber, visible LED, fully coated circuit board, superior RF / Transient protection suitable for 2 wires loop connection, complete with plug into common separate base & housing constructed of LEXAN (or polycarbonate) complete with connections etc. as required and to be installed below / above false ceiling roof and concealed space and as per enclosed specifications ,complete as required. (Cost of plug in common base shall deemed to be included in cost of detectors). | 16.00 | Job | 5000.00 | 2325.00 | 37200.00 | 3600.00 | 57600.00 | 37200.00 | Vrinda Nano Technologies Pvt Ltd
3.00 | Supply, Installation, Testing & commissioning of UL / EN listed (latest version) Addressable Manual call station (Resetable pull / push type) suitable for semi flush mounting, IP 54 for indoor use & IP 65 for outdoor use with inbuilt fault isolator / isolator module with double gang outlet box, equipment for key operated test-reset lock. Manual pull station shall be connected with two wire to SLC loop of Fire Control Panel. Cover shall be made out of LEXAN (or poly carbonate equivalent) with clear operating instruction and the word Fire appearing on the front complete with connections etc. as required and as per enclosed specifications. | 2.00 | Job | 7500.00 | 8675.00 | 17350.00 | 7500.00 | 15000.00 | 15000.00 | Nexpo Power Solutions Private Limited
4.00 | Supply, installation, testing and commissioning of UL / EN listed (latest version) Hooter-cum- strobe with inbuilt fault isolator / isolator module with adjustable sound level in the range of min. 90 db to Max. 120 db at 1M distance complete with termination etc. as required and as per enclosed specification. | 2.00 | Job | 3500.00 | 6500.00 | 13000.00 | 3800.00 | 7600.00 | 7600.00 | Nexpo Power Solutions Private Limited
5.00 | Supply and laying of 2 core , 1.5 sq. mm . Fire Survival cable , armoured copper conductor of 600/1000 V grade, insulated with specially formulated PVC , coated with special fire resistance materials and overall sheathed with special PVC, with special properties as Zero Halogen Low Smoke insulation Basic construction as per BS 7846 -2009 with accessories Llike juction boxes, shaddle, clamp, screws etc. & circuit integrity as per BS 6387 C.W.Z/BS EN 50200. | 300.00 | Meter | 46.00 | 125.00 | 37500.00 | 165.00 | 49500.00 | 37500.00 | Vrinda Nano Technologies Pvt Ltd
6.00 | SITC of 4.5 kg Co2 type fire extingusher wall mounting accessories etc complete as required. | 6.00 | Job | 6500.00 | 20650.00 | 123900.00 | 18000.00 | 108000.00 | 108000.00 | Nexpo Power Solutions Private Limited
7.00 | SITC of 4.5 kg ABC type fire extingusher wall mounting accessories etc complete as required. | 6.00 | Job | 5500.00 | 16750.00 | 100500.00 | 16000.00 | 96000.00 | 96000.00 | Nexpo Power Solutions Private Limited
8.00 | SITC of Intelligent Monitor Module complete as required. | 1.00 | Each | 5500.00 | 2800.00 | 2800.00 | 2500.00 | 2500.00 | 2500.00 | Nexpo Power Solutions Private Limited
9.00 | B. SH-II Aerosol based Fire suppression system SITC of Aerosol based Fire Suppression System consisting of Aerosol generator having aerosol mass of 60 gm shall be thermally actuated by means of aluminium alloy thermal sensor complying to UL 2775/EN 15276-1 that can be mounted over the generator itself. The housing shall be constructed of stainless steel shell. Housing shall be sealed with a non permeable membrane. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program/ (ISO-17025 & ISO-15779). Fixed Condensed Aerosol Systems per NFPA 2010. Design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Thermal Sensor. | 8.00 | Job | 28850.00 | 25500.00 | 204000.00 | 30000.00 | 240000.00 | 204000.00 | Vrinda Nano Technologies Pvt Ltd
10.00 | SITC of Aerosol Generator having aerosol mass of 500gm shall be electrically actuated by means of Fire Alarm cum Release Panel. The housing shall be constructed of stainless steel shell.Housing shall be sealed with a non permeable membrane. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program/(ISO-17025 & ISO-15779). Aerosol generators shall be listed by Underwriter’s Laboratories (UL) to UL Subject 2775 / EN 15276-1 covering Fixed Condensed Aerosol Systems per NFPA 2010. Design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Gland. | 4.00 | Job | 70556.00 | 4620.00 | 18480.00 | 42000.00 | 168000.00 | 18480.00 | Vrinda Nano Technologies Pvt Ltd
11.00 | SITC of Aerosol Generator having aerosol mass of 1500gm shall be electrically actuated by means of Fire Alarm cum Release Panel. The housing shall be constructed of stainless steel shell.Housing shall be sealed with a non permeable membrane.Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program/(ISO-17025 & ISO-15779). Aerosol generators shall be listed by Underwriter’s Laboratories (UL) to UL Subject 2775 / EN 15276-1 covering Fixed Condensed Aerosol Systems per NFPA 2010. Design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Gland. | 5.00 | Job | 179568.00 | 110850.00 | 554250.00 | 100000.00 | 500000.00 | 500000.00 | Nexpo Power Solutions Private Limited
12.00 | SITC of Aerosol Generator having aerosol mass of 2500gm shall be electrically actuated by means of Fire Alarm cum Release Panel. The housing shall be constructed of stainless steel shell.Housing shall be sealed with a non permeable membrane. Aerosol generated shall be potassium based. Agent shall have no ozone depletion potential and no global warming potential. Agent shall be listed by the US EPA under the SNAP program/(ISO-17025 & ISO-15779). Aerosol generators shall be listed by Underwriter’s Laboratories (UL) to UL Subject 2775 / EN 15276-1 covering Fixed Condensed Aerosol Systems per NFPA 2010. Design density of the aerosol should be less than 100g/cu.mtr for Class A, B & C fires as per NFPA. The Aerosol generator should have self life of 15 years. Aerosol generator shall be supplied with Stainless steel Bracket & Gland. | 8.00 | Job | 179568.00 | 135250.00 | 1082000.00 | 142500.00 | 1140000.00 | 1082000.00 | Vrinda Nano Technologies Pvt Ltd
13.00 | Supply, installation testing & commissioning of UL Listed Conventional agent release control panel with battery back up for 30 minutes in alarm condition. Panel shall be of 04 zones with provision to integrate necessary manual release switch, zone indication, fault indication, alarm display. Quoted rate shall include necessary battery & interconnections. | 5.00 | Job | 115000.00 | 65200.00 | 326000.00 | 38500.00 | 192500.00 | 192500.00 | Nexpo Power Solutions Private Limited
14.00 | Supply, Installation, testing & Commissioning Of Conventional type UL Listed Optical smoke detectors complete with base, locking screw etc. | 8.00 | Job | 2500.00 | 5780.00 | 46240.00 | 3200.00 | 25600.00 | 25600.00 | Nexpo Power Solutions Private Limited
15.00 | Supply, Installation, Testing & Commissioning Of Conventional type UL Listed Heat combination detectors (ROR and Fixed temperature) complete with base, locking screw etc. | 8.00 | Job | 2500.00 | 5149.00 | 41192.00 | 3300.00 | 26400.00 | 26400.00 | Nexpo Power Solutions Private Limited
16.00 | Supply, installation, testing & commissioning of UL Listed Manual call point, Break glass type and body of polycarbonate along with back box with necessary interconnection with the gas release panel. The manual call point must be connected in between any one selected zone. | 5.00 | Job | 5700.00 | 5500.00 | 27500.00 | 3500.00 | 17500.00 | 17500.00 | Nexpo Power Solutions Private Limited
17.00 | Supply, installation, testing & commissioning of UL Listed Manual Release Switch (Green) with double action having body of metal alongwith backbox and necessary interconnection with the gas release panel. | 5.00 | Job | 6200.00 | 16500.00 | 82500.00 | 58250.00 | 291250.00 | 82500.00 | Vrinda Nano Technologies Pvt Ltd
18.00 | Supply, installation, testing & commissioning of UL Listed Manual Abort Switch (Yellow) with double action having body of metal alongwith backbox and necessary interconnection with the gas release panel. | 5.00 | Job | 6200.00 | 13500.00 | 67500.00 | 10000.00 | 50000.00 | 50000.00 | Nexpo Power Solutions Private Limited
19.00 | Supply, installation, testing & commissioning of UL Listed Conventional Sounder cum strobe with 24V DC, Audiable Sound 75 db @ 1 mtr range (16 V DC). It is used for Fire, Burglar & Emergency Alarm System, Low current consume @ 47 -73 mA Candela: flashing every second, 4 candela settings :15 /30 /75/110cd output and 2 different tone audiable sound conventional Electronic Hooter cum sounder along with backbox, having body of polycarbonate. | 5.00 | Job | 6800.00 | 2750.00 | 13750.00 | 2500.00 | 12500.00 | 12500.00 | Nexpo Power Solutions Private Limited
20.00 | Supply and Laying of 2 core 1.5 sq. mm. FRLS armored Cable with accessories Like juction boxes, shaddle, clamp, screws etc. | 300.00 | Mtr | 47.00 | 165.00 | 49500.00 | 125.00 | 37500.00 | 37500.00 | Nexpo Power Solutions Private Limited
21.00 | C. SH-III LIGHTNING PROTECTION SYSTEM Supply, Installation, Testing & Commissioning of Conventional Vertical Air terminal Lightening Arrestor, made of 1 inch dia 5 feet length soild 90% or more pure copper rod, positioned above and fixed/joined/welded with 100 MM dia. FRP, 2 Mtr. Length mounted on 100 MM dia. GI Mast, 2 Mtr. Length Class B GI pipe and installing the same on ground including providing GI base plate of suitable thickness at bottom, making plinth, RCC foundation as per technical specification or as specified by EIC or his authorised representative. The structure must be supported by providing suitable no. of Stay wires i/c connecting the stay wires to the GI Pipe, providing and grouting of stays etc. complete as required. | 4.00 | Job | 53000.00 | 150000.00 | 600000.00 | 45000.00 | 180000.00 | 180000.00 | Nexpo Power Solutions Private Limited
22.00 | Supply, Installation, Testing & Commissioning of Fixing clamp with tensioning strap, for fixing Combi supporting tubes, e.g. to antenna masts or other pipes. Without spacer. | 12.00 | Job | 2484.00 | 4625.00 | 55500.00 | 3500.00 | 42000.00 | 42000.00 | Nexpo Power Solutions Private Limited
23.00 | Supply, Installation, Testing & Commissioning of HVI long Conductor (on a reel), black HVI Conductor High-voltage-resistant insulated downconductor for keeping the separation distance from conductive parts according to EN 62305-3 Equivalent separation distance s =< 75 cm (in air) or s =< 150 cm (solid building material). (5 Feet Air termination to nearby earthing). | 125.00 | Meter | 4500.00 | 8500.00 | 1062500.00 | 7200.00 | 900000.00 | 900000.00 | Nexpo Power Solutions Private Limited
24.00 | Supply, Installation, Testing & Commissioning of Conductor holder with tensioning strap, for fastening the HVI Conductor (black) or HVI light Conductor e.g. at pipes.Type with metal conductor holder. (For HVI Conductor) | 40.00 | Job | 282.00 | 1340.00 | 53600.00 | 1250.00 | 50000.00 | 50000.00 | Nexpo Power Solutions Private Limited
25.00 | Supply, Installation, Testing & Commissioning of Connection kit for HVI long Conductor, D 23 mm for installation inside the supporting tube, StSt,Connection elements for sealing the HVI long Conductor on both ends; to establish the sealing end of the conductor in the supporting tube (head piece) and connection element for other parts of the external lightning protection system or earth-termination system (four heat shrinkable sleeves included (2x black, 2x grey). (For HVI Conductor Connetion to Air Termination). | 4.00 | Job | 8400.00 | 12325.00 | 49300.00 | 8500.00 | 34000.00 | 34000.00 | Nexpo Power Solutions Private Limited
26.00 | Supplying and laying of electrical hose pipe in a 50mm diameter, require it to be GI pipe (Galvanized Iron) conforming to IS-1239 for sizes ISI marked. (For underground laying of HVI Cable till Earthing) | 60.00 | Mtr | 684.00 | 1600.00 | 96000.00 | 800.00 | 48000.00 | 48000.00 | Nexpo Power Solutions Private Limited
27.00 | Supply, Installation, Testing & Commissioning of 25 mm X 3 mm copper strip at 0.75 metre below ground as strip earth electrode in 40 mm dia G.I.pipe from earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm). (For Interconnecting all Earthing for LA) | 60.00 | Mtr | 1385.00 | 1385.00 | 83100.00 | 1350.00 | 81000.00 | 81000.00 | Nexpo Power Solutions Private Limited
28.00 | Supply, Installation, Testing & Commissioning of 25 mm X 3 mm copper strip at above surface near DVOR Ground for maximum earthing subdistribution. (For Interconnecting and for maximum surface utilization under DVOR MS Structure area for earth bonding). | 60.00 | Mtr | 1100.00 | 1100.00 | 66000.00 | 1100.00 | 66000.00 | 66000.00 | Nexpo Power Solutions Private Limited, Vrinda Nano Technologies Pvt Ltd
29.00 | Supply, Installation, Testing & Commissioning of POE surge arrester of class D M surge arrester, class D SPD class: type 2 / P1 Tested to EN 61643-21 For universal use according to EN 50173 for all data services up to 57 V d.c. For protecting four pairs of data network interfaces via RJ45 sockets, for single-user application or application in distribution cabinets, space-saving, width of 19 mm. Type: DPA M CLD RJ45B 48. NABL/KEMA. | 4.00 | Job | 5800.00 | 13500.00 | 54000.00 | 5500.00 | 22000.00 | 22000.00 | Nexpo Power Solutions Private Limited
30.00 | Supply, Installation, Testing & Commissioning of RJ45B 48 surge arrester of class D M surge arrester, class D SPD class: type 2 / P1 Tested to EN 61643-21 For universal use according to EN 50173 for all data services up to 57 V d.c. For protecting four pairs of data network interfaces via RJ45 sockets, for single-user application or application in distribution cabinets, space-saving, width of 19 mm. Type: DPA M CLD RJ45B 48. NABL/KEMA | 8.00 | Job | 5800.00 | 1650.00 | 13200.00 | 3500.00 | 28000.00 | 13200.00 | Vrinda Nano Technologies Pvt Ltd
31.00 | SITC of Lightning strike counter used to count the digital impulse currents. Device for installation preferably on down conductors of the lightning protection system or between equipotential bonding bar and earth-termination system. Operating current (8/20 μs)- 1 kA, Max. discharge current (10/350 μs)- 100 kA, Clamping range- Rd/Fl 8-10/30 mm, Number of occurrences up to 999, Operating temperature range (TU) -20 °C ... +60 °C. Lithium battery 3V, CR123A, | 2.00 | Job | 40350.00 | 25300.00 | 50600.00 | 20000.00 | 40000.00 | 40000.00 | Nexpo Power Solutions Private Limited
32.00 | D. SH-IV LIGHTNING PROTECTION SYSTEM (SUBSTATION BUILDING) Supply, Installation, Testing & Commissioning of 700 mm air termination rod. Diameter Ø- 8 mm, Cross-section- 50 mm2, of Material- AlMgSi Parallel Connectors for (700mm air terminal) connecting two conductors in parallel manner. Material- StSt, with clamping range- Rd / Rd 7-10 mm & Complied as per Standard EN 62561-1. | 6.00 | Job | 200.00 | 2500.00 | 15000.00 | 1500.00 | 9000.00 | 9000.00 | Nexpo Power Solutions Private Limited
33.00 | Supply, Installation, Testing & Commissioning of Air-termination rod clamps for connecting air-termination rods with one or two conductors. Material of clamp Al, with clamping range of air-termination rod 16 mm and Clamping range of conductor Rd 2x8-10 mm, & Complied as per Standard EN 62561-1. | 12.00 | Job | 500.00 | 750.00 | 9000.00 | 670.00 | 8040.00 | 8040.00 | Nexpo Power Solutions Private Limited
34.00 | Supply, Installation, Testing & Commissioning of Side Wall Clamp | 6.00 | Job | 850.00 | 1150.00 | 6900.00 | 810.00 | 4860.00 | 4860.00 | Nexpo Power Solutions Private Limited
35.00 | Roof Conductor & Roof Conductor Holder Supply, Installation, Testing & Commissioning of Roof Conductor of Diameter Ø- 8 mm, Cross-section- 50 mm2, of Material- AlMgSi & Complied as per Standard EN 62561-2. | 100.00 | Mtr | 200.00 | 550.00 | 55000.00 | 350.00 | 35000.00 | 35000.00 | Nexpo Power Solutions Private Limited
36.00 | Supply, Installation, Testing & Commissioning of Conductor holder with a slotted saddle clamp, for fixing round conductors. For use with different materials, e.g. Al, StSt, St/tZn and Cu, fixed conductor routing, with female thread. With accessories Screw and Gitty, Material SS (M5 x 50mm) | 50.00 | Job | 282.00 | 550.00 | 27500.00 | 375.00 | 18750.00 | 18750.00 | Nexpo Power Solutions Private Limited
37.00 | Supply, Installation, Testing & Commissioning of Roof conductor holder FB2 for flat roofs with concrete block-C35/45 with double conductor holder- Rd 8 mm fixed,Dimension- 141 x 86 x 70 mm | 50.00 | Job | 240.00 | 750.00 | 37500.00 | 525.00 | 26250.00 | 26250.00 | Nexpo Power Solutions Private Limited
38.00 | Supply, Installation, Testing & Commissioning of Universal connector of Material- StSt, with clamping range- 8-10mm, with truss head screw M10x35 mm & Complied as per Standard EN 62561-1. | 30.00 | Job | 370.00 | 375.00 | 11250.00 | 260.00 | 7800.00 | 7800.00 | Nexpo Power Solutions Private Limited
39.00 | FOR DOWN CONDUCTOR SITC of Down Conductor of Diameter Ø- 8 mm, Cross-section- 50 mm2, of Material- AlMgSi & Complied as per Standard EN 62561-2., | 40.00 | Mtr | 200.00 | 625.00 | 25000.00 | 350.00 | 14000.00 | 14000.00 | Nexpo Power Solutions Private Limited
40.00 | Supply, Installation, Testing & Commissioning of Conductor holder with a slotted saddle clamp, for fixing round conductors. For use with different materials, e.g. Al, StSt, St/tZn and Cu, fixed conductor routing, with female thread. With accessories Screw and Gitty, Material SS (M5 x 50mm) | 40.00 | Job | 282.00 | 565.00 | 22600.00 | 850.00 | 34000.00 | 22600.00 | Vrinda Nano Technologies Pvt Ltd
41.00 | SITC of UNI Disconnecting Clamps with intermediate plate for round and flat conductor of Material- StSt, Material thickness- 2.5 mm, with clamping range- Rd / Fl 8-10 / 30 mm, & Complied as per Standard IEC/EN 62561-1., | 6.00 | Job | 412.00 | 2260.00 | 13560.00 | 750.00 | 4500.00 | 4500.00 | Nexpo Power Solutions Private Limited
42.00 | SITC of GI flat (25x5 mm) for interconnection of earth pit & termination to earth pit Weight 1.2 kg/m (approx.) Cross Section 150 mm2 ,Coating thickness Avg. 70 microns. As per IEC 62561-2 ,Material Hot dipped Galvanized Iron | 25.00 | Mtr | 290.00 | 350.00 | 8750.00 | 225.00 | 5625.00 | 5625.00 | Nexpo Power Solutions Private Limited
43.00 | SITC of GI strip holder of material- Dow moulded compound, having height- 19mm, Slot Size- 25x5 mm. | 6.00 | Job | 150.00 | 500.00 | 3000.00 | 200.00 | 1200.00 | 1200.00 | Nexpo Power Solutions Private Limited
44.00 | Providing joints by using brazing technique on 25 mm X 3 mm copper strip on surface or in recess for connections to another copper earth strip for interconnection to all earth's of Lightening Arrestors, counterpoise , Equipment and Electrical power supply earthing etc. as required. | 200.00 | Job | 450.00 | 1050.00 | 210000.00 | 1100.00 | 220000.00 | 210000.00 | Vrinda Nano Technologies Pvt Ltd
45.00 | E. SH-V EARTHING, SPD & LIDGS SITC of Copper bonded rod with Low carbon steel, high tensile strength copper bonded rod with min 254 microns of copper plating, UL listed with company name marked on rod. Diameter- 17.2 mm, Length- 3 meters, Material- Copper Bonded, Coating thickness- 250 microns, min, Approvals- Tested acc. IEC / EN 62561-2, UL 467., 20 kg backfilled compound, - Material Carbon based backfill/earthing compound, Fulgurite formation test at direct lightning (10/350 μs), lightning long duration test at- 100C No fulgurites/Pass, Environmentally Friendly ROHS certified, Resistivity- < 0.12 ΩM, Complying Standard- IEC 62561-7 , Testing Approvals Certified from- NABL accredited Laboratories, StSt 316 grade clamp to terminate the load on earth electrode. Dimension- 160x35x3 mm, Poly plastic pit cover of material- Polymer Body & Cover, Product Code- HEP, Dimensions- 308 mm (L) x 308 mm (W) X 214 mm (H), Weight 2.5 kg (5.50 LBS). | 12.00 | Set | 10008.00 | 28500.00 | 342000.00 | 22500.00 | 270000.00 | 270000.00 | Nexpo Power Solutions Private Limited
46.00 | Supply, Installation, Testing and Commissioning of Cu plate earthing station including excavation, back filling, using 600x600x3.15 mm GI Plate with Earthing Enchancement Compound / Salt & Charcol filling along with complete 40 mm dia GI perferated water pipe of 3m long with funnel.As per specifications and in conformity with IS 3043. | 6.00 | Set | 23600.00 | 22500.00 | 135000.00 | 20000.00 | 120000.00 | 120000.00 | Nexpo Power Solutions Private Limited
47.00 | SITC of GI flat (25x5 mm) for interconnection of earth pit & termination to earth pit Weight 1.2 kg/m (approx.) Cross Section 150 mm2 ,Coating thickness Avg. 70 microns. As per IEC 62561-2 ,Material Hot dipped Galvanized Iron | 50.00 | Mtr | 290.00 | 300.00 | 15000.00 | 235.00 | 11750.00 | 11750.00 | Nexpo Power Solutions Private Limited
48.00 | SITC of Providing of Plastic Corrosion Protection strip: Approx 1.1 mm thick Width 50mm. Made of petrolatum- coated chemical fibre fabric | 2.00 | Job | 378.00 | 3500.00 | 7000.00 | 2500.00 | 5000.00 | 5000.00 | Nexpo Power Solutions Private Limited
49.00 | SITC of 3 Phase / Type1+2 (KEMA Certified) Lightning current & Surge Protection Device at mains LT panel (3 phase, 415 V) for (L-N) Single- pole combined lightning current and surge arrester, Type 1 SPD The device shall be non-exhausting metal encapsulated, spark gap based technology and tested as per latest and valid IEC 61643-11:2011 or EN 61643-11:2012 standards. It shall be capable to discharge Lightning current (10/350µs) of 25kA (L-N) and 100kA(N-E) and voltage protection level of device shall be ≤ 1.5 KV,. The device shall have inbuilt fuse for L N. Follow current extinguishing capability [L- N]/[N-PE] : 100kArms / 100Arms. The device shall have built in fuse and operation of SPD shall be independent of Line current for L N SPD. The short circuit with stand capability of the device shall be 100 KArms for L-N SPD. The device shall have mechanical indication for both the states (green for ‘healthy’ and red for failure) on L-N and N-PE. The device shall be certified by KEMA /VDE or NABL lab as per IEC 61643- 11:2011 or or EN 61643-11:2012 for testing of all parameter at 10/350 µs and 8/20 µs. with transparent enclosure IP65 | 2.00 | Job | 40380.00 | 120000.00 | 240000.00 | 110000.00 | 220000.00 | 220000.00 | Nexpo Power Solutions Private Limited
50.00 | Supply, Installation, Testing and Commissioning of Single Phase modular type Surge Protection Device (CLASS- B,1,Stage- 1/primary) with minimum lightning impulse current (limp) of 100KA (10/350 micro seconds) neutral to earth, 50 KA (10/350 micro sec) line to neutral, limiting voltage less than 1.5 KV, to be installed in parrallel at the mains panel of power entry point including making connection of surge protection device in parallel to the busbar of the main electrical panel using 16 Sq mm single core PVC insulated flexible copper conductor cables, in IP55 grade powder coated metal enclosure with 63 Amp. service/ bypass changeover switch, on the mains power entry point at the incomers including all accessories such as suitable rating MCBs, making end terminations,fixing/mounting arrangement of SPD. | 4.00 | Job | 34960.00 | 95400.00 | 381600.00 | 72500.00 | 290000.00 | 290000.00 | Nexpo Power Solutions Private Limited
51.00 | Supply, Installation, Testing and Commissioning of single phase surge protection device type 2 / class II M TT 2P 320 FM surge arrester Modular and pluggable two pole surge arrester for single-phase 230 V TT and TN systems, width: 2 modules With remote signalling contact Type 2 SPD according to EN 61643-11 Max. continuous operating voltage: 320 V a.c. Voltage protection level: <= 1.5 kV Nominal discharge current: 20 kA Short circuit strength: 25 kA rms Energy coordinated according to IEC 62305-4 with arresters of the Red/Line series Fault indication. Type: VT2 M TT 2P 320 FM. Certified by CE, KEMA and UL. Surge protection devices shall be enclosed in polycarbonate enclosure of IP 65 with accessories | 4.00 | Job | 5200.00 | 26500.00 | 106000.00 | 62000.00 | 248000.00 | 106000.00 | Vrinda Nano Technologies Pvt Ltd
52.00 | Supply, Installation, Testing & Commissioning of 100 KA isolating spark gap according to IEC 62561-3:2011 (81/387/CDV) / EN 62561-3 for lightning equipotential bonding according to IEC 62305-3, particularly for use in potentially explosive atmospheres up to zone 1 or 21 IECEx / ATEX certification (2014/34/EU) Ex marking according to IEC / EN 60079: Gas II 2G Ex d IIC T6 IEC / EN 61241: Dust II 2D Ex tD A21 IP67 T 80°C Lightning impulse current (10/350) : 100 kA Class of lightning current carrying capability acc. to IEC 62561-3: 2011 (81/387/CDV) / EN 62561-3: H Nominal discharge current (8/20): 100 kA Rated impulse sparkover voltage: <= 1.25 kV Power frequency sparkover voltage (50Hz): <= 0.5 kV Rated power frequency withstand voltage (50 Hz): <= 250 V Rated discharge current (50 Hz): 500 A / 0.2 sec. (Tu <= 45°C) Degree of protection: IP67 Enclosure: M10 x 25 screw and spring washer on both ends | 4.00 | Job | 20300.00 | 23000.00 | 92000.00 | 16500.00 | 66000.00 | 66000.00 | Nexpo Power Solutions Private Limited
53.00 | Supply, Installation, Testing & Commissioning of 32 Amps Multistage 1 phase Series Power Filter with neutral protection with MOV 40 KA + 25 KA rating in IP55 grade Powder coated metal enclosure with a 63 Amps service bypass changeover switch and copper inter connection cables and end termination etc. as required to be installed at input of the UPS/Voltage stabilizer in series complete as required with CE Certified including Accessories Kit. (Secondary Protection) | 6.00 | Job | 14050.00 | 68000.00 | 408000.00 | 70000.00 | 420000.00 | 408000.00 | Vrinda Nano Technologies Pvt Ltd
54.00 | Supply and Laying of 1C X 6 sq.mm FRLS Copper flexible wire | 100.00 | Mtr | 110.00 | 125.00 | 12500.00 | 110.00 | 11000.00 | 11000.00 | Nexpo Power Solutions Private Limited
55.00 | Supply and Laying of 1C X 10 sq.mm FRLS Copper flexible wire | 100.00 | Mtr | 191.00 | 250.00 | 25000.00 | 165.00 | 16500.00 | 16500.00 | Nexpo Power Solutions Private Limited
56.00 | Supply and Laying of 1C X 16 sq.mm FRLS Copper flexible wire | 100.00 | Mtr | 295.00 | 300.00 | 30000.00 | 250.00 | 25000.00 | 25000.00 | Nexpo Power Solutions Private Limited
57.00 | SITC of Low Impedance Digital Grounding System 240kA Three Phase four wire LIDGS 4th Generation equipment Grounding & bonding system with built in 100% Lightning and Surges, static charge, Noises, ESD, EPR and abnormal electrical characteristics eliminator which enter from power and other service lines and ensuring clear bonding potential (earth to Neutral voltage) less than 1.0V, a digital 3 Digit LCD Impulse real Date time Counter with threshold of IKA, selfhealth visual status indicator, built Zero leakage Current based solution. Lightning Impulse Current Discharge Capability up to 12 KA (10/350μsec) Surge Discharge Current Capability up to 40KA (8/20μsec) 7 Modes of Protection (LI-N, N-PE, LI PE) total surge handling capacity 240KA Short-circuit extinguishing and limiting capabilities up to 25KArms without tripping of Let- through-energy of less than 01 Joule in a Prewired pulverulent body painted metal enclosure to be connected in parallel to the power supply circuit, Conforming solution and Accessories Kit.is CE NABL IEC 61643-11-2011. | 1.00 | Job | 265750.00 | 225000.00 | 225000.00 | 248000.00 | 248000.00 | 225000.00 | Vrinda Nano Technologies Pvt Ltd
| Total in Figures |  |  |  |  | 7558372.00 |  | 6930725.00
Lowest Amount Quoted BY: Nexpo Power Solutions Private Limited(6930725.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of DVOR at Katihar station. SH- Provision of Electrical and Fire protection system of DVOR Katihar station. Tender ID: 2025_AAI_261218_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Nexpo Power Solutions Private Limited (BID ID -958826) | 6930725.00 | L1
| 2 | Vrinda Nano Technologies Pvt Ltd (BID ID -964433) | 7558372.00 | L2