## BoQ1
Government eProcurement System Created By: Hrithik Kumar Singh Created Date/Time: 17-Oct-2025 02:33 PM Tender Title: RELOCATION OF ELECTRICAL SUBSTATION Tender ID: 2025_GAIL_246477_1
Tender Inviting Authority: Sr Officer (C&P), GAIL (India) Limited, Vadodara
Name of Work: RELOCATION OF ELECTRICAL SUBSTATION EQUIPMENT AND SITC OF NEW ELECTRICAL EQUIPMENT
Contract No: GAIL/BDA/CNP/HKS/25/W-18 (Tender Id: 2025_GAIL_246477_1)
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | RAJ ELECTRICALS (GSTN-24AAHFR2079K1ZY) BID ID -904057 |  | EVERCREST PROJECTS PVT LTD (GSTN-24AADCE7826L1ZE) BID ID -904768 |  | RAKESH TRIPATHI (GSTN-NA) BID ID -904812
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, Installation, Testing, and Commissioning of Indoor Type 11KV 800A ICOG Microprocessor based VCB (Internal Arc Tested as per IEC 62271-200) with Arc Flash Relay, Feeder & Transformer Auxiliary Protection and Multifunction Meter (Details as per Technical Specifications sheet), including protections such as 50, 51, 50N, 51N, 27, 59, WTI, OTI, BUCHHOLZ TMP, Master Trip Relay 86. The panel must support Short-Time Current (25 kA for 0.1 sec). This should have communication capability through Modbus/TCP-IP/Ethernet for data (Contact health, Relay, status, Faults, tripping etc.). OEM designed and tested panel. Make should be same as LT Panel. | 1.00 | NOS |  | 635250.00 | 749595.00 | 664000.00 | 783520.00 | 990000.00 | 1168200.00 | 749595.00 | RAJ ELECTRICALS
2.00 | Supply, Installation, Testing and Commissioning of 11KV, 800A HTMC Panel with VCB as per the attached technical specifications along with the required discom (MGVCL) approvals, testing etc. | 1.00 | NOS |  | 390863.00 | 461218.34 | 463200.00 | 546576.00 | 414000.00 | 488520.00 | 461218.34 | RAJ ELECTRICALS
3.00 | Dismantling, Shifting, Installation, Testing and Commissioning of 11000/433V, 400 KVA OLTC Transformer including associated works and overcoming site-specific hurdles as per scope of work, along with supply of temporary Diesel Engine Generator (DEG) during the shutdown period, as per terms and conditions mentioned in the scope of work. | 1.00 | NOS |  | 78750.00 | 92925.00 | 68750.00 | 81125.00 | 270000.00 | 318600.00 | 81125.00 | EVERCREST PROJECTS PVT LTD
4.00 | Dismantaling, Shifting, Installation, Testing and Commissioning of 380 KVA Diesel Generator set including associated works and overcoming site-specific hurdles. New MGVCL tested CT and Energy meter (to be procured as per line item 37) to be installed in the LT Panel. | 1.00 | NOS |  | 78750.00 | 92925.00 | 62500.00 | 73750.00 | 207000.00 | 244260.00 | 73750.00 | EVERCREST PROJECTS PVT LTD
5.00 | Supply, Installation, Testing and Commissioning of LT PANEL, floor mounted with cable entry from top (TTA design based on IEC 61439, 415V AC, 50kA, 50 Hz) along with ASVG+APFC system, base frame and various hardware accessories as per attached LT Panel SOQ & Scope of Work. Make should be same as VCB. | 1.00 | NOS |  | 3413550.00 | 4027989.00 | 3673944.00 | 4335253.92 | 1530000.00 | 1805400.00 | 1805400.00 | RAKESH TRIPATHI
6.00 | Supply, installation, testing, and commissioning of an MCC panel for the Fire Water Pump House, with cable entry from the top, along with a base frame and various hardware accessories, as per the attached FWPH Panel Annexure and Scope of Work. The scope also includes the removal of old starters and panels. | 1.00 | NOS |  | 446775.00 | 527194.50 | 875736.00 | 1033368.48 | 630000.00 | 743400.00 | 527194.50 | RAJ ELECTRICALS
7.00 | Supply, installation, commissioning, and end-to-end integration of an Energy Management System (EMS) software, including configuration devices; a 65-inch wall-mounted LED display with a tilt-adjustable bracket (X and Y axes) and Z-axis extendibility; workstation; latest compatible operating system; all necessary hardware; and other required accessories, with lifetime licensing, as per the scope of work. Make should be same as VCB, LT Panel. | 1.00 | NOS |  | 341250.00 | 402675.00 | 1869000.00 | 2205420.00 | 900000.00 | 1062000.00 | 402675.00 | RAJ ELECTRICALS
8.00 | Supply, laying, testing, and commissioning of 2R × 3C × 150 sq.mm, 11 kV grade (E) XLPE, FRLS aluminium conductor armoured cable, with a permissible quantity variation of ±10%, along with proper tagging, marking, and securing with cable ties. Proper cable scheduling is to be provided. | 60.00 | MTR |  | 1108.00 | 78446.40 | 2754.00 | 194983.20 | 900.00 | 63720.00 | 63720.00 | RAKESH TRIPATHI
9.00 | Supply, Laying, Testing and Commissioning of 2R X 3.5C X 300 SQMM 1.1KV GRADE XLPE, FRLS Aluminium conductor armoured cable (TFMR to LT Panel, LT Panel TO MCC, DEG) (200 mtr each run) in the existing masonry open duct/trench, Above 185 sq. mm and upto 400 sq. mm, with a permissible variation of ±10% in quantity, along with proper tagging, marking, and securing with cable ties. Proper cable scheduling is to be provided. | 400.00 | MTR |  | 1351.00 | 637672.00 | 3506.00 | 1654832.00 | 1710.00 | 807120.00 | 637672.00 | RAJ ELECTRICALS
10.00 | Supply, Laying, Testing and Commissioning of 2R X 3.5C X 185 SQMM 1.1KV GRADE XLPE, FRLS Aluminium conductor armoured cable (LT Panel to MP HALL) (250Mtr Each run) in the existing masonry open duct/trench, Above 95 sq. mm and upto 185 sq. mm, with a permissible variation of ±10% in quantity, along with proper tagging, marking, and securing with cable ties. Proper cable scheduling is to be provided. | 500.00 | MTR |  | 888.00 | 523920.00 | 2326.00 | 1372340.00 | 1170.00 | 690300.00 | 523920.00 | RAJ ELECTRICALS
11.00 | Supply, Laying, Testing and Commissioning of 3.5C X 185 SQMM 1.1KV GRADE XLPE, FRLS Aluminium conductor armoured cable (LT Panel to FWPH, HVAC) in the existing masonry open duct/trench, Above 95 sq. mm and upto 185 sq. mm, with a permissible variation of ±10% in quantity, along with proper tagging, marking, and securing with cable ties. Proper cable scheduling is to be provided. | 300.00 | MTR |  | 888.00 | 314352.00 | 1163.00 | 411702.00 | 1170.00 | 414180.00 | 314352.00 | RAJ ELECTRICALS
12.00 | Supply, Laying, Testing and Commissioning of 3.5C X 50 SQMM 1.1KV GRADE XLPE, FRLS Aluminium conductor armoured cable (LT Panel to GH) in the existing masonry open duct/trench, Above 35 sq. mm and upto 95 sq. mm, with a permissible variation of ±10% in quantity, along with proper tagging, marking, and securing with cable ties. Proper cable scheduling is to be provided. | 75.00 | MTR |  | 319.00 | 28231.50 | 436.00 | 38586.00 | 360.00 | 31860.00 | 28231.50 | RAJ ELECTRICALS
13.00 | Supply, Laying, Testing and Commissioning of 4C X 16 SQMM 1.1KV GRADE XLPE, FRLS Aluminium conductor armoured cable (LT Panel to SECURITY GATE & other locations) in the existing masonry open duct/trench, Upto 35 sq. mm, with a permissible variation of ±10% in quantity, along with proper tagging, marking, and securing with cable ties. Proper cable scheduling is to be provided. | 190.00 | MTR |  | 161.00 | 36096.20 | 234.00 | 52462.80 | 180.00 | 40356.00 | 36096.20 | RAJ ELECTRICALS
14.00 | Supply, Laying, Testing and Commissioning of 3C X 2.5 SQMM 1.1KV GRADE XLPE, FRLS Copper armoured cable in the existing masonry open duct/trench, Upto 35 sq. mm, with a permissible variation of ±10% in quantity, along with proper feruling, marking, and securing with cable ties. Proper cable scheduling is to be provided. | 150.00 | MTR |  | 146.00 | 25842.00 | 189.00 | 33453.00 | 1350.00 | 238950.00 | 25842.00 | RAJ ELECTRICALS
15.00 | Supplying and making end termination with brass double compression gland and bi-metallic lugs for following size of XLPE insulated, PVC sheathed Copper conductor cable of 1.1 KV grade as required, 3 X 2.5 sq. mm (25mm) | 4.00 | Each |  | 651.00 | 3072.72 | 1123.00 | 5300.56 | 450.00 | 2124.00 | 2124.00 | RAKESH TRIPATHI
16.00 | Supplying and making end termination with brass double compression gland and aluminuim lugs for following size of XLPE insulated, PVC sheathed aluminium conductor cable of 1.1 KV grade as required, 4 X 16 sq. mm (25mm) | 4.00 | Each |  | 786.00 | 3709.92 | 679.00 | 3204.88 | 1350.00 | 6372.00 | 3204.88 | EVERCREST PROJECTS PVT LTD
17.00 | Supplying and making end termination with brass double compression gland and aluminuim lugs for following size of XLPE insulated, PVC sheathed aluminium conductor cable of 1.1 KV grade as required, 3½ X 50 sq. mm (35mm) | 2.00 | Each |  | 1178.00 | 2780.08 | 1188.00 | 2803.68 | 1350.00 | 3186.00 | 2780.08 | RAJ ELECTRICALS
18.00 | Supplying and making end termination with brass double compression gland and aluminuim lugs for following size of XLPE insulated, PVC sheathed aluminium conductor cable of 1.1 KV grade as required, 3½ X 185 sq. mm (57mm) | 8.00 | Each |  | 2921.00 | 27574.24 | 2442.00 | 23052.48 | 2700.00 | 25488.00 | 23052.48 | EVERCREST PROJECTS PVT LTD
19.00 | Supplying and making end termination with brass double compression gland and aluminuim lugs for following size of XLPE insulated, PVC sheathed aluminium conductor cable of 1.1 KV grade as required, 3½ X 300 sq. mm (70mm) | 8.00 | Each |  | 4354.00 | 41101.76 | 3906.00 | 36872.64 | 3600.00 | 33984.00 | 33984.00 | RAKESH TRIPATHI
20.00 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV (E) grade as required : 120- 185 sq. mm | 6.00 | Each |  | 6300.00 | 44604.00 | 16030.00 | 113492.40 | 15300.00 | 108324.00 | 44604.00 | RAJ ELECTRICALS
21.00 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV (E) grade as required : 120-185 sq. mm | 2.00 | Each |  | 6458.00 | 15240.88 | 16260.00 | 38373.60 | 14400.00 | 33984.00 | 15240.88 | RAJ ELECTRICALS
22.00 | Supplying and installing of 600 mm width X 75 mm depth X 2.0 mm thickness perforated hot dipped galvanised iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders / mounted on angle supports including G.I. bolts, nuts along with cable tray cover etc as required with a permissible variation of ±10% in quantity. | 75.00 | MTR |  | 1785.00 | 157972.50 | 2833.00 | 250720.50 | 1800.00 | 159300.00 | 157972.50 | RAJ ELECTRICALS
23.00 | Earthing GI Earth Electrode 3000 mm length, 65 mm diameter, 4 mm thick, along with accessories like SS nuts, bolts etc, and providing masonry enclosure as per scope of work with MS chequered cover plate 600 mm X 600 mm X 5 mm thick, having locking arrangement and charcoal / coke and salt earthing media. Proper earthing layout is to be provided. | 10.00 | SET |  | 14700.00 | 173460.00 | 27570.00 | 325326.00 | 9000.00 | 106200.00 | 106200.00 | RAKESH TRIPATHI
24.00 | Providing, installing, testing and commissioning of maintenance-free type earthing pit comprising 3000 mm long, 76/80 mm dia. low carbon steel, copper-bonded electrode (minimum copper coating thickness 250 micron), UL-listed, ISI-marked, CPRI/ERDA-approved, with 32 × 6 mm Class B copper-coated strip as inner electrode. Electrode to be filled with high-conductivity, anti-corrosive crystalline conductive mixture. Installation to be in a 200 mm dia. bore with specified chemical backfill, complete with all excavation, refilling, and finishing. MS chequered cover plate 600 × 600 × 5 mm thick with locking arrangement to be provided. Proper earthing layout is to be provided. | 6.00 | SET |  | 22575.00 | 159831.00 | 26236.00 | 185750.88 | 13500.00 | 95580.00 | 95580.00 | RAKESH TRIPATHI
25.00 | Providing and fixing 50 mm X 6 mm HOT DIP G.I. strip on surface or in recess for connections etc. as required, including welding, required excavation. ( HT Panel ,Transformer Body ) | 120.00 | MTR |  | 303.00 | 42904.80 | 328.00 | 46444.80 | 450.00 | 63720.00 | 42904.80 | RAJ ELECTRICALS
26.00 | Providing and fixing 50 mm X 6 mm HOT DIP G.I. strip on surface or in recess for connections etc. as required, including welding. ( DG, LT Panel Body ) | 100.00 | MTR |  | 303.00 | 35754.00 | 328.00 | 38704.00 | 450.00 | 53100.00 | 35754.00 | RAJ ELECTRICALS
27.00 | Providing and fixing 40 mm X 6 mm CU STRIP. strip on surface or in recess for connections etc. as required. including brazing, required excavation along with heat shrink type sleeve. (DG / TRANSFORMER Neutral) | 30.00 | MTR |  | 2437.00 | 86269.80 | 2668.00 | 94447.20 | 3240.00 | 114696.00 | 86269.80 | RAJ ELECTRICALS
28.00 | Providing and fixing 25 mm X 6 mm CU STRIP. strip on surface or in recess for connections etc. as required. including brazing, required excavation along with heat shrink sleeve for HTMC. | 30.00 | MTR |  | 1638.00 | 57985.20 | 1690.00 | 59826.00 | 2520.00 | 89208.00 | 57985.20 | RAJ ELECTRICALS
29.00 | Supply, erection, fabrication, cutting, welding and installation of structural steel using m.s. angles supports, clamps, coupler plates, flats, channels etc. as per drawing and specification with one coat of zinc rich primer and two coats of approved enamel paints with all hardwares such as anchor fastners, GI nutbolts and washers etc. complete to the satisfaction of EIC, approx 500 Kg. | 500.00 | LS |  | 163.00 | 96170.00 | 148.00 | 87320.00 | 144.00 | 84960.00 | 84960.00 | RAKESH TRIPATHI
30.00 | Supply, Installation of Safety Items : Rubber Mate 1.1KV GRADE for LV Panels | 2.00 | MTR |  | 3255.00 | 7681.80 | 1440.00 | 3398.40 | 1800.00 | 4248.00 | 3398.40 | EVERCREST PROJECTS PVT LTD
31.00 | Providing and erecting printed instruction chart both in English / Hindi / Gujarati and duly framed with front glass, for treatment of person suffering from Electric Shock. | 4.00 | Each |  | 3675.00 | 17346.00 | 2320.00 | 10950.40 | 1800.00 | 8496.00 | 8496.00 | RAKESH TRIPATHI
32.00 | Supply and erecting first aid box with all the standard contents. | 1.00 | Each |  | 2730.00 | 3221.40 | 2810.00 | 3315.80 | 1350.00 | 1593.00 | 1593.00 | RAKESH TRIPATHI
33.00 | Providing & Fixing Of Danger Board / caution board as per standard. | 4.00 | Each |  | 683.00 | 3223.76 | 1440.00 | 6796.80 | 450.00 | 2124.00 | 2124.00 | RAKESH TRIPATHI
34.00 | Supply, application and testing of Di-Electric (Insulative) Floor Coating System on RCC Floor Substitute To Rubber Mat for Class-A (415V) Panel area with necessary floor preparation. Thickness minimum 2 MM. Color Blue. 1. High Breakdown Voltage @ ERDA Tested (45kV and above) 2. Leakage Current – less than 10mA @ 33kV 3. AC Proof of Voltage Withstand Voltage of 22kV ac for 3Min Avg. Thickness : 2 mm and above | 85.00 | SQM |  | 3675.00 | 368602.50 | 2725.00 | 273317.50 | 3500.00 | 351050.00 | 273317.50 | EVERCREST PROJECTS PVT LTD
35.00 | Liasoning work with MGVCL as per scope of work a. Registration of application. b. Arranging for technical feasibility site survey from M/s MGVCL c. Obtaining detailed estimate from M/s MGVCL. d. Arranging for payment of estimation and Execution of agreement with M/s MGVCL. e. Release of power on proposed place from M/s MGVCL | 1.00 | JOB |  | 84000.00 | 99120.00 | 200000.00 | 236000.00 | 90000.00 | 106200.00 | 99120.00 | RAJ ELECTRICALS
36.00 | Liasoning work with CEA as per scope of work a. Prepare and submission of application at Electrical Inspectorate. b. Approval of Drawings. c. Arrange for Ele. Inspector site inspection. d. Receipt of NOC and submit at MGVCL for further action. | 1.00 | JOB |  | 105000.00 | 123900.00 | 200000.00 | 236000.00 | 75000.00 | 88500.00 | 88500.00 | RAKESH TRIPATHI
37.00 | Liasonig work for DG and co-ordination with EI and all neccessory Drawing approvals a. Prepare & Approval of Drawings. b. Arrangement of Energy Meter & CT procured new. c. Submission of test report and arranging of site inspection of Electrical Inspector. d. Arranging for final Approval. e. Arranging for installation of tested Meter & CT f. Arranging for final sealing from Discom Lab Department. | 1.00 | JOB |  | 157500.00 | 185850.00 | 200000.00 | 236000.00 | 75000.00 | 88500.00 | 88500.00 | RAKESH TRIPATHI
| Total in Figures |  |  |  |  | 9756458.30 |  | 15134790.92 |  | 9747803.00
Lowest Amount Quoted BY: RAKESH TRIPATHI(9747803.00)

## BOQ Summary
BOQ Summary Details Tender Title: RELOCATION OF ELECTRICAL SUBSTATION Tender ID: 2025_GAIL_246477_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | RAKESH TRIPATHI (BID ID -904812) | 9747803.00 | L1
| 2 | RAJ ELECTRICALS (BID ID -904057) | 9756458.30 | L2
| 3 | EVERCREST PROJECTS PVT LTD (BID ID -904768) | 15134790.92 | L3