## BoQ1
Government eProcurement System Created By: RAGHU L Created Date/Time: 04-Sep-2025 12:44 PM Tender Title: NPCIL/KK5and6/CIVIL/PT/2025/27 Construction of Balance of Plant (BoP) Buildings and Structures of KKNPP 5and6 Tender ID: 2025_NPCIL_229149_1
Tender Inviting Authority: Project Director - KK3to6.
Name of Work: Construction of Balance of Plant (BOP) Buildings & Structures of KKNPP-5&6
Contract No: NPCIL/KK-5&6/CONST/CIVILI/PT/2025/27
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | JATAN CONSTRUCTIONS PVT LTD (GSTN-08AAACJ3635P1Z7) BID ID -836380 |  | P AND C PROJECTS PRIVATE LIMITED (GSTN-33AABCP2483L1ZB) BID ID -838817 |  | Dineshchandra R Agrawal Infracon Pvt. Ltd. (GSTN-24AABCD9523D1Z0) BID ID -840028 |  | DEE VEE PROJECTS LIMITED (GSTN-NA) BID ID -837242 |  | BRIDGE AND ROOF COMPANY INDIA LIMITED (GSTN-NA) BID ID -835864 |  | VRC Constructions (India) Limited (GSTN-NA) BID ID -839500 |  | Ocean Lifespaces India Private Limited (GSTN-NA) BID ID -833197
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | EARTHWORK
2.00 | Site clearance and Earthwork excavation
3.00 | General clearance of site, removal of shrubs / uprooting of vegetations, trees, bushes etc. removal of rubbish and disposing at places up to 3km lead including making temporary access etc. complete. | 128500.00 | Sq. Meter |  | 22.00 | 2827000.00 | 16.00 | 2056000.00 | 25.00 | 3212500.00 | 20.00 | 2570000.00 | 32.00 | 4112000.00 | 31.00 | 3983500.00 | 14.00 | 1799000.00 | 1799000.00 | Ocean Lifespaces India Private Limited
4.00 | Earth work excavation in all types of soil to the required grade, level and slope for all depths and lifts as per the drawings and specifications either manually or using mechanical equipments, removal of roots and vegetation, cleaning the loose materials, segregating the useful / serviceable material and carting of excavated material up to a lead of 3km, leveling etc. complete as per drawing and specification. Note: 1.The cost of dewatering required for the excavation shall be paid under relevant item. 2.The lead for the disposal of earth is the shortest distance from the centre of layout of the structure for which excavation is to be carried out to centre of dump yard. 3.Any over excavation beyond the limits specified in the drawing /specification shall be filled with concrete of the same grade of leveling course and no payment shall be made on this account for the excess excavation and leveling course. | 125000.00 | Cu. Meter |  | 250.00 | 31250000.00 | 408.00 | 51000000.00 | 260.00 | 32500000.00 | 350.00 | 43750000.00 | 240.00 | 30000000.00 | 387.50 | 48437500.00 | 320.00 | 40000000.00 | 30000000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
5.00 | Excavation in all types of rocks (Highly weathered, Moderately weathered and Hard rock) for all depths and lifts by mechanical equipments (hydraulic excavator) by chiselling, cleaning the loose materials, segregating useful excavated rock materials, carting to dump yard with in a lead of 3 Km, stacking of useful rock materials separately etc. complete as per drawing and specification. Note : 1.The cost of dewatering required for the excavation shall be paid under relevant item. 2.The lead for the disposal of earth is the shortest distance from the centre of layout of the structure for which excavation is to be carried out to centre of dump yard. 3.Any over excavation beyond the limits specified in the drawing /specification shall be filled with concrete of the same grade of leveling course and no payment shall be made on this account for the excess excavation and leveling course. | 25500.00 | Cu. Meter |  | 1470.00 | 37485000.00 | 2694.00 | 68697000.00 | 1573.00 | 40111500.00 | 1350.00 | 34425000.00 | 991.00 | 25270500.00 | 1860.00 | 47430000.00 | 2667.00 | 68008500.00 | 25270500.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
6.00 | Excavation in all types of rocks (Highly weathered, Moderately weathered and Hard rock) for all depths and lifts by drilling and controlled blasting using non electric delay blast initiation system, cleaning the loose materials, segregating useful excavated rock materials, carting to dump yard with in a lead of 3 Km, stacking of useful rock materials separately, monitoring the Peak particle velocity and AOP of every blasting operation at five specified locations during the blasting by deploying authorised specialized agency, collecting the data, preparation and submission of report etc. complete as per drawing and specification. Note : 1.The cost of dewatering required during excavation shall be paid under relevant item 2.The lead for the disposal of Rock is the shortest distance from the centre of layout of the structure for which excavation is to be carried out to centre of dump yard. 3.Any over excavation beyond the levels specified in the drawing shall be filled with concrete of the same grade of leveling course and no payment shall be made on this account for the excess excavation and leveling course. 4.Approval and clearance shall be obtained from the concerned Authority for the storing /Transporting and use of explosives. Blasting operation shall be carried out by licensed blasting personnel. 5.Scope includes cost of monitoring peak particle velocity (PPV) & AOP (Air Over Pressure) during every blasting operation. | 7500.00 | Cu. Meter |  | 2940.00 | 22050000.00 | 3137.00 | 23527500.00 | 1300.00 | 9750000.00 | 1450.00 | 10875000.00 | 1176.00 | 8820000.00 | 1395.00 | 10462500.00 | 2014.00 | 15105000.00 | 8820000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
7.00 | Extra over item 1.1.2, 1.1.3 & 1.1.4 for additional lead of every 0.5km or part there of over and above the specified initial lead of 3 Km. | 65500.00 | Cu. Meter |  | 44.00 | 2882000.00 | 21.00 | 1375500.00 | 50.00 | 3275000.00 | 50.00 | 3275000.00 | 33.00 | 2161500.00 | 15.50 | 1015250.00 | 61.00 | 3995500.00 | 1015250.00 | VRC Constructions (India) Limited
8.00 | Pre-shearing in all types of rock in vertical / inclined plane with recommended methodology to the depths shown in the drawing, blasting with suitable charge (controlled blasting) and fine stripping of the rock faces at boundary of excavation pits etc. complete as per drawing and specification. Note: The actual area of exposed surface of the rock at the pre-sheared area shall be measured for payment. | 1000.00 | Sq. Meter |  | 882.00 | 882000.00 | 3870.00 | 3870000.00 | 2000.00 | 2000000.00 | 600.00 | 600000.00 | 529.00 | 529000.00 | 4650.00 | 4650000.00 | 3840.00 | 3840000.00 | 529000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
9.00 | Filling works
10.00 | Filling and compacting in layers not more than 300 mm thick to required slopes and grades as per the construction drawings to the specified areas with available excavated soil from the dump yard within a lead up to 3km, segregating suitable soil in dump yard, watering, compaction with suitable power roller to achieve 95% Proctor density of the filled area, conducting Procter density test etc., complete as per drawing and specification. Note: The Proctor density test shall be conducted in each layer for every 300 m2. | 100000.00 | Cu. Meter |  | 250.00 | 25000000.00 | 503.00 | 50300000.00 | 280.00 | 28000000.00 | 360.00 | 36000000.00 | 251.00 | 25100000.00 | 201.50 | 20150000.00 | 268.00 | 26800000.00 | 20150000.00 | VRC Constructions (India) Limited
11.00 | Supply, filling and compacting suitable borrowed soil in layers not more than 300 mm thick to required slopes and grades as per drawing to the specified areas, watering, compaction with suitable power roller to achieve 95% Proctor density of the filled area, conducting Procter density test etc., complete as per drawings and specifications. Note: The Proctor density test shall be conducted in each layer for every 300 m2. | 10500.00 | Cu. Meter |  | 1367.00 | 14353500.00 | 1357.00 | 14248500.00 | 520.00 | 5460000.00 | 900.00 | 9450000.00 | 621.00 | 6520500.00 | 1085.00 | 11392500.00 | 1398.00 | 14679000.00 | 5460000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
12.00 | Supply and filling GSB (granular sub base) with 40 mm downgraded aggregate in layers of thickness not more than 300 mm including cleaning the base, compacting to the correct lines and levels, watering, compaction with suitable power roller to achieve density of fill 1760kg/m3, conducting Procter density test, etc., complete as per the construction drawings and specifications. Note: The Procter density test shall be conducted in each layer for every 1000 m2 area. | 1000.00 | Cu. Meter |  | 3087.00 | 3087000.00 | 2272.00 | 2272000.00 | 2678.00 | 2678000.00 | 2700.00 | 2700000.00 | 1982.00 | 1982000.00 | 2898.50 | 2898500.00 | 2621.00 | 2621000.00 | 1982000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
13.00 | Conducting Proctor density test as per relevant IS code at locations specified by the ENGINEER for NPCIL requirements. | 500.00 | Nos. |  | 1029.00 | 514500.00 | 2987.00 | 1493500.00 | 1500.00 | 750000.00 | 3000.00 | 1500000.00 | 297.00 | 148500.00 | 930.00 | 465000.00 | 183.00 | 91500.00 | 91500.00 | Ocean Lifespaces India Private Limited
14.00 | Providing and laying rubble soling to a consolidated thickness of 150-200 mm, using rubble spotless stone, murrum (gravel) hand packed, well rammed and consolidated including watering etc., complete as per drawings and specifications. | 6000.00 | Sq. Meter |  | 754.00 | 4524000.00 | 652.00 | 3912000.00 | 531.00 | 3186000.00 | 2200.00 | 13200000.00 | 542.00 | 3252000.00 | 620.00 | 3720000.00 | 1748.00 | 10488000.00 | 3186000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
15.00 | Dewatering works Dewatering outside or within various structures and buildings by submission of dewatering scheme, deploying required dewatering pumps, pipelines including standby equipment, additional equipment to cater the urgent needs, providing and erection of pipe sleeves and support embedded parts, wherever necessary, installation of pumps and pipelines, setting it to work, commissioning, maintaining the equipment and pipelines, maintaining day-to-day records in log books, dismantling and taking back the pumps and pipelines on completion of dewatering requirement etc., complete.
16.00 | Hire charges including repair and maintenance for the dewatering pumps fitted with energy meter including suction hose, foot valve and flexible delivery pipe to connect it to the main dewatering pipeline etc. complete. Note: The unit of Measurement is HP-days i.e. the HP of the pumps the no of days of deployment. | 50500.00 | BHP day |  | 132.00 | 6666000.00 | 315.00 | 15907500.00 | 45.00 | 2272500.00 | 300.00 | 15150000.00 | 198.00 | 9999000.00 | 38.75 | 1956875.00 | 307.00 | 15503500.00 | 1956875.00 | VRC Constructions (India) Limited
17.00 | Hire charges for the deployment of discharges pipe lines as per the dewatering scheme for Medium class G.I 50 mm to 100 mm diameter including the specials etc. complete. Note: The unit of Measurement is Rm. Days i.e. The Rm of pipeline laid x the no of days of deployment. | 55000.00 | RM Days |  | 20.00 | 1100000.00 | 156.00 | 8580000.00 | 14.00 | 770000.00 | 75.00 | 4125000.00 | 119.00 | 6545000.00 | 38.75 | 2131250.00 | 21.00 | 1155000.00 | 770000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
18.00 | Hire charge for the deployment of discharges pipe lines as per the dewatering scheme for Medium class G.I. above 100 mm diameter including the specials etc. complete. Note: The unit of Measurement is Rm. Days i.e. The Rm of pipeline laid x the no of days of deployment. | 50500.00 | RM Days |  | 39.00 | 1969500.00 | 234.00 | 11817000.00 | 9.00 | 454500.00 | 100.00 | 5050000.00 | 132.00 | 6666000.00 | 62.00 | 3131000.00 | 31.00 | 1565500.00 | 454500.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
19.00 | Operational cost of the dewatering pumps based on energy consumption. Note: The payment shall be made based on energy meter reading of the pump . | 105500.00 | KWH |  | 24.00 | 2532000.00 | 19.00 | 2004500.00 | 43.00 | 4536500.00 | 15.00 | 1582500.00 | 16.00 | 1688000.00 | 27.90 | 2943450.00 | 22.00 | 2321000.00 | 1582500.00 | DEE VEE PROJECTS LIMITED
20.00 | WATER PROOFING AND WATER STOPPER
21.00 | Water Proofing
22.00 | Supply and laying two layers of 4.5mm thick each, SBS modified elastomeric bitumen based waterproofing membrane for the horizontal surface below the foundations and tunnel base slab including equipment, tools & tackles, all consumables, base preparation by providing and applying primer as per manufacturer’s recommendation etc., complete as per the construction drawings and specifications. The first layer (lower) shall be thermo fusible having PE finish on both sides and the second layer (top) shall be of granular finish on upper side and thermo fusible PE finish on the other side. Minimum overlap of the joints shall be 150mm in the direction of roll length and 100mm on sides. Note: The actual surface area covered by the waterproofing membrane shall only be measured for payment (overlap shall not be paid). | 30000.00 | Sq. Meter |  | 1793.00 | 53790000.00 | 2854.00 | 85620000.00 | 1980.00 | 59400000.00 | 2000.00 | 60000000.00 | 2115.00 | 63450000.00 | 930.00 | 27900000.00 | 1209.00 | 36270000.00 | 27900000.00 | VRC Constructions (India) Limited
23.00 | Supply and laying two layers of 4.5mm thick each, SBS modified elastomeric bitumen based waterproofing membrane over the vertical surface of the foundations, basement walls and tunnels below ground, including equipment, tools & tackles, all consumables, base preparation by providing and applying primer as per manufacturer's recommendations etc., complete as per the construction drawings and specifications. Both the layers shall be having thermo fusible PE finish on both the sides. Minimum overlap of the joints shall be 150mm in the direction of roll length and 100mm on sides. Note: The actual surface area covered by the waterproofing membrane shall only be measured for payment (overlap shall not be paid). | 10000.00 | Sq. Meter |  | 1793.00 | 17930000.00 | 2854.00 | 28540000.00 | 2070.00 | 20700000.00 | 2100.00 | 21000000.00 | 2115.00 | 21150000.00 | 1085.00 | 10850000.00 | 1209.00 | 12090000.00 | 10850000.00 | VRC Constructions (India) Limited
24.00 | Supply and laying polyethylene film of 500 micron thickness in two layers using bitumen to protect the water proofing membrane for the vertical sides of foundation, walls, tunnels as per the construction drawings and specifications. | 20000.00 | Sq. Meter |  | 147.00 | 2940000.00 | 823.00 | 16460000.00 | 372.00 | 7440000.00 | 340.00 | 6800000.00 | 760.00 | 15200000.00 | 217.00 | 4340000.00 | 128.00 | 2560000.00 | 2560000.00 | Ocean Lifespaces India Private Limited
25.00 | Supply and applying two coat of approved bituminous waterproofing paint on external concrete surfaces of the foundation, basement walls base preparation and application as per manufacturer’s specifications, including all related materials, equipment, labour, tools and tackles, consumables etc., complete as per construction drawings and specifications. | 30000.00 | Sq. Meter |  | 147.00 | 4410000.00 | 372.00 | 11160000.00 | 177.00 | 5310000.00 | 180.00 | 5400000.00 | 291.00 | 8730000.00 | 186.00 | 5580000.00 | 297.00 | 8910000.00 | 4410000.00 | JATAN CONSTRUCTIONS PVT LTD
26.00 | Supply and laying roof water proofing on flat and vertical surfaces using 500 micron thick protecting polyurethane UV resistant top coat over 2mm thick spray type polyurethane base coat over 75 micron thick epoxy primer over minimum 25mm thick (considering slopped roof surface) screed concrete or light weight concrete of density 600-800 kg/m3. The work shall be performed as per manufacturer’s specifications, construction drawings and NPCIL specifications. The rate shall be inclusive of all related materials, equipment, labour, tools and tackles, consumables etc., complete. Note: Light weight concrete will be paid under the relevant item. | 9500.00 | Sq. Meter |  | 1985.00 | 18857500.00 | 1792.00 | 17024000.00 | 1733.00 | 16463500.00 | 3400.00 | 32300000.00 | 2941.00 | 27939500.00 | 2325.00 | 22087500.00 | 2574.00 | 24453000.00 | 16463500.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
27.00 | Supply and fixing PVC water stopper of serrated type having central bulb and trapezoidal ribs on each side or Kicker/surface PVC water Stopper, conforming to IS 12200 & IS 15058. The PVC water stopper shall be of approved make and the rate shall be inclusive of fixing it at all elevations and locations in horizontal/vertical position, joining as per the manufacturer recommendation, keeping it in position during concreting using jigs and fixtures made up of reinforcement rods etc., complete as per the construction drawing and specification.
28.00 | 230mm wide, of minimum 8 mm thickness. | 1000.00 | RM |  | 500.00 | 500000.00 | 797.00 | 797000.00 | 474.00 | 474000.00 | 750.00 | 750000.00 | 230.00 | 230000.00 | 620.00 | 620000.00 | 1444.00 | 1444000.00 | 230000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
29.00 | 250mm wide, of minimum 8 mm thickness. | 1000.00 | RM |  | 603.00 | 603000.00 | 929.00 | 929000.00 | 519.00 | 519000.00 | 850.00 | 850000.00 | 254.00 | 254000.00 | 697.50 | 697500.00 | 1222.00 | 1222000.00 | 254000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
30.00 | CONCRETE WORKS
31.00 | PLAIN CEMENT CONCRETE (PCC) Supply and laying plain cement concrete (PCC) of all grades at temperature not exceeding 38℃,including Type-G admixture having minimum 18% water reduction as per ASTM C-494, manufactured as per the approved mix design including transportation, pouring, compaction, levelling, finishing with wooden float, green cutting if required, curing etc., complete as per the construction drawings and specifications. Note: 1.Rate to include all tests to be conducted on materials, green and hardened concrete as per specification and approved QAP. 2.Variation in the quantity of cement w.r.t. that specified in the subsections below to meet the strength, water permeability or any other technical requirement specified in the working drawings and specification shall be paid or deducted under relevant item.
32.00 | PCC of all grades using 40 mm and down, graded hard stone aggregates with cement content of 270 kg/m3 for levelling course below the foundations and other works/areas of all structures. | 5250.00 | Cu. Meter |  | 6700.00 | 35175000.00 | 10096.00 | 53004000.00 | 7156.00 | 37569000.00 | 6500.00 | 34125000.00 | 6925.00 | 36356250.00 | 7529.90 | 39531975.00 | 5825.00 | 30581250.00 | 30581250.00 | Ocean Lifespaces India Private Limited
33.00 | PCC of all grades using 4.75 mm and down, graded hard stone aggregates with cement content of 380 kg/m3 for screed concrete in the area below and above the membrane waterproofing layers, floor liner, finished floor over primary/secondary concrete and filling between the block masonry and membrane water proofing of external walls and other works/areas of thickness not exceeding 100mm etc., complete as per the construction drawings and specifications. Note: Rate shall include concrete finish requirement for laying waterproofing membrane and floor liner as per as per manufacturer recommendation and construction drawings. | 5500.00 | Cu. Meter |  | 8430.00 | 46365000.00 | 9662.00 | 53141000.00 | 8912.00 | 49016000.00 | 7000.00 | 38500000.00 | 7930.00 | 43615000.00 | 8915.60 | 49035800.00 | 6058.00 | 33319000.00 | 33319000.00 | Ocean Lifespaces India Private Limited
34.00 | PCC of all grades using 20 mm and down, graded hard stone aggregates with cement content of 340 kg/m3 for the secondary concrete of various floors of buildings and structures and other works/areas of all structures as per the construction drawings and specifications. | 7850.00 | Cu. Meter |  | 7540.00 | 59189000.00 | 9282.00 | 72863700.00 | 7955.00 | 62446750.00 | 8000.00 | 62800000.00 | 8227.00 | 64581950.00 | 8580.80 | 67359280.00 | 6058.00 | 47555300.00 | 47555300.00 | Ocean Lifespaces India Private Limited
35.00 | PCC of all grades using 12.5mm and down, graded hard stone aggregates with cement content of 340 kg/m3 for the secondary concrete of various floors of buildings and structures and other works/areas of all structures as per the construction drawings and specifications. | 1500.00 | Cu. Meter |  | 7540.00 | 11310000.00 | 9282.00 | 13923000.00 | 7955.00 | 11932500.00 | 7800.00 | 11700000.00 | 7368.00 | 11052000.00 | 8580.80 | 12871200.00 | 6058.00 | 9087000.00 | 9087000.00 | Ocean Lifespaces India Private Limited
36.00 | Filcrete of M10 grade having pumpable consistency for backfilling below ground level with cement and manufactured sand mix with a cement content of 220 kg/m3 inclusive of all materials, tools, formwork, plant, testing, pumping to the required location etc., complete as per the construction drawings, specifications and as per direction of the ENGINEER. | 5000.00 | Cu. Meter |  | 7660.00 | 38300000.00 | 8521.00 | 42605000.00 | 7058.00 | 35290000.00 | 7000.00 | 35000000.00 | 6872.00 | 34360000.00 | 7111.40 | 35557000.00 | 6990.00 | 34950000.00 | 34360000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
37.00 | Supply and laying damp proof course in two layers of 20mm thickness including formwork, troweled to finish, curing etc., with two coats of hot bitumen of grade A120/S120 conforming to IS 73 applied over it at a rate of 1.7 kg/m2. Dry sharp sand shall be sprinkled evenly before hardening of second coat of bitumen paint complete as per the specifications. | 2500.00 | Sq. Meter |  | 700.00 | 1750000.00 | 1326.00 | 3315000.00 | 342.00 | 855000.00 | 500.00 | 1250000.00 | 859.00 | 2147500.00 | 775.00 | 1937500.00 | 583.00 | 1457500.00 | 855000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
38.00 | Providing as per requirement light weight PCC of density 600 to 800 kg/m3 for preparation of under bed for waterproofing treatment or as specified in the construction drawings using 20mm down, graded aggregates and cement content of 340 kg/m3 laid in panels as per specifications. | 500.00 | Cu. Meter |  | 8970.00 | 4485000.00 | 11512.00 | 5756000.00 | 7955.00 | 3977500.00 | 6500.00 | 3250000.00 | 8590.00 | 4295000.00 | 8525.00 | 4262500.00 | 6706.00 | 3353000.00 | 3250000.00 | DEE VEE PROJECTS LIMITED
39.00 | Reinforced Cement Concrete (RCC): Carrying out concrete mix design and qualification of ingredients as per the technical specifications, providing as per requirement and placing reinforced cement concrete (RCC) of all grades in-situ or for RCC precast elements at yard at temperature not exceeding 38℃, including Type-G admixture having minimum 18% water reduction as per ASTM C-494 and as per approved mix design, produced in automatic batching plant, transporting to site, pouring by mechanical means such as pumps, placer booms, crane and buckets in various structures at all elevations and locations, providing chutes wherever required, compacting, finishing, making grooves, providing openings /cut-outs, construction joints, green cutting, curing including all tools and tackles, preparation of pour plan, maintaining records, preparation of post pour inspection report subsequent to de-shuttering,etc., complete as per drawing and specification. Note: 1.Rate to include all tests to be conducted on materials, green and hardened concrete as per specification and approved QAP. 2.Variation in quantity of cement w.r.t. that specified in the subsections below to meet the strength, water permeability or any other technical requirement specified in the construction drawings and specification shall be paid or deducted under relevant item. 3.Extra over for reduction in placement temperature shall be paid under relevant item. 4.Reinforcement shall be paid under relevant item. 5.Transportation and erection of precast structural element shall be paid under relevant item.
40.00 | RCC of all grade using 40 mm and down, graded hard stone aggregate and cement content of 340 kg/m3. | 5510.00 | Cu. Meter |  | 7400.00 | 40774000.00 | 9039.00 | 49804890.00 | 7939.00 | 43743890.00 | 8500.00 | 46835000.00 | 8280.00 | 45622800.00 | 8735.80 | 48134258.00 | 6408.00 | 35308080.00 | 35308080.00 | Ocean Lifespaces India Private Limited
41.00 | RCC of all grade using 20 mm and down, downgraded hard stone aggregate and cement content of 390 kg/m3. | 50000.00 | Cu. Meter |  | 8100.00 | 405000000.00 | 9042.00 | 452100000.00 | 8536.00 | 426800000.00 | 9000.00 | 450000000.00 | 8491.00 | 424550000.00 | 9154.30 | 457715000.00 | 6990.00 | 349500000.00 | 349500000.00 | Ocean Lifespaces India Private Limited
42.00 | Self-compacting concrete of all grades using 10mm down aggregates and cement content of 390 kg/m3, viscosity modifying agents for the secondary concrete as per approved mix design at locations as specified in the construction drawing. | 1250.00 | Cu. Meter |  | 9500.00 | 11875000.00 | 9765.00 | 12206250.00 | 8692.00 | 10865000.00 | 12000.00 | 15000000.00 | 9549.00 | 11936250.00 | 10850.00 | 13562500.00 | 6990.00 | 8737500.00 | 8737500.00 | Ocean Lifespaces India Private Limited
43.00 | Precast concrete elements Providing, casting, finishing, curing, hoisting, transportation, placing in position using crane of sufficient capacity, making connections using cement mortar in ratio 1:2 by volume, - precast wall panels of Physical Protection System (PPS), precast slabs, precast manholes and covers for surface drains, precast trenches, precast beam/columns and precast pedestals, using cement concrete of all grades using 20mm and down, graded hard stone aggregate with cement content of 390 kg/m3, excluding cost of reinforcement but including formwork/moulds, tools & tackles, lifting jigs for erection, crane, etc., all complete, as per construction drawings and specifications. | 5000.00 | Cu. Meter |  | 14155.00 | 70775000.00 | 22208.00 | 111040000.00 | 12136.00 | 60680000.00 | 16500.00 | 82500000.00 | 15661.00 | 78305000.00 | 15500.00 | 77500000.00 | 26086.00 | 130430000.00 | 60680000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
44.00 | Rate adjustment for Concrete items (PCC &RCC)
45.00 | Rate adjustment (addition or deduction) for all the concrete items under 3.1 and 3.2 (PCC & RCC) for the variation in quantity of cement under the relevant items to meet strength, water permeability or any other technical requirement specified in the working drawings and specification. | 600000.00 | kg |  | 7.20 | 4320000.00 | 7.00 | 4200000.00 | 7.00 | 4200000.00 | 7.50 | 4500000.00 | 9.00 | 5400000.00 | 9.30 | 5580000.00 | 8.00 | 4800000.00 | 4200000.00 | P AND C PROJECTS PRIVATE LIMITED, Dineshchandra R Agrawal Infracon Pvt. Ltd.
46.00 | Extra over for all the concrete items under 3.1 and 3.2 (PCC & RCC) for meeting the placement temperature as per technical requirements specified in the construction drawings by partial or full replacement of water by chilled water/ice.
47.00 | For placement temperature less than 29°C. | 1000.00 | Cu. Meter |  | 110.00 | 110000.00 | 96.00 | 96000.00 | 650.00 | 650000.00 | 1500.00 | 1500000.00 | 463.00 | 463000.00 | 775.00 | 775000.00 | 408.00 | 408000.00 | 96000.00 | P AND C PROJECTS PRIVATE LIMITED
48.00 | FORMWORK
49.00 | Providing, fixing/erecting and removing and taking back formwork for all PCC, RCC, in-situ straight or curved walls or precast elements at yard, including the pockets of equipment and tank foundations at all levels, aligning as per the specified tolerance, fastening etc., complete of normal/self-compacting/light weight concrete with film faced densified plywood including preparation of scheme, submission of formwork design & drawing, centring, staging, scaffolding, working platforms for concrete placement at all elevations and locations etc., complete as per drawing and specification. Note: 1.Rate to include chamfers / drip mouldings / cut-outs and application of approved form / mould release agent and all related materials, equipment, labour, tools & tackles, consumables etc., complete. 2.The rate shall be inclusive of design,erection and removal of form work support system. 3.area of concrete formed shall be measured for payment. | 250000.00 | Sq. Meter |  | 1100.00 | 275000000.00 | 959.00 | 239750000.00 | 1504.00 | 376000000.00 | 990.00 | 247500000.00 | 667.00 | 166750000.00 | 1240.00 | 310000000.00 | 990.00 | 247500000.00 | 166750000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
50.00 | Preparation of vertical construction joints at all elevations as per the approved design with form work / weld mesh & chicken mesh, green cutting, cleaning, including all material, tools and tackle etc, complete as per the specification. Note: The sectional area of the approved construction joints shall be considered for payment. | 1000.00 | Sq. Meter |  | 500.00 | 500000.00 | 639.00 | 639000.00 | 334.00 | 334000.00 | 1200.00 | 1200000.00 | 463.00 | 463000.00 | 7750.00 | 7750000.00 | 318.00 | 318000.00 | 318000.00 | Ocean Lifespaces India Private Limited
51.00 | Reinforcement steel/Weld mesh/Chicken mesh:
52.00 | Reinforcement steel: Providing as per requirement and placing in position High Yield Strength Deformed (HYSD) bars Fe 500D grade conforming to IS:1786 of various diameters for all RCC and precast construction works at all locations and elevations, including cutting, bending, fixing in position, tying with 16 gauge soft annealed binding wire etc., complete as per the construction drawing and specification. Note: 1.Material shall be delivered to site with MTC fulfilling the technical requirements as per specifications. 2.Rate to include all tests to be conducted as per the approved QAP. 3.The chairs provided to support the reinforcement for design position shall be separately measured and paid in this item itself.
53.00 | Diameter 20 mm and below. | 7000.00 | MT |  | 103000.00 | 721000000.00 | 103868.00 | 727076000.00 | 97918.00 | 685426000.00 | 101000.00 | 707000000.00 | 92380.00 | 646660000.00 | 105400.00 | 737800000.00 | 99025.00 | 693175000.00 | 646660000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
54.00 | Diameter above 20 mm. | 3500.00 | MT |  | 102000.00 | 357000000.00 | 101491.00 | 355218500.00 | 97454.00 | 341089000.00 | 101000.00 | 353500000.00 | 91190.00 | 319165000.00 | 105400.00 | 368900000.00 | 99025.00 | 346587500.00 | 319165000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
55.00 | In-situ fillet lap welding of High Yield Strength Deformed (HYSD) bars Fe 500D grade of diameter 12mm to 36mm as per specification at locations including qualification of the process, conducting the tests as per approved QA plan etc., complete. Note: The lap length shall be as per the welding process qualification to meet joint strength requirement as per ASME Section III Div 2.
56.00 | up to 20 mm diameter | 1500.00 | RM |  | 88.00 | 132000.00 | 244.00 | 366000.00 | 421.00 | 631500.00 | 300.00 | 450000.00 | 1850.00 | 2775000.00 | 1550.00 | 2325000.00 | 61.00 | 91500.00 | 91500.00 | Ocean Lifespaces India Private Limited
57.00 | above 20 mm diameter | 1000.00 | RM |  | 110.00 | 110000.00 | 260.00 | 260000.00 | 561.00 | 561000.00 | 300.00 | 300000.00 | 2775.00 | 2775000.00 | 2325.00 | 2325000.00 | 80.00 | 80000.00 | 80000.00 | Ocean Lifespaces India Private Limited
58.00 | Mechanical splicing of High Yield Strength Deformed (HYSD) bars Fe 500D grade using threaded couplers of approved make including providing as per requirement, labour, tools, tackles, cold forging equipment, threading equipment, all consumables, carrying out tests as per specifications etc., complete.
59.00 | 16mm diameter | 500.00 | Nos. |  | 116.00 | 58000.00 | 66.00 | 33000.00 | 156.00 | 78000.00 | 200.00 | 100000.00 | 114.00 | 57000.00 | 124.00 | 62000.00 | 117.00 | 58500.00 | 33000.00 | P AND C PROJECTS PRIVATE LIMITED
60.00 | 20mm diameter | 500.00 | Nos. |  | 170.00 | 85000.00 | 71.00 | 35500.00 | 174.00 | 87000.00 | 250.00 | 125000.00 | 133.00 | 66500.00 | 186.00 | 93000.00 | 117.00 | 58500.00 | 35500.00 | P AND C PROJECTS PRIVATE LIMITED
61.00 | 25mm diameter | 1000.00 | Nos. |  | 275.00 | 275000.00 | 79.00 | 79000.00 | 234.00 | 234000.00 | 300.00 | 300000.00 | 185.00 | 185000.00 | 279.00 | 279000.00 | 175.00 | 175000.00 | 79000.00 | P AND C PROJECTS PRIVATE LIMITED
62.00 | 28mm diameter | 2000.00 | Nos. |  | 340.00 | 680000.00 | 94.00 | 188000.00 | 277.00 | 554000.00 | 400.00 | 800000.00 | 218.00 | 436000.00 | 496.00 | 992000.00 | 175.00 | 350000.00 | 188000.00 | P AND C PROJECTS PRIVATE LIMITED
63.00 | 32mm diameter | 1000.00 | Nos. |  | 390.00 | 390000.00 | 105.00 | 105000.00 | 323.00 | 323000.00 | 500.00 | 500000.00 | 251.00 | 251000.00 | 620.00 | 620000.00 | 175.00 | 175000.00 | 105000.00 | P AND C PROJECTS PRIVATE LIMITED
64.00 | Grouting of High Yield Strength Deformed (HYSD) bars Fe 500D grade of diameter 12mm to 32 mm including required drilling appropriate diameter hole to a minimum depth of 10 times diameter of the bar or as shown in the construction drawing with epoxy chemical mortar of make Hilti HIT-Re500 V4 or approved equivalent (including its supply), qualification of the system, cleaning grout hole, grouting, providing other consumables, equipment tools and tackle etc., complete by conducting mock-up, conducting the tests as per approved QA plan, and installation by qualified personnel authorised by the grout manufacturer. Note: 1.Payment will be made for the length in running meter (RM) of bar anchored using grout i.e., length of bar embedded. 2.Reinforcement bar shall be paid under relevant BOQ item.
65.00 | 16mm diameter | 300.00 | RM |  | 2800.00 | 840000.00 | 332.00 | 99600.00 | 2564.00 | 769200.00 | 3000.00 | 900000.00 | 5022.00 | 1506600.00 | 1550.00 | 465000.00 | 584.00 | 175200.00 | 99600.00 | P AND C PROJECTS PRIVATE LIMITED
66.00 | 20mm diameter | 300.00 | RM |  | 4200.00 | 1260000.00 | 398.00 | 119400.00 | 3113.00 | 933900.00 | 4500.00 | 1350000.00 | 9383.00 | 2814900.00 | 2092.50 | 627750.00 | 961.00 | 288300.00 | 119400.00 | P AND C PROJECTS PRIVATE LIMITED
67.00 | 25mm diameter | 100.00 | RM |  | 7430.00 | 743000.00 | 398.00 | 39800.00 | 3723.00 | 372300.00 | 5000.00 | 500000.00 | 12952.00 | 1295200.00 | 2790.00 | 279000.00 | 1899.00 | 189900.00 | 39800.00 | P AND C PROJECTS PRIVATE LIMITED
68.00 | 28mm diameter | 100.00 | RM |  | 8270.00 | 827000.00 | 465.00 | 46500.00 | 4715.00 | 471500.00 | 5000.00 | 500000.00 | 13877.00 | 1387700.00 | 3875.00 | 387500.00 | 2358.00 | 235800.00 | 46500.00 | P AND C PROJECTS PRIVATE LIMITED
69.00 | 32mm diameter | 100.00 | RM |  | 10900.00 | 1090000.00 | 465.00 | 46500.00 | 5714.00 | 571400.00 | 6000.00 | 600000.00 | 18502.00 | 1850200.00 | 4960.00 | 496000.00 | 3443.00 | 344300.00 | 46500.00 | P AND C PROJECTS PRIVATE LIMITED
70.00 | Supply and placing in position approved MS welded wire mesh of various mesh sizes and thickness for RCC or any other works at all elevations and locations, including providing as per requirement, cleaning, cutting, bending, fixing, tying with 16 gauge soft annealed binding wire with minimum overlapping of 150mm etc., complete as per the construction drawings and specifications. | 50.00 | MT |  | 123480.00 | 6174000.00 | 122725.00 | 6136250.00 | 157169.00 | 7858450.00 | 120000.00 | 6000000.00 | 121587.00 | 6079350.00 | 131750.00 | 6587500.00 | 99025.00 | 4951250.00 | 4951250.00 | Ocean Lifespaces India Private Limited
71.00 | Providing as per requirement and placing in position 22 gauge chicken wire mesh for the joints between RCC and masonry at all elevations and locations, including providing as per requirement, cleaning, cutting, bending, fixing, etc., complete. | 4800.00 | Sq. Meter |  | 265.00 | 1272000.00 | 471.00 | 2260800.00 | 105.00 | 504000.00 | 250.00 | 1200000.00 | 159.00 | 763200.00 | 465.00 | 2232000.00 | 137.00 | 657600.00 | 504000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
72.00 | Embankment Construction
73.00 | Formation of embankment using approved quality soil excavated from locally available borrow areas (as per the direction of ENGINEER), stripping, watering of borrow area, loading, unloading, transporting from all leads & lifts, surface watering /dewatering, lowering of water level to at least 600 mm below the bottom of the working level as required, depositing on the bank/dyke in layer not exceeding 150 mm in compacted thickness for forming the embankment with all leads, lifts, breaking clods, watering, compaction to achieve a minimum dry density of 95% for dyke with vibratory roller or any other mechanical means as approved by the ENGINEER, forming extra width on edges, trimming of slopes to obtain the section as per construction drawing with all incidental charges including providing as per requirement and laying plastic sheet/ gunny bags, cost of labour, equipment, soil/ earth material, filter material wherever necessary, etc., complete as per specifications, construction drawings and as directed by the ENGINEER. (Payment shall be made on the basis of compacted earth). The rate shall be inclusive of the field/laboratory tests to be performed while executing the works. | 1500.00 | Cu. Meter |  | 735.00 | 1102500.00 | 3679.00 | 5518500.00 | 520.00 | 780000.00 | 700.00 | 1050000.00 | 198.00 | 297000.00 | 1085.00 | 1627500.00 | 454.00 | 681000.00 | 297000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
74.00 | Supply and laying 150mm thick dry-stone pitching using hard granite stones including preparation of bed in line, level, slope as specified, hammer dressing the stones, laying, and filling up the gaps with earth etc., complete as per drawings and specifications. | 1000.00 | Sq. Meter |  | 919.00 | 919000.00 | 564.00 | 564000.00 | 657.00 | 657000.00 | 2600.00 | 2600000.00 | 555.00 | 555000.00 | 775.00 | 775000.00 | 1002.00 | 1002000.00 | 555000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
75.00 | MASONRY (CC BLOCK /BRICK /RANDOM RUBBLE MASONRY) & PARTITION
76.00 | Cement Concrete Block Masonry
77.00 | Supply and constructing cement concrete block masonry of M20 grade, using solid blocks of specified size in cement mortar 1:4 by volume at all elevations and locations, wherever required suitable for 12 mm GI rod, cross or Tee grooving including scaffolding, racking out joints, curing etc., complete as per drawings and specifications. The supply and fixing GI rods shall be paid under relevant item. | 11000.00 | Cu. Meter |  | 10151.00 | 111661000.00 | 8363.00 | 91993000.00 | 10579.00 | 116369000.00 | 9000.00 | 99000000.00 | 10084.00 | 110924000.00 | 8680.00 | 95480000.00 | 8467.00 | 93137000.00 | 91993000.00 | P AND C PROJECTS PRIVATE LIMITED
78.00 | Supply and fixing to the embedded parts in columns/beams using welding, GI rods in brickwork as per details shown in construction drawings & specifications or as directed by ENGINEER at all locations and elevations, and complete it. | 5000.00 | Kg |  | 147.00 | 735000.00 | 160.00 | 800000.00 | 123.00 | 615000.00 | 200.00 | 1000000.00 | 87.00 | 435000.00 | 155.00 | 775000.00 | 99.00 | 495000.00 | 435000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
79.00 | Fly ash Brick Masonry
80.00 | Supply and constructing fly ash block masonry, using approved fly ash bricks, class designation 7.5 in cement mortar 1:6 (by volume), at all elevations and locations including scaffolding, racking out joints, curing etc., complete as per construction drawings and specifications. | 400.00 | Cu. Meter |  | 8634.00 | 3453600.00 | 8847.00 | 3538800.00 | 11189.00 | 4475600.00 | 9500.00 | 3800000.00 | 10361.00 | 4144400.00 | 8525.00 | 3410000.00 | 8738.00 | 3495200.00 | 3410000.00 | VRC Constructions (India) Limited
81.00 | Supply and constructing fly ash block masonry, using fly ash bricks class designation 7.5 in cement mortar 1:4 (by volume), laying of 2 Nos. 6 / 8 mm dia. reinforcement bars at every fourth layer at all elevations and locations including scaffolding, racking out joints, curing etc., complete as per drawing and specification. Note: The reinforcement shall be paid under relevant item. | 800.00 | Cu. Meter |  | 8781.00 | 7024800.00 | 8979.00 | 7183200.00 | 11361.00 | 9088800.00 | 9800.00 | 7840000.00 | 10560.00 | 8448000.00 | 8525.00 | 6820000.00 | 8738.00 | 6990400.00 | 6820000.00 | VRC Constructions (India) Limited
82.00 | Supply and constructing light weight fly ash block masonry M20 grade, using solid blocks of specified size and density not more than 1800 kg/m3 in cement mortar 1:4 by volume, at all elevations and locations including scaffolding, racking out joints, curing etc., complete as per specifications and construction drawings. | 600.00 | Cu. Meter |  | 10151.00 | 6090600.00 | 8363.00 | 5017800.00 | 12402.00 | 7441200.00 | 9000.00 | 5400000.00 | 11696.00 | 7017600.00 | 9300.00 | 5580000.00 | 8467.00 | 5080200.00 | 5017800.00 | P AND C PROJECTS PRIVATE LIMITED
83.00 | Random Rubble Masonry
84.00 | Supply and constructing random rubble masonry of suitable thickness at all elevations in cement mortar 1:6 (by volume) using hard granite stones including hammer dressing the stones, raking out the joints, scaffolding, providing weep holes, key stones, curing etc., complete as per drawings and specifications. | 2500.00 | Cu. Meter |  | 5880.00 | 14700000.00 | 5613.00 | 14032500.00 | 4138.00 | 10345000.00 | 5500.00 | 13750000.00 | 7405.00 | 18512500.00 | 6200.00 | 15500000.00 | 6204.00 | 15510000.00 | 10345000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
85.00 | Flush pointing on stone masonry / random Rubble masonry with Cement mortar 1:3, pointing neatly and finishing the joints as specified, scaffolding, curing etc., complete as per drawings and specifications. | 8000.00 | Sq. Meter |  | 257.00 | 2056000.00 | 328.00 | 2624000.00 | 248.00 | 1984000.00 | 200.00 | 1600000.00 | 370.00 | 2960000.00 | 232.50 | 1860000.00 | 137.00 | 1096000.00 | 1096000.00 | Ocean Lifespaces India Private Limited
86.00 | Supply and fixing 200 mm thick partition using 20mm thick bison board (single or multiple thickness) at both faces and filling the interspaces with mineral wool having density not less than 144 kg/ m3 as insulating material, elastic strips, fixing screws over the structural frames at all elevation, necessary equipment, staging, scaffolding, tools, and tackles etc., complete as per drawings and specifications. Note: The structural frames shall be paid under relevant item. | 800.00 | Sq. Meter |  | 3455.00 | 2764000.00 | 2390.00 | 1912000.00 | 3402.00 | 2721600.00 | 1500.00 | 1200000.00 | 595.00 | 476000.00 | 6975.00 | 5580000.00 | 4363.00 | 3490400.00 | 476000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
87.00 | GROUTING:
88.00 | Supply, mixing and grouting approved high strength ready mix non-shrink grout of compressive strength not less than 60 MPa of ‘Conbextra® GP- 2 ’ of M/s Fosroc make or approved equivalent, below equipment base plate, penetrations, embedded parts, for post installed reinforcement bars, etc., at all elevation and locations as per construction drawings and specifications. | 50.00 | Cu. Meter |  | 73500.00 | 3675000.00 | 55272.00 | 2763600.00 | 43497.00 | 2174850.00 | 65000.00 | 3250000.00 | 77974.00 | 3898700.00 | 77500.00 | 3875000.00 | 65902.00 | 3295100.00 | 2174850.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
89.00 | Providing as per requirement, mixing and grouting approved high strength ready mix non-shrink grout of compressive strength not less than 65 MPa of ‘Ultratech Power Grout NS1’ or ‘Fosroc BB92IN’ or approved equivalent, at the joints of precast elements, below equipment base plate, penetrations, embedded parts, for post installed reinforcement bars, etc., at all elevation and locations as per construction drawings and specifications. | 25.00 | Cu. Meter |  | 80850.00 | 2021250.00 | 49378.00 | 1234450.00 | 63156.00 | 1578900.00 | 90000.00 | 2250000.00 | 170817.00 | 4270425.00 | 93000.00 | 2325000.00 | 52425.00 | 1310625.00 | 1234450.00 | P AND C PROJECTS PRIVATE LIMITED
90.00 | Supply, mixing and grouting low viscosity expansive aqua-reactive water barrier and grouting system "POLYGROUT” or equivalent including drilling and fixing nozzle, dry packing, grouting, arranging all equipment, accessories, tools, and tackles required to carry out the work at all elevation and locations etc., complete as per specifications. Note: The quantity of grout as per actual consumption shall be paid. | 200.00 | Litres |  | 2026.00 | 405200.00 | 1029.00 | 205800.00 | 858.00 | 171600.00 | 3500.00 | 700000.00 | 988.00 | 197600.00 | 2325.00 | 465000.00 | 1107.00 | 221400.00 | 171600.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
91.00 | Supply, mixing and grouting under equipment bases, steel structures, etc., including preparation of concrete surface by chipping, cleaning, etc., with approved quality of formwork as required, curing and finishing the exposed surfaces with 1:1:2 cement concrete (nominal mix by volume) with 6mm down stone chips and necessary anti-shrinkage admixture as per drawing, specification and direction of ENGINEER. 28-day cube crushing strength of grout shall be minimum 30 N/mm2. | 50.00 | Cu. Meter |  | 10421.00 | 521050.00 | 5781.00 | 289050.00 | 15000.00 | 750000.00 | 60000.00 | 3000000.00 | 23285.00 | 1164250.00 | 38750.00 | 1937500.00 | 7169.00 | 358450.00 | 289050.00 | P AND C PROJECTS PRIVATE LIMITED
92.00 | CAULKING AND SEALANTS /EXPANSION JOINTS
93.00 | Supply and fixing high density expanded polystyrene board of density not less than 30 kg/m3 covered with 2 layers of 0.4 mm thick polyethylene sheets of approved make properly secured in position using approved adhesives/masking tapes including tools and tackles required to carry out the work at expansion joints at all elevation and locations as per drawings and specifications.
94.00 | 100mmThick | 500.00 | Sq. Meter |  | 2772.00 | 1386000.00 | 2031.00 | 1015500.00 | 1806.00 | 903000.00 | 1300.00 | 650000.00 | 1123.00 | 561500.00 | 4960.00 | 2480000.00 | 4703.00 | 2351500.00 | 561500.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
95.00 | 50mmThick | 600.00 | Sq. Meter |  | 2317.00 | 1390200.00 | 1434.00 | 860400.00 | 917.00 | 550200.00 | 1050.00 | 630000.00 | 747.00 | 448200.00 | 2480.00 | 1488000.00 | 2345.00 | 1407000.00 | 448200.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
96.00 | 30mm Thick | 500.00 | Sq. Meter |  | 1927.00 | 963500.00 | 896.00 | 448000.00 | 623.00 | 311500.00 | 770.00 | 385000.00 | 548.00 | 274000.00 | 1550.00 | 775000.00 | 1461.00 | 730500.00 | 274000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
97.00 | 20mmThick | 1200.00 | Sq. Meter |  | 1765.00 | 2118000.00 | 597.00 | 716400.00 | 490.00 | 588000.00 | 500.00 | 600000.00 | 463.00 | 555600.00 | 1240.00 | 1488000.00 | 1018.00 | 1221600.00 | 555600.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
98.00 | Supply and fixing 2 mm GI sheets of curved or flat profile cut and bend to required size, fixing to concrete by providing Hilti HUS 7.5/60 or equivalent screws as per requirement as metal compensator including tools and tackles required to carry out the work at expansion joints at all elevation and locations as per construction drawings and specifications Note: The screw anchors will be paid under relevant item. | 2000.00 | Kg |  | 221.00 | 442000.00 | 119.00 | 238000.00 | 165.00 | 330000.00 | 330.00 | 660000.00 | 165.00 | 330000.00 | 310.00 | 620000.00 | 105.00 | 210000.00 | 210000.00 | Ocean Lifespaces India Private Limited
99.00 | Supply and fixing EPDM - rubber cord of approved make including tools and tackles required to carry out the work at expansion joints at all elevation and locations as per drawings and specification.
100.00 | 20mm diameter | 1200.00 | RM |  | 757.00 | 908400.00 | 177.00 | 212400.00 | 182.00 | 218400.00 | 190.00 | 228000.00 | 321.00 | 385200.00 | 620.00 | 744000.00 | 320.00 | 384000.00 | 212400.00 | P AND C PROJECTS PRIVATE LIMITED
101.00 | 30mm diameter | 840.00 | RM |  | 893.00 | 750120.00 | 287.00 | 241080.00 | 273.00 | 229320.00 | 220.00 | 184800.00 | 482.00 | 404880.00 | 1240.00 | 1041600.00 | 673.00 | 565320.00 | 184800.00 | DEE VEE PROJECTS LIMITED
102.00 | 40mm diameter | 510.00 | RM |  | 1441.00 | 734910.00 | 514.00 | 262140.00 | 364.00 | 185640.00 | 300.00 | 153000.00 | 634.00 | 323340.00 | 2170.00 | 1106700.00 | 692.00 | 352920.00 | 153000.00 | DEE VEE PROJECTS LIMITED
103.00 | Supply, mixing and caulking with Polysulphide sealing compound (gun Grade / Pourablegrade) of approved make at expansion joints, around penetrations, embedded parts, construction joints of various size, shape including preparation of surfaces, application of primer, tools and tackles required to carry out the work at all elevation and locations as per drawing and specification. | 120000.00 | Per 10cc |  | 11.00 | 1320000.00 | 5.00 | 600000.00 | 13.00 | 1560000.00 | 16.00 | 1920000.00 | 11.00 | 1320000.00 | 23.25 | 2790000.00 | 2.00 | 240000.00 | 240000.00 | Ocean Lifespaces India Private Limited
104.00 | Supply and fixing in position approved quality pre-moulded bitumen pads (expansion joints filler board confirming to IS 1838 part I 1983) of specified thickness in expansion joints of all RCC works /brick walls/ any other surfaces as specified, at all heights including applying necessary bitumen solution primer wherever required and finishing the exposed ends with shilikot/Expandex or equivalent sealing compound confirming to IS-1834 Grade A, to make the joints water tight, complete all as per construction drawings and specifications. | 1150.00 | Sq. Meter |  | 1176.00 | 1352400.00 | 418.00 | 480700.00 | 1127.00 | 1296050.00 | 400.00 | 460000.00 | 991.00 | 1139650.00 | 1550.00 | 1782500.00 | 656.00 | 754400.00 | 460000.00 | DEE VEE PROJECTS LIMITED
105.00 | Supply and fixing at all elevations and locations profiled galvanised MS sheet of 1mm thickness with fixed edge on one side and sliding edge with holes on other side between expansion gap/separation gap fixed using Hilti or equivalent make stainless steel screw anchors of size M6 X 100 at 300mm c/c as per construction drawings. Note: The screw anchors will be paid under relevant item. | 500.00 | Sq. Meter |  | 994.00 | 497000.00 | 454.00 | 227000.00 | 1254.00 | 627000.00 | 2000.00 | 1000000.00 | 1520.00 | 760000.00 | 1860.00 | 930000.00 | 909.00 | 454500.00 | 227000.00 | P AND C PROJECTS PRIVATE LIMITED
106.00 | FINISHING WORKS
107.00 | Plastering
108.00 | Providing as per requirement and applying internal plaster 12mm thick with cement mortar 1:4, for walls, columns, beams, skirting etc., including hacking of concrete surface, scaffolding, providing grooves, bands, copings, mouldings, finishing, curing etc., complete at all levels as per construction drawings and specifications. | 160000.00 | Sq. Meter |  | 417.00 | 66720000.00 | 476.00 | 76160000.00 | 446.00 | 71360000.00 | 330.00 | 52800000.00 | 377.00 | 60320000.00 | 542.50 | 86800000.00 | 583.00 | 93280000.00 | 52800000.00 | DEE VEE PROJECTS LIMITED
109.00 | Providing as per requirement and applying external plaster 20mm thick in two layers with cement mortar 1:4, for walls, columns, beams, etc., including hacking of concrete surface, scaffolding, providing grooves, bands, copings, mouldings, finishing, curing etc., complete at all levels as per construction drawings and specifications. | 40000.00 | Sq. Meter |  | 648.00 | 25920000.00 | 562.00 | 22480000.00 | 635.00 | 25400000.00 | 360.00 | 14400000.00 | 476.00 | 19040000.00 | 775.00 | 31000000.00 | 757.00 | 30280000.00 | 14400000.00 | DEE VEE PROJECTS LIMITED
110.00 | Providing cement plaster for the ceiling surface of 6mm thickness in cement mortar 1:3 at all elevations including hacking and preparing the surface, scaffolding, finishing, curing etc., complete as per construction drawings and specifications. | 40000.00 | Sq. Meter |  | 382.00 | 15280000.00 | 488.00 | 19520000.00 | 318.00 | 12720000.00 | 370.00 | 14800000.00 | 330.00 | 13200000.00 | 542.50 | 21700000.00 | 612.00 | 24480000.00 | 12720000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
111.00 | PAINTING OVER CONCRETE/PLASTERED SURFACE
112.00 | Supply and application of two coats of acrylic water emulsion paint of approved make and shade to interior walls, columns, beams and ceiling, over plastered block masonry at all elevations, preparation of the surface to be painted by filling of tie rod holes with cement mortar 1:3 and filling air holes on the concrete surfaces with CM 1:1.5, making good of irregularities more than 3mm using grinders/corborandum stones, curing, cleaning with air water jet, applying suitable priming coat as per paint manufacturer specification, putty and even application of 2 coats of paint to make uniform finish including tools and tackles, consumables, scaffolding etc., complete as per construction drawings and specifications. | 250000.00 | Sq. Meter |  | 176.00 | 44000000.00 | 143.00 | 35750000.00 | 436.00 | 109000000.00 | 160.00 | 40000000.00 | 225.00 | 56250000.00 | 248.00 | 62000000.00 | 221.00 | 55250000.00 | 35750000.00 | P AND C PROJECTS PRIVATE LIMITED
113.00 | Providing and applying Birla white or approved equivalent make Anti-Efflorescence wall putty for a thickness around 1.5 mm as per manufacturer’s instructions to the internal plastered surfaces including preparation of surfaces, scaffolding etc. at all elevations, complete as per drawings and specifications. | 250000.00 | Sq. Meter |  | 88.00 | 22000000.00 | 131.00 | 32750000.00 | 117.00 | 29250000.00 | 100.00 | 25000000.00 | 271.00 | 67750000.00 | 124.00 | 31000000.00 | 92.00 | 23000000.00 | 22000000.00 | JATAN CONSTRUCTIONS PVT LTD
114.00 | Supply and application of epoxy paint - Protestomastic® of M/s Berger or approved equivalent and shade of total dry film thickness not less than 260 microns in multiple coats to interior walls, columns, beams, floors and ceiling at all elevations, preparation of the surface to be painted by filling of tie rod holes with CM 1:3 and filling air holes on the concrete surfaces with CM 1:1.5, making good of irregularities more than 3mm using grinders/corborandum stones, curing, cleaning with air water jet, applying suitable priming coat, putty and even application of paint with airless spray or brush till the required DFT is achieved including all tools and tackles, consumables, scaffolding etc., complete as per drawings and specifications. | 500.00 | Sq. Meter |  | 551.00 | 275500.00 | 418.00 | 209000.00 | 395.00 | 197500.00 | 900.00 | 450000.00 | 430.00 | 215000.00 | 930.00 | 465000.00 | 725.00 | 362500.00 | 197500.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
115.00 | Supply and application of two coats of high performance aliphatic acrylate based protective coating “Sikagard®-550 W IN” or approved equivalent, having anti carbonation, UV resistance and crack bridging properties, over a coat of compatible primer to external / internal surface of concrete, plastered surface, walls, columns, beams and ceiling at all elevations, preparation of the surface to be painted by filling of tie rod holes with CM 1:3 and filling air holes on the concrete surfaces with CM 1:1.5, making good of irregularities more than 3mm using grinders/corborandum stones, curing, cleaning with air water jet, applying putty and even application of paint with roller or brush including all tools and tackles, consumables, scaffolding etc., complete as per drawings and specifications. | 40000.00 | Sq. Meter |  | 375.00 | 15000000.00 | 538.00 | 21520000.00 | 690.00 | 27600000.00 | 500.00 | 20000000.00 | 958.00 | 38320000.00 | 186.00 | 7440000.00 | 513.00 | 20520000.00 | 7440000.00 | VRC Constructions (India) Limited
116.00 | Supply and application of synthetic enamel paint of approved make and shade in single or multiple coat to a total DFT not less than 150 microns to interior walls , columns, beams and ceiling at all elevations, preparation of the surface to be painted by filling of tie rod holes with CM 1:3 and filling air holes on the concrete surfaces with CM 1:1.5, making good of irregularities more than 3mm using grinders/corborandum stones, curing, cleaning with air water jet, applying putty and even application of paint with roller or brush till the required DFT is achieved including all tools and tackles, consumables, scaffolding etc., complete as per drawing and specification. | 4500.00 | Sq. Meter |  | 265.00 | 1192500.00 | 167.00 | 751500.00 | 674.00 | 3033000.00 | 250.00 | 1125000.00 | 225.00 | 1012500.00 | 232.50 | 1046250.00 | 201.00 | 904500.00 | 751500.00 | P AND C PROJECTS PRIVATE LIMITED
117.00 | Supply and application of acid and alkali resistant epoxy paint of approved make and shade of total film thickness not less than 250 microns in multiple coats to interior walls , columns, beams, floors and ceiling at all elevations, preparation of the surface to be painted by filling of tie rod holes with CM 1:3 and filling air holes on the concrete surfaces with CM 1:1.5, making good of irregularities more than 3mm using grinders/corborandum stones, curing, cleaning with air water jet, applying suitable priming coat, putty and even application of paint with airless spray or brush till the required DFT is achieved including all tools and tackles, consumables, scaffolding etc., complete as per drawings and specifications. | 2000.00 | Sq. Meter |  | 669.00 | 1338000.00 | 538.00 | 1076000.00 | 908.00 | 1816000.00 | 900.00 | 1800000.00 | 396.00 | 792000.00 | 930.00 | 1860000.00 | 725.00 | 1450000.00 | 792000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
118.00 | Supply and application of approved make and shade self-levelling epoxy paint over concrete floors for the specified dry film thickness over a coat of primer, base preparation, filling the undulation with suitable filler material to make uniform finish, as per manufacturers specification all related materials, consumables, equipment, tools and tackles etc., complete as per drawings and specifications.
119.00 | With self-levelling epoxy paint for the dry film thickness of 2mm including supplying and mixing filler sand as per manufacturers specification. | 5000.00 | Sq. Meter |  | 1176.00 | 5880000.00 | 956.00 | 4780000.00 | 1007.00 | 5035000.00 | 1100.00 | 5500000.00 | 604.00 | 3020000.00 | 1627.50 | 8137500.00 | 1750.00 | 8750000.00 | 3020000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
120.00 | With self-levelling epoxy paint for the dry film thickness of 1mm including supplying and mixing filler sand as per manufacturers specification. | 7500.00 | Sq. Meter |  | 845.00 | 6337500.00 | 597.00 | 4477500.00 | 756.00 | 5670000.00 | 850.00 | 6375000.00 | 466.00 | 3495000.00 | 1162.50 | 8718750.00 | 1109.00 | 8317500.00 | 3495000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
121.00 | With nuclear grade self-levelling epoxy paint for dry film thickness of 2mm including supplying and mixing filler-sand as per manufacturers specification in controlled access areas. | 5000.00 | Sq. Meter |  | 1985.00 | 9925000.00 | 1792.00 | 8960000.00 | 2223.00 | 11115000.00 | 2000.00 | 10000000.00 | 415.00 | 2075000.00 | 1627.50 | 8137500.00 | 1750.00 | 8750000.00 | 2075000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
122.00 | With self-levelling anti-static epoxy paint for the dry film thickness of 2mm over antistatic primer including supplying and mixing filler sand as per manufacturers specification. | 500.00 | Sq. Meter |  | 5880.00 | 2940000.00 | 1673.00 | 836500.00 | 1638.00 | 819000.00 | 2062.50 | 1031250.00 | 1123.00 | 561500.00 | 1860.00 | 930000.00 | 1814.00 | 907000.00 | 561500.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
123.00 | Supply and fixing 3M of type 1181 or equivalent, 12.5mm wide copper strip/foil with suitable adhesive at specified grids (not exceeding 10m) over the antistatic primer etc. Complete as per manufacturers specification. | 500.00 | RM |  | 176.00 | 88000.00 | 418.00 | 209000.00 | 176.00 | 88000.00 | 800.00 | 400000.00 | 107.00 | 53500.00 | 775.00 | 387500.00 | 123.00 | 61500.00 | 53500.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
124.00 | Supply and application of one coat of epoxy paint of approved make and shade to a total film thickness not less than 50 microns over the existing epoxy paint coat for the door frame and shutter, cleaning, all tools and tackles, consumables, scaffolding & staging etc., complete. | 4000.00 | Sq. Meter |  | 272.00 | 1088000.00 | 323.00 | 1292000.00 | 378.00 | 1512000.00 | 400.00 | 1600000.00 | 466.00 | 1864000.00 | 542.50 | 2170000.00 | 532.00 | 2128000.00 | 1088000.00 | JATAN CONSTRUCTIONS PVT LTD
125.00 | PAINTING OF CONCRETE / STRUCTURAL SURFACES FOR NOMENCLATURE
126.00 | Providing and application one coat of background painting with Black/White/Yellow/Red shade of synthetic enamel paint of Akzonobel/Asian/Berger/over a coat of approved chloride free primer including cost of paint materials, primer, transportation, consumables, manpower including preparation of surface on concrete/ plastered / steel surfaces (SS/CS) to be painted by washing, cleaning & removing of dirt, dust, oil & grease with required agents, scaling & rust removing by scrapping, rubbing with sand paper, wire brush and buffing, grinding using mechanical tools & tackles / necessary equipment etc., including erection and de-erection of scaffolding at all elevations required for completing the work as per technical specifications and as directed by the ENGINEER. | 5000.00 | Sq. Meter |  | 294.00 | 1470000.00 | 418.00 | 2090000.00 | 405.00 | 2025000.00 | 250.00 | 1250000.00 | 423.00 | 2115000.00 | 310.00 | 1550000.00 | 322.00 | 1610000.00 | 1250000.00 | DEE VEE PROJECTS LIMITED
127.00 | Providing and writing of letters/figures/symbols/signs of sizes specified in sub sections below with stencil on item No. 10.2.17.1 using synthetic enamel paint of Akzonobel/Asian / Berger/ including the cost of labour, paint material, transportation, consumables etc. as construction drawings and directed by Engineer.
128.00 | Size 4 cm X 3 cm | 20000.00 | Nos. |  | 29.00 | 580000.00 | 4.00 | 80000.00 | 59.00 | 1180000.00 | 250.00 | 5000000.00 | 10.00 | 200000.00 | 23.25 | 465000.00 | 42.00 | 840000.00 | 80000.00 | P AND C PROJECTS PRIVATE LIMITED
129.00 | Size 6 cm X 4 cm | 20000.00 | Nos. |  | 44.00 | 880000.00 | 4.00 | 80000.00 | 59.00 | 1180000.00 | 375.00 | 7500000.00 | 16.00 | 320000.00 | 46.50 | 930000.00 | 49.00 | 980000.00 | 80000.00 | P AND C PROJECTS PRIVATE LIMITED
130.00 | Size 8 cm X 6 cm | 10000.00 | Nos. |  | 59.00 | 590000.00 | 6.00 | 60000.00 | 59.00 | 590000.00 | 460.00 | 4600000.00 | 24.00 | 240000.00 | 77.50 | 775000.00 | 54.00 | 540000.00 | 60000.00 | P AND C PROJECTS PRIVATE LIMITED
131.00 | Size 15 cm X 10 cm | 5000.00 | Nos. |  | 74.00 | 370000.00 | 12.00 | 60000.00 | 59.00 | 295000.00 | 590.00 | 2950000.00 | 29.00 | 145000.00 | 186.00 | 930000.00 | 57.00 | 285000.00 | 60000.00 | P AND C PROJECTS PRIVATE LIMITED
132.00 | Size 20 cm X 15 cm | 5000.00 | Nos. |  | 88.00 | 440000.00 | 16.00 | 80000.00 | 59.00 | 295000.00 | 750.00 | 3750000.00 | 37.00 | 185000.00 | 310.00 | 1550000.00 | 59.00 | 295000.00 | 80000.00 | P AND C PROJECTS PRIVATE LIMITED
133.00 | FLOORING, SKIRTING, DADO
134.00 | Supply and fixing in position 10 mm (+/- 1 mm) thick premium quality vitrified floor / wall tiles conforming to IS: 15622, of approved make, size, glaze and shade, laid on 20mm thick cement mortar 1:4 for floors and 12mm thick cement mortar 1:3 for walls, skirting including filling the joint with white cement and matching colour pigment, curing, all related materials, equipment, tools & tackles, scaffolding, all consumables etc., complete as per drawings and specifications. | 10000.00 | Sq. Meter |  | 1564.00 | 15640000.00 | 1258.00 | 12580000.00 | 1350.00 | 13500000.00 | 1600.00 | 16000000.00 | 1652.00 | 16520000.00 | 1395.00 | 13950000.00 | 1645.00 | 16450000.00 | 12580000.00 | P AND C PROJECTS PRIVATE LIMITED
135.00 | Supply and fixing in position 6 mm or higher thickness premium quality ceramic floor tiles with anti-skid finish / wall tiles conforming to IS: 15622, of approved make, size, and shade, laid on 20mm thick cement mortar 1:4 for floors and 12mm thick cement mortar 1:3 for walls, skirting including filling the joint with white cement and matching colour pigment, curing, all related materials, equipment, tools & tackles, scaffolding, all consumables etc., complete as per drawings and specifications. | 2000.00 | Sq. Meter |  | 1464.00 | 2928000.00 | 1103.00 | 2206000.00 | 1050.00 | 2100000.00 | 1300.00 | 2600000.00 | 1916.00 | 3832000.00 | 1240.00 | 2480000.00 | 1464.00 | 2928000.00 | 2100000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
136.00 | Supply and fixing in position acid and alkali resistant tiles of approved make and colour at various elevations with 20mm thick acid and alkali resistance mortar, caulking of joints with acid alkali resistant mortar, all related materials, equipment, tools & tackles, scaffolding, all consumables etc., complete as per drawing and specification.
137.00 | 20mm thick tiles | 1000.00 | Sq. Meter |  | 3333.00 | 3333000.00 | 3741.00 | 3741000.00 | 2713.00 | 2713000.00 | 1980.00 | 1980000.00 | 2247.00 | 2247000.00 | 2325.00 | 2325000.00 | 2288.00 | 2288000.00 | 1980000.00 | DEE VEE PROJECTS LIMITED
138.00 | above 20 mm up to 40 mm thick tiles | 500.00 | Sq. Meter |  | 3717.00 | 1858500.00 | 3741.00 | 1870500.00 | 5367.00 | 2683500.00 | 2250.00 | 1125000.00 | 2643.00 | 1321500.00 | 3875.00 | 1937500.00 | 3204.00 | 1602000.00 | 1125000.00 | DEE VEE PROJECTS LIMITED
139.00 | Supply and laying to proper levels and slopes hardonite cement concrete flooring of total 50 mm thickness using 38 mm thick base layer of cement concrete of grade M30 with 12.5mm and down, graded aggregate and a top layer of 12mm thick wearing coat with metallic concrete hardener of approved quality, mixed in the ratio of 1:4 (4 parts of cement : 1 part of metallic hardener) and mixing the same with 2 parts of 6 mm aggregate, making the paste with water cement ratio not exceeding 0.4, including cement slurry, providing glass strips of 3mm thick, laying in alternate bays in panels of size not more than 5m2 in chequered board fashion, mechanical compaction, finishing using power trowels, curing, concrete cutting, filling the gaps between the panels with polysulphide filler inclusive of all materials, equipment etc., complete as per construction drawings and specifications. | 15000.00 | Sq. Meter |  | 869.00 | 13035000.00 | 672.00 | 10080000.00 | 749.00 | 11235000.00 | 960.00 | 14400000.00 | 925.00 | 13875000.00 | 930.00 | 13950000.00 | 619.00 | 9285000.00 | 9285000.00 | Ocean Lifespaces India Private Limited
140.00 | Supply and laying 20 mm (+/- 2 mm) thick polished natural granite slab of approved colour/shade, size suit to site, with all exposed edges buffed for walls and floors at all elevations and locations, set over a base of cement mortar 1:4, 20 mm thick neatly pointed with white cement and colouring pigments to match the shade of the stone, fixing the stone with wall by 2 numbers Hilti HRD-UGT-14X110/40 or approved equivalent make galvanized counter sunk anchor fastener per 1 m2 or as required with wall, curing, rubbing, polishing etc., complete as per construction drawings. | 3000.00 | Sq. Meter |  | 4279.00 | 12837000.00 | 4584.00 | 13752000.00 | 2925.00 | 8775000.00 | 3000.00 | 9000000.00 | 4163.00 | 12489000.00 | 3875.00 | 11625000.00 | 4777.00 | 14331000.00 | 8775000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
141.00 | Supply and laying full body vitrified step tiles having self-embossed grooves for grip, bull nose finish (in treads), anti-skid for staircase and landing, laid over base of 1:3 cement mortar (1 cement: 3 coarse sand) of 12 mm (average) thick, pointed with white cement slurry mixed with pigments to match the shade, including curing, rubbing, polishing etc., complete as per construction drawings and specifications. The thickness shall be minimum 12mm for step tile and minimum 6mm for riser, skirting and landing. | 3000.00 | Sq. Meter |  | 2782.00 | 8346000.00 | 1319.00 | 3957000.00 | 1725.00 | 5175000.00 | 1820.00 | 5460000.00 | 1619.00 | 4857000.00 | 2480.00 | 7440000.00 | 2854.00 | 8562000.00 | 3957000.00 | P AND C PROJECTS PRIVATE LIMITED
142.00 | ROOF INSULATION/DECKING
143.00 | Providing as per requirement and laying heat insulation over the prepared under bed for roofs with using 40 to 60 mm thick highly elastic two component spray applied PU foam (density 40kg/cum) or insulation / mineral wool mattress 200 kg/m3 density at all levels and locations, all related materials, consumables, equipment, labour, tools & tackles, scaffolding etc., complete as per drawings and specifications. | 6750.00 | Sq. Meter |  | 1911.00 | 12899250.00 | 454.00 | 3064500.00 | 380.00 | 2565000.00 | 830.00 | 5602500.00 | 1441.00 | 9726750.00 | 1550.00 | 10462500.00 | 3015.00 | 20351250.00 | 2565000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
144.00 | Supply and laying single skin permanently colour coated troughed metal roof sheet not less than 0.6 mm BMT/TCT with galvanised as per construction drawings and specifications. | 1500.00 | Sq. Meter |  | 985.00 | 1477500.00 | 514.00 | 771000.00 | 1328.00 | 1992000.00 | 1500.00 | 2250000.00 | 1295.00 | 1942500.00 | 1240.00 | 1860000.00 | 1407.00 | 2110500.00 | 771000.00 | P AND C PROJECTS PRIVATE LIMITED
145.00 | Supply and fixing roofing at all elevations using zinc-aluminium alloy coated profile sheet of 0.45mm thickness of TATA "Durashine" make or equivalent of approved colour including over laps, side cladding, ridges, eaves board, gutters, including fixing of necessary 6mm diameter J or L GI hooks, bolts, nuts, screws, bitumen washers, sealing of joints, preparation of installation drawings etc., complete all as per manufacturer's recommendations including scaffolding as per construction drawings and specifications. Note:Payment shall be made only to the superficial area. No over laps, corrugations/profile will be considered in the quantity measured for payment. | 850.00 | Sq. Meter |  | 985.00 | 837250.00 | 2987.00 | 2538950.00 | 996.00 | 846600.00 | 1500.00 | 1275000.00 | 1123.00 | 954550.00 | 1240.00 | 1054000.00 | 1407.00 | 1195950.00 | 837250.00 | JATAN CONSTRUCTIONS PVT LTD
146.00 | Supply and fixing zinc coated steel decking system of thickness 0.8mm - EZYDECKTM of Tata Bluescope Steel or approved equivalent at all elevations of approved colour including overlaps, required manpower, fasteners, tools required for fixing, retrievable supporting material , preparation of installation drawings etc., complete as per manufacturer's recommendations, construction drawings and specifications. The supply and fixing as per construction drawings, the shear studs will be paid under relevant item. | 10000.00 | Sq. Meter |  | 2058.00 | 20580000.00 | 1255.00 | 12550000.00 | 1338.00 | 13380000.00 | 1900.00 | 19000000.00 | 1553.00 | 15530000.00 | 1627.50 | 16275000.00 | 1675.00 | 16750000.00 | 12550000.00 | P AND C PROJECTS PRIVATE LIMITED
147.00 | DOORS
148.00 | Design and qualification of three criteria fireproof doors / gates /hatches for the specified fire rating, seismic and functional requirements as per the technical specification, detailing, submission of design and fabrication drawing for approval, manufacturing the sample doors/hatches with fixtures and fittings as per specification, qualification of the same by conducting fire performance test as per IS 3614 (Part-2) for three criteria (stability, integrity and insulation) at approved fire testing laboratory, repeat qualification test, if required, and submitting the final fire performance qualification report, qualification of fire performance qualified hatch design for leak tightness not more than 2 m3/day at differential pressure up to 2 kPa by providing special gasket, fire performance qualified doors with sealed rabbet ledge type for leak tightness not more than 2m3/day at differential pressure up to 200 Pa by providing special gasket etc., complete. Note: Payment shall be made only for the qualified tests for the fire performance and leak tightness. The cost includes the cost of the sample doors / hatches tested.
149.00 | Single leaf / double leaf 2.0 hr rating fireproof or sealed door / hatch
150.00 | Fire performance test | 3.00 | Each |  | 1543500.00 | 4630500.00 | 2390.00 | 7170.00 | 1000000.00 | 3000000.00 | 1650000.00 | 4950000.00 | 33040.00 | 99120.00 | 930000.00 | 2790000.00 | 75724.00 | 227172.00 | 7170.00 | P AND C PROJECTS PRIVATE LIMITED
151.00 | Leak tightness test | 3.00 | Each |  | 1396500.00 | 4189500.00 | 1792.00 | 5376.00 | 1000000.00 | 3000000.00 | 1650000.00 | 4950000.00 | 23789.00 | 71367.00 | 775000.00 | 2325000.00 | 75724.00 | 227172.00 | 5376.00 | P AND C PROJECTS PRIVATE LIMITED
152.00 | Design, detailing, supply and fixing single or double leaves three criteria fireproof doors/hatches/gates designed for seismic and functional requirements as per the technical specification, fabricated from hollow/in filled pressed galvanised iron steel frame/shutter of 2 hr fire rating, manufactured as per approved specific fire performance qualified design with hardware, fixtures and fittings as detailed in the specification and construction drawings, providing vision panel in each leaf using borosilicate float glass or approved equivalent of size specified in the drawings and having same fire rating as door, making arrangement for installing hydraulic door closer, dead lock and panic bar, replaceable intumescent sealing and gaskets along the perimeter for providing fire performance and tightness, fire retardant corrosion protection coating with not less than 160 micron DFT epoxy paint of approved shade over suitable primer of 60-70 micron, providing and filling of hollow portions of door frame with suitable fire stop material, fixing in position at various floors of the building by welding to the existing embedded parts or with anchor fasteners at specified intervals, providing and fixing name plate made of 4 mm thick SS plate of size 300mm x 300mm width embossing the KKS code, designation and year of manufacturing, submission of erection report etc., complete at all levels as per drawing, technical document and specification. Notes: 1.The total weight of the door/ hatches / gates frame (excluding fire stop compound to be filled in the door frame) and shutter along with fixtures, fittings shall be measured together for payment. 2.The fire stop compound filling inside door frame, panic bar, hydraulic door closer and dead lock shall be paid under relevant item. 3.The payment shall be made in stages on percentage of rate quoted against item as specified in the sub items below. 4.The fireproof doors with sealed rabbet ledge type shall be fitted with special gasket and cam lock with lever arrangement to ensure leak tightness not more than 2 m3/ day at pressure difference up to 200Pa. 5.The fireproof hatches shall be fitted with special gasket for providing leak tightness not more than 2 m3/day at pressure difference up to 2 kPa.
153.00 | Single leaf fireproof hatches of 2.0hr fire rating Stage-1: Supply as per requirement - 75% of quoted rate. Stage-2: Transporting to site and erection and commissioning - 25% of quoted rate. | 10000.00 | Kg |  | 889.00 | 8890000.00 | 287.00 | 2870000.00 | 645.00 | 6450000.00 | 850.00 | 8500000.00 | 304.00 | 3040000.00 | 542.50 | 5425000.00 | 857.00 | 8570000.00 | 2870000.00 | P AND C PROJECTS PRIVATE LIMITED
154.00 | Single/double leaves fireproof doors of 2.0hr fire rating Stage-1: Supply as per requirement - 75% of quoted rate. Stage-2: Transporting to site and erection and commissioning - 25% of quoted rate. | 60000.00 | Kg |  | 948.00 | 56880000.00 | 287.00 | 17220000.00 | 647.00 | 38820000.00 | 800.00 | 48000000.00 | 304.00 | 18240000.00 | 465.00 | 27900000.00 | 857.00 | 51420000.00 | 17220000.00 | P AND C PROJECTS PRIVATE LIMITED
155.00 | Single leaf fireproof door of 2.0hr fire rating with sealed rabbit ledge. Stage-1: Supply as per requirement - 75% of quoted rate. Stage-2: Transporting to site and erection and commissioning - 25% of quoted rate. | 15000.00 | Kg |  | 919.00 | 13785000.00 | 287.00 | 4305000.00 | 648.00 | 9720000.00 | 850.00 | 12750000.00 | 449.00 | 6735000.00 | 465.00 | 6975000.00 | 857.00 | 12855000.00 | 4305000.00 | P AND C PROJECTS PRIVATE LIMITED
156.00 | Design, detailing and supply and fixing as per requirement single or double leaves steel doors/hatches/gates as per below item description of various size designed for seismic and functional requirement of differential pressure as per the technical specification, submission of design and fabrication drawing for approval, fabricated using hollow metal pressed steel/structural steel frames, shutters, fitted with hardware, fixtures and fittings as detailed in the specification or construction drawings, providing 6mm clear sheet vision panel of specified size in each leaf as specified, making arrangement for installing hydraulic door closer and dead lock, replaceable gasket sealing along the perimeter for tightness, corrosion protection coating with 160 micron DFT epoxy paint of approved shade over suitable primer of 60-70micron, application of additional PU coating of 40-60 micron on the external face, filling of hollow portions of door frame with concrete, fixing in position at various floors of the buildings by welding to the existing embedded parts or with anchor fasteners at specified intervals, providing fixing name plate made of 4 mm thick SS plate of size 300mm x 300mm width embossing the KKS code, designation and year of manufacturing, submission of erection report etc., complete at all levels as per drawings, technical documents and specifications. Notes: 1.The total weight of the door frame and shutter (excluding concrete filled in the door frame) along with fixtures, fittings shall be measured together for payment. 2.The concrete filled inside the door frame, hydraulic door closer and dead lock shall be paid under relevant item. 3.The payment shall be made in stages on percentage of rate quoted against item as specified below. Stage-1: Supply as per requirement - 75% of quoted rate. Stage-2: Transporting to site and erection and commissioning - 25% of quoted rate.
157.00 | Single/double leaf steel doors/hatches/gates | 2500.00 | Kg |  | 845.00 | 2112500.00 | 287.00 | 717500.00 | 645.00 | 1612500.00 | 950.00 | 2375000.00 | 304.00 | 760000.00 | 542.50 | 1356250.00 | 669.00 | 1672500.00 | 717500.00 | P AND C PROJECTS PRIVATE LIMITED
158.00 | Single/double leaf steel doors/hatches/gates with insulation of mineral wool having density not less than 144 kg/m3. | 5000.00 | Kg |  | 860.00 | 4300000.00 | 287.00 | 1435000.00 | 645.00 | 3225000.00 | 1000.00 | 5000000.00 | 456.00 | 2280000.00 | 542.50 | 2712500.00 | 679.00 | 3395000.00 | 1435000.00 | P AND C PROJECTS PRIVATE LIMITED
159.00 | Single/double leaf steel doors/hatches/gates without insulation with sealing arrangement for air intake chambers of the plenum ventilation centres. | 5000.00 | kg |  | 867.00 | 4335000.00 | 287.00 | 1435000.00 | 645.00 | 3225000.00 | 900.00 | 4500000.00 | 337.00 | 1685000.00 | 465.00 | 2325000.00 | 669.00 | 3345000.00 | 1435000.00 | P AND C PROJECTS PRIVATE LIMITED
160.00 | Single/double leaf metal doors/gates of various sizes with sealed rabbet ledge and insulation of mineral wool having density not less than 144 kg/m3. | 8000.00 | Kg |  | 845.00 | 6760000.00 | 287.00 | 2296000.00 | 645.00 | 5160000.00 | 900.00 | 7200000.00 | 449.00 | 3592000.00 | 465.00 | 3720000.00 | 679.00 | 5432000.00 | 2296000.00 | P AND C PROJECTS PRIVATE LIMITED
161.00 | Supply and installation of heavy duty door closure of Dormakaba® make TS 73 Door Closer with standard arm or approved equivalent to the specified doors as per construction drawing and specification. | 1000.00 | Nos. |  | 5145.00 | 5145000.00 | 11113.00 | 11113000.00 | 4888.00 | 4888000.00 | 5500.00 | 5500000.00 | 4824.00 | 4824000.00 | 7440.00 | 7440000.00 | 10797.00 | 10797000.00 | 4824000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
162.00 | Supply and installation of heavy duty 7 lever dead lock of Godrej® make or equivalent to the specified doors as per construction drawing and specification. | 1000.00 | Nos. |  | 7350.00 | 7350000.00 | 2689.00 | 2689000.00 | 6983.00 | 6983000.00 | 7500.00 | 7500000.00 | 5419.00 | 5419000.00 | 5425.00 | 5425000.00 | 4806.00 | 4806000.00 | 2689000.00 | P AND C PROJECTS PRIVATE LIMITED
163.00 | Supply and installation of approved make panic bar of Dormakaba® make PHA 2000 1 point modular panic bar or approved equivalent to the specified fire doors as per construction drawing and specification. | 250.00 | Nos. |  | 11025.00 | 2756250.00 | 16131.00 | 4032750.00 | 10475.00 | 2618750.00 | 12000.00 | 3000000.00 | 15198.00 | 3799500.00 | 20925.00 | 5231250.00 | 13723.00 | 3430750.00 | 2618750.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
164.00 | Supply and filling fire stop compound to the door frame as per the approved fire performance / insulation requirement. | 25000.00 | Kg |  | 204.00 | 5100000.00 | 358.00 | 8950000.00 | 158.00 | 3950000.00 | 500.00 | 12500000.00 | 3436.00 | 85900000.00 | 186.00 | 4650000.00 | 195.00 | 4875000.00 | 3950000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
165.00 | Supply, erection and dismantling of temporary steel partitions/doors of various sizes as per functional requirement and to suit at site condition, frame fabricated with M.S angles and shutter with 2-3 mm MS sheets fitted with fixtures such as M.S hinges, MS handles and aldrop, painted with two coats of enamel paint of approved shade over a coat of suitable primer, fixing the door by welding with embedded parts or with anchor fasteners, dismantling the same before erection of permanent door and making good of the embedded parts by grinding, handing over the dismantled steel door to the NPCIL store etc., complete. Note: Total weight of door including fittings, fixtures shall be measured for payment.
166.00 | Providing as per requirement, installation at any location steel doors with locking as directed by NPCIL and handing over to the NPCIL store after dismantling. | 5000.00 | Kg |  | 154.00 | 770000.00 | 143.00 | 715000.00 | 173.00 | 865000.00 | 300.00 | 1500000.00 | 205.00 | 1025000.00 | 201.50 | 1007500.00 | 46.00 | 230000.00 | 230000.00 | Ocean Lifespaces India Private Limited
167.00 | FALSE CEILING
168.00 | Preparation of shop drawings for the entire scope of false ceiling to show complete system installation, including framing around fixtures, ducts, grills, access panels, fire alarm, spray, smoke detectors , ventilation grills and communication system, etc., complete for the approval of ENGINEER prior to execution of work. Note : 1.Scope includes side cladding with anodised aluminium frame work using anodised aluminium sections, with adjustable GI rods, holding cleats grid work suitably modified along the walls and beams, fixed with anchor bolts, making extra frame work around the air conditioning and electrical fixtures and fittings fixed with necessary clips and fixing 12.5 mm thick GYPBOARD® or equivalent approved make as per IS: 2095, mock-up, etc., complete as per construction drawings and specifications 2.suitable mock up shall be arranged and approval of Engineer has to be obtained prior to the execution of work.
169.00 | Supply and fixing in position by qualified system installer suspended gypsum board false ceiling of Gyproc® or approved equivalent. | 5000.00 | Sq. Meter |  | 1882.00 | 9410000.00 | 1028.00 | 5140000.00 | 1485.00 | 7425000.00 | 1650.00 | 8250000.00 | 1916.00 | 9580000.00 | 1240.00 | 6200000.00 | 1281.00 | 6405000.00 | 5140000.00 | P AND C PROJECTS PRIVATE LIMITED
170.00 | Supply and fixing in position by qualified system installer suspended aluminium false ceiling Luxalon® 84C or approved equivalent with grid concealed system and butt joint panels. | 700.00 | Sq. Meter |  | 5108.00 | 3575600.00 | 8185.00 | 5729500.00 | 2216.00 | 1551200.00 | 3000.00 | 2100000.00 | 1916.00 | 1341200.00 | 3100.00 | 2170000.00 | 2380.00 | 1666000.00 | 1341200.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
171.00 | System having tray type of panel of rectangular shape and minimum thickness of 0.7mm thickness with electro statically polyester powder coated minimum thickness of 60 microns of approved RAL colour shade. | 1500.00 | Sq. Meter |  | 5329.00 | 7993500.00 | 5377.00 | 8065500.00 | 1204.00 | 1806000.00 | 3300.00 | 4950000.00 | 4229.00 | 6343500.00 | 3100.00 | 4650000.00 | 3524.00 | 5286000.00 | 1806000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
172.00 | Supply and fixing of Aluminium ventilation grills of size 600mm x 600mm as per specification and directed by ENGINEER. | 1000.00 | Nos. |  | 3602.00 | 3602000.00 | 2581.00 | 2581000.00 | 4347.00 | 4347000.00 | 4620.00 | 4620000.00 | 3238.00 | 3238000.00 | 3100.00 | 3100000.00 | 2778.00 | 2778000.00 | 2581000.00 | P AND C PROJECTS PRIVATE LIMITED
173.00 | Structural and embeded parts works
174.00 | Supply, transportation to site, storage, fabrication of carbon steel structural elements using IS rolled sections, plate sections, parallel flange beams (NPB), universal beams (UB), universal columns (UC), rail sections, beams for supporting crane rails, crane platforms, gantry girders, plates/sheets, chequered plate, ERW pipes, square/circular hot finished seamless tube (HFS, of Yst 240 MPa), MS flats, square/round bars etc., preparation of detailed metal structure (DMS) i.e., fabrication and erection drawings, work procedure, fabrication without surface preparation or with surface preparation by grit blasting / pickling in acid and supply and application of Inorganic Zinc Silicate (Zinc rich) primer of M/s. BERGER / ASIAN or approved equivalent with DFT not less than 75 microns or as brought out in item descriptions below, handling, transporting to site and erection in position with necessary stiffeners, gussets, base plates, welding, supply & fixing of bolts, fixing the gratings over platforms with clamps and HILTI or equivalent make self-tapping screws (including supply as per requirement), welding of anchor bars, including all tools and tackles, temporary erection bolts, consumables, scaffoldings/temporary platforms, at all elevations and locations, complete for inside and outside the buildings/ structures, preparation of reports etc., as per construction drawings and specifications. Notes: 1. Material shall be delivered to site with MTC fulfilling the technical requirement as per specification. 2. Rate to include all tests to be conducted as per the approved QAP. 3. The temporary erection bolts shall not be considered for payment. 4. The machining of any component shall be measured separately under relevant item. 5. The NDE for the weld joints as per drawing and specification shall be measured separately under relevant items. 6. The payment shall be made in stages on percentage of rate quoted against item as specified in the sub items below.
175.00 | Structural steel/handrail/grating/ladder/ventilation stack works using elements of grade E250 Quality A/BR/B0/C as per IS 2062 for various applications as per the construction drawings and specifications. Stage-1: Supply and per requirement, fabrication, surface preparation and application of inorganic zinc silicate primer not less than 75 micron DFT - 70% of quoted rate. Stage-2: Transporting to the location and erection - 30% of quoted rate. | 1250.00 | MT |  | 149940.00 | 187425000.00 | 119489.00 | 149361250.00 | 151288.00 | 189110000.00 | 135000.00 | 168750000.00 | 124230.00 | 155287500.00 | 217000.00 | 271250000.00 | 151450.00 | 189312500.00 | 149361250.00 | P AND C PROJECTS PRIVATE LIMITED
176.00 | Structural steel/handrail/grating/ladder works using elements of grade E250 Quality A/BR/B0/C as per IS 2062 structural steel elements for various applications as per the construction drawings and specifications including application of hot dip galvanizing (HDG) not less than 70 microns. Stage-1: Supply and per requirement, fabrication, surface preparation and hot dip galvanising - 70% of quoted rate. Stage-2: Transporting to the location and erection - 30% of quoted rate. | 100.00 | MT |  | 183750.00 | 18375000.00 | 119489.00 | 11948900.00 | 174168.00 | 17416800.00 | 175000.00 | 17500000.00 | 191632.00 | 19163200.00 | 232500.00 | 23250000.00 | 163100.00 | 16310000.00 | 11948900.00 | P AND C PROJECTS PRIVATE LIMITED
177.00 | Structural steel works using elements of grade E350 Quality A/BR/B0/C as per IS 2062 for various applications as per the construction drawings and specifications. Stage-1: Supply and per requirement, fabrication, surface preparation and application of Inorganic Zinc Silicate primer - 70% of Quoted rate. Stage-2: Transporting to the location and erection - 30% of quoted rate. | 300.00 | MT |  | 161700.00 | 48510000.00 | 119489.00 | 35846700.00 | 153335.00 | 46000500.00 | 150000.00 | 45000000.00 | 135464.00 | 40639200.00 | 217000.00 | 65100000.00 | 151450.00 | 45435000.00 | 35846700.00 | P AND C PROJECTS PRIVATE LIMITED
178.00 | Temporary covers using GI sheets over the erected gratings or any other place as required with clamps and hardware to prevent fall of objects without surface preparation and primer. Stage-1: Providing as per requirement of materials -70% of quoted rate. Stage-2: Transporting to the location and erection -30% of quoted rate. | 10.00 | MT |  | 183750.00 | 1837500.00 | 119489.00 | 1194890.00 | 131395.00 | 1313950.00 | 225000.00 | 2250000.00 | 158592.00 | 1585920.00 | 201500.00 | 2015000.00 | 139800.00 | 1398000.00 | 1194890.00 | P AND C PROJECTS PRIVATE LIMITED
179.00 | Rail sections ISCR 80 as per IS-3443 or as shown in the construction drawings of minimum tensile strength 710 MPa including levelling, alignment, welding/fixing to embedded parts / supports etc., complete. Stage-1: Supply as per requirement and fabrication -70% of quoted rate. Stage-2: Transporting to the location and erection -30% of quoted rate. Note: The ancillary items required for fixing the rail section with the structural element will be paid under relevant item. | 45.00 | MT |  | 183750.00 | 8268750.00 | 119489.00 | 5377005.00 | 130650.00 | 5879250.00 | 220000.00 | 9900000.00 | 132160.00 | 5947200.00 | 186000.00 | 8370000.00 | 174750.00 | 7863750.00 | 5377005.00 | P AND C PROJECTS PRIVATE LIMITED
180.00 | Entry gates grade E250 Quality A as per IS 2062 including guide rails and wheels with ball bearings as per details specified in the construction drawings including making temporary support arrangement during while fixing it with civil structure, etc., complete. Stage-1: Supply as per requirement and fabrication -70% of quoted rate. Stage-2: Transporting to the location and erection -30% of quoted rate. | 5.00 | MT |  | 161700.00 | 808500.00 | 119489.00 | 597445.00 | 147518.00 | 737590.00 | 250000.00 | 1250000.00 | 165200.00 | 826000.00 | 232500.00 | 1162500.00 | 174750.00 | 873750.00 | 597445.00 | P AND C PROJECTS PRIVATE LIMITED
181.00 | Grills grade E250 Quality A as per IS 2062 for windows including fixing with required hardware such as screws, nuts, washer, bolts, etc., as per construction drawings and specifications. Stage-1: Supply as per requirement and fabrication -70% of quoted rate. Stage-2: Transporting to the location and erection -30% of quoted rate. | 5.00 | MT |  | 161700.00 | 808500.00 | 131438.00 | 657190.00 | 160518.00 | 802590.00 | 225000.00 | 1125000.00 | 151984.00 | 759920.00 | 201500.00 | 1007500.00 | 116500.00 | 582500.00 | 582500.00 | Ocean Lifespaces India Private Limited
182.00 | Supply and erecting of various type of foundation/anchor bolts/hex headed bolts/studs and hardware of specified length, size as per construction drawing including suitable threading, supplying check/lock nuts as per design requirement, making suitable template for erection of bolts prior to concrete and protecting the projected portion of bolt and thread by lubricant/grease with plastic protecting cover/cap, after erection torque tightening of the nuts to the value as specified in the construction drawings and specifications, at all elevations and locations, etc., complete. Note: 1. Material shall be delivered to site with MTC fulfilling the technical requirement as per specification. 2. Rate to include all tests to be conducted as per the approved QAP. 3. The temporary erection bolts will not be considered for payment. 4. The payment shall be made in stages on percentage of rate quoted against item as specified in the sub items below. 5. Supply, fabrication and fixing of template, if any, shall be paid as per separate item for structural steel works.
183.00 | Mild steel foundation/anchor bolts of strength class E250A (below 20mm diameter) and E250 BR (above 20mm diameter) as per IS 2062 including nuts and welded end plate as per construction drawings and specifications. Stage-1: Supply of materials and fabrication - 80% of Quoted rate. Stage-2: Transporting to the location and erection -20% of Quoted rate. | 3000.00 | Kg |  | 215.00 | 645000.00 | 143.00 | 429000.00 | 143.00 | 429000.00 | 300.00 | 900000.00 | 145.00 | 435000.00 | 201.50 | 604500.00 | 148.00 | 444000.00 | 429000.00 | P AND C PROJECTS PRIVATE LIMITED, Dineshchandra R Agrawal Infracon Pvt. Ltd.
184.00 | Galvanized iron Anchor bolts/foundation bolts / Studs of strength class 8.8 as per IS 1367 and IS 3757/EN-19/equivalent material, suitable threads pitch at the ends along with washers, nut and lock nuts, galvanized coating thickness not less than 40μm as per the construction drawings and specifications. Stage-1: Supply of materials and fabrication - 80% of Quoted rate. Stage-2: Transporting to the location and erection -20% of Quoted rate. | 3000.00 | Kg |  | 223.00 | 669000.00 | 143.00 | 429000.00 | 325.00 | 975000.00 | 300.00 | 900000.00 | 198.00 | 594000.00 | 232.50 | 697500.00 | 186.00 | 558000.00 | 429000.00 | P AND C PROJECTS PRIVATE LIMITED
185.00 | Cadmium coated Hex headed bolts / studs of Strength Class 8.8 as per IS 1367 and IS 3757/EN-19/equivalent material, suitable threads at the end along with washers, nuts and lock nuts, cadmium coating to the thickness not less than 40μm as per drawing and specification. Stage-1: Supply of materials and fabrication - 80% of Quoted rate. Stage-2: Transporting to the location and erection -20% of Quoted rate. | 10000.00 | Kg |  | 241.00 | 2410000.00 | 179.00 | 1790000.00 | 618.00 | 6180000.00 | 310.00 | 3100000.00 | 172.00 | 1720000.00 | 248.00 | 2480000.00 | 276.00 | 2760000.00 | 1720000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
186.00 | Cadmium coated Hex headed bolts / studs of Strength Class 10.9 as per IS 1367 and IS 3757/EN-19/equivalent material, suitable threads at the end along with washers, nuts and lock nuts, cadmium coating to the thickness not less than 40μm as per drawing and specification. Stage-1: Supply of materials and fabrication - 80% of Quoted rate. Stage-2: Transporting to the location and erection -20% of Quoted rate. | 500.00 | Kg |  | 268.00 | 134000.00 | 179.00 | 89500.00 | 683.00 | 341500.00 | 400.00 | 200000.00 | 185.00 | 92500.00 | 263.50 | 131750.00 | 302.00 | 151000.00 | 89500.00 | P AND C PROJECTS PRIVATE LIMITED
187.00 | Fabrication,Supply, transportation to site, storage,and erection of Mild steel / Carbon Steel structural embedded parts with anchorage elements and penetrations using IS standard rolled sections, Plates / Sheets, chequered plates, ISRO round rods, flats, Square / circular Hot finished seamless tube (HFS), ERW pipes etc. Preparation of detailed fabrication & erection drawings, work procedure, cutting, rolling, bending, channel / angle forming from plate, grinding,drilling / Countersunk drilling, welding, welding of anchor bars, straightening of EP after welding, surface preparationby grit blasting / pickling in acid, supply and application of Inorganic Zinc Silicate (Zinc rich) Primer of M/s. BERGER /ASIAN or approved equivalent with DFT not less than 75 microns, handling , transporting to site and erection inposition with necessary jigs, fixtures, including all tools and tackles, consumables, necessary scaffoldings / temporaryplatforms, at all elevations and locations, complete for inside and outside the buildings, structures, preparation ofreports etc. Note 1: The carbon steel anchorage element is MS rods of Grade SAE-1015/ISRO conform to IS 1732,MS rods( confirming to IS 1875)/ MS flats (confirming to IS 2062)/ Fe 500D reinforment bar( confirming to IS1786) welded to the carbon steel / stainless steel embeded parts. Note 2: 1.Material shall be delivered to site with MTC fulfilling the technical requirement as perspecification. 2.Rate to include all tests to be conducted as per the approved QAP. 3.Machining of any componentshall be measured separately as per the relevant B.O.Q item. 4.The NDE for the weld joints as per drawing and specification shall be measuredseparately as per the relevant B.O.Q items. 5.The jigs and fixtures for erecting the embedded parts, penetration inposition shall be measured separately as per the relevant B.O.Q items corresponding to the material of jigs andfixtures. 6.The payment shall be made in stages on percentage of rate quoted against item as specified in the subitems below.
188.00 | Embedded parts at floor/wall/slab manufactured using steel plates and rolled section of grade E250 Quality A as per IS2062-2011. Stage-1 :Supply of materials , fabrication, surface preparation and application of Inorganic Zinc Silicateprimer -70% of Quoted rate. Stage-2 :Transporting to the location and erection -30% of Quoted rate. | 640.00 | MT |  | 149940.00 | 95961600.00 | 119489.00 | 76472960.00 | 156975.00 | 100464000.00 | 190000.00 | 121600000.00 | 124230.00 | 79507200.00 | 217000.00 | 138880000.00 | 144955.00 | 92771200.00 | 76472960.00 | P AND C PROJECTS PRIVATE LIMITED
189.00 | Tubular penetrations with or without flange plates/stiffeners using ERW pipes of Yst 240 as per IS 1239 / IS 1161 / IS 3589. Stage-1: Supply of materials and fabrication - 70% of quoted rate. Stage-2: Transporting to the location and erection -30% of Quoted rate. | 40.00 | MT |  | 161700.00 | 6468000.00 | 119489.00 | 4779560.00 | 163670.00 | 6546800.00 | 200000.00 | 8000000.00 | 171808.00 | 6872320.00 | 217000.00 | 8680000.00 | 149848.00 | 5993920.00 | 4779560.00 | P AND C PROJECTS PRIVATE LIMITED
190.00 | Tubular penetrations with or without flange plates/stiffeners using hot finished seamless (HFS) pipes of Yst 240 as per IS 1239 / IS 1161 / IS 3589. Stage-1: Supply of materials and fabrication - 70% of quoted rate. Stage-2: Transporting to the location and erection -30% of Quoted rate. | 12.00 | MT |  | 161700.00 | 1940400.00 | 119489.00 | 1433868.00 | 172770.00 | 2073240.00 | 220000.00 | 2640000.00 | 198240.00 | 2378880.00 | 232500.00 | 2790000.00 | 181041.00 | 2172492.00 | 1433868.00 | P AND C PROJECTS PRIVATE LIMITED
191.00 | Tubular/rectangular penetrations with or without flange plate and stiffeners fabricated using steel plates of grade E 250 Quality A of different sizes and thicknesses up to 20mm. Stage-1: Supply of materials and fabrication - 70% of quoted rate. Stage-2: Transporting to the location and erection -30% of Quoted rate. | 50.00 | MT |  | 161700.00 | 8085000.00 | 119489.00 | 5974450.00 | 156975.00 | 7848750.00 | 200000.00 | 10000000.00 | 151984.00 | 7599200.00 | 217000.00 | 10850000.00 | 155964.00 | 7798200.00 | 5974450.00 | P AND C PROJECTS PRIVATE LIMITED
192.00 | Embedded parts of carbon steel liner at floor / wall using rolled sections of grade E 250 Quality A or built up channel / angle from plate using Grade E 250 Quality BR as per IS 2062-2011 with additional impact requirement of 27J at room temperature, welded with anchor rod / flat etc., complete. | 10.00 | MT |  | 154350.00 | 1543500.00 | 119489.00 | 1194890.00 | 170170.00 | 1701700.00 | 280000.00 | 2800000.00 | 158592.00 | 1585920.00 | 217000.00 | 2170000.00 | 151071.00 | 1510710.00 | 1194890.00 | P AND C PROJECTS PRIVATE LIMITED
193.00 | Supply, fabrication and erection as per requirement of stainless steel plates and embedded parts of various thickness and shapes conforming to ASTM A 240- TP321 with IGC TESTED as per A-262 Practice -E for liner and other specified works in the construction drawings, fit up and welding of shop joints using GTAW process, inspection, welding of CS/SS anchorage elements, dissimilar welding, handling, transporting to site and erection in position with necessary jigs, fixtures, inspection including all tools and tackles, consumables, necessary scaffoldings / temporary platforms, at all elevations and locations, complete for inside and outside the buildings, structures, preparation of reports etc., as per drawing and specification. Notes: 1.Material shall be delivered to site with MTC fulfilling the technical requirement as per specification. 2.Rate to include all tests to be conducted as per the approved QAP. 3.The quantity of anchor bars shall be measured separately the relevant SOQR item. 4.The NDE for the weld joints as per drawing and specification shall be measured separately as per the relevant B.O.Q items. 5.The jigs and fixtures for erecting the embedded parts, penetration in position shall be measured separately as per the relevant B.O.Q items corresponding to the material of jigs and fixtures. 6.The payment shall be made in stages on percentage of rate quoted against item as specified in the sub items below. Stage-1:Providing as per requirement Supply of materials and fabrication -70% of quoted rate. Stage-2: Transporting to the location and erection -30% of quoted rate. | 10.00 | MT |  | 882000.00 | 8820000.00 | 537702.00 | 5377020.00 | 428168.00 | 4281680.00 | 1000000.00 | 10000000.00 | 396480.00 | 3964800.00 | 697500.00 | 6975000.00 | 526299.00 | 5262990.00 | 3964800.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
194.00 | Supplying carbon steel plates of various thickness up to 20mm conforming to Grade E 250 Quality - A /B /C / E 250 BR as per IS 2062 along with MTC for physical, chemical & mechanical properties as specified by ENGINEER. Notes: 1. Material shall be delivered to site with MTC fulfilling the technical requirement as per specification. 2. Rate to include all tests to be conducted as per the approved QAP. | 10.00 | MT |  | 169050.00 | 1690500.00 | 179234.00 | 1792340.00 | 84305.00 | 843050.00 | 300000.00 | 3000000.00 | 85904.00 | 859040.00 | 131750.00 | 1317500.00 | 145625.00 | 1456250.00 | 843050.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
195.00 | Supply and fixing at all elevations and locations round/hexagonal headed, cadmium coated shear studs confirming to BS EN ISO 13918 standard or approved equivalent, fixed using drawn arc welding, including the ceramic ferrules as shear connectors for the composite slab construction as per specifications and construction drawings.
196.00 | M13x75 | 600.00 | Kg |  | 158.00 | 94800.00 | 179.00 | 107400.00 | 748.00 | 448800.00 | 600.00 | 360000.00 | 165.00 | 99000.00 | 232.50 | 139500.00 | 269.00 | 161400.00 | 94800.00 | JATAN CONSTRUCTIONS PVT LTD
197.00 | M16x75 | 600.00 | Kg |  | 158.00 | 94800.00 | 179.00 | 107400.00 | 748.00 | 448800.00 | 650.00 | 390000.00 | 192.00 | 115200.00 | 232.50 | 139500.00 | 269.00 | 161400.00 | 94800.00 | JATAN CONSTRUCTIONS PVT LTD
198.00 | PAINTING FOR STRUCTURAL STEEL
199.00 | Supply, transportation, temperature controlled storage and application of UV resistant paint over structural steel members of total dry film thickness (DFT) of 275 microns consisting of following coats on already primed surfaces - 1. Zinc rich epoxy primer coat of total DFT 75 micron in two layers of make Interzinc® 52 or approved equivalent. 2. Epoxy body coat of total DFT not less than 150 micron in two layers of make Intergard ® 475 HS or equivalent. 3. Finish coat of acrylic polyurethane of total DFT 50 micron in single layer of make Interthane ® 990 or approved equivalent. including preparation of surface as per manufacturers recommendations, tools & tackles, consumables, scaffolding and all required machinery, etc., at all elevations and locations as per construction drawings and specifications.
200.00 | External structural steel members of platforms, ladder, grating, etc., as per specifications and drawings. | 300.00 | MT |  | 23520.00 | 7056000.00 | 26288.00 | 7886400.00 | 17901.00 | 5370300.00 | 15000.00 | 4500000.00 | 18502.00 | 5550600.00 | 23250.00 | 6975000.00 | 20640.00 | 6192000.00 | 4500000.00 | DEE VEE PROJECTS LIMITED
201.00 | External surface of vent stack (03 UKH) as per specifications and drawings. | 500.00 | Sq. Meter |  | 595.00 | 297500.00 | 574.00 | 287000.00 | 895.00 | 447500.00 | 2500.00 | 1250000.00 | 925.00 | 462500.00 | 620.00 | 310000.00 | 3020.00 | 1510000.00 | 287000.00 | P AND C PROJECTS PRIVATE LIMITED
202.00 | Supply. transportation, storage and application of synthetic enamel paint of approved make and shade over structural steel members of total dry film thickness (DFT) of 200 micron consisting of following coats on already primed surfaces - 1. Zinc chromate primer coat of approved make of total DFT 50 micron. 2. Synthetic enamel paint coat of total DFT 150 micron in two layers. including preparation of surface as per manufacturers recommendations, tools & tackles, consumables, scaffolding and all required machinery, etc., at all elevations and locations as per construction drawings and specifications.
203.00 | Over internal structural steel members of platforms, ladder, grating, etc., as per specifications and drawings. | 700.00 | MT |  | 3726.00 | 2608200.00 | 17923.00 | 12546100.00 | 12168.00 | 8517600.00 | 10230.00 | 7161000.00 | 7269.00 | 5088300.00 | 15500.00 | 10850000.00 | 12815.00 | 8970500.00 | 2608200.00 | JATAN CONSTRUCTIONS PVT LTD
204.00 | Over ducts, conduits, trays, etc., as per specifications and drawings. | 5000.00 | Sq. Meter |  | 294.00 | 1470000.00 | 442.00 | 2210000.00 | 608.00 | 3040000.00 | 1534.50 | 7672500.00 | 251.00 | 1255000.00 | 310.00 | 1550000.00 | 2327.00 | 11635000.00 | 1255000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
205.00 | Supply and application of high build epoxy paint over structural steel girders, trusses, etc., of total dry film thickness (DFT) of 275 microns consisting of following coats on already primed surfaces 1.Zinc rich primer coat of approved make of total DFT 50 micron. 2.Epoxy paint Epilux 89 or approved equivalent in multiple coats to a total minimum DFT of 250 micron. including preparation of surface as per manufacturers recommendations, tools & tackles, consumables, scaffolding and all required machinery, etc., at all elevations and locations as per construction drawings and specifications. | 500.00 | MT |  | 14781.00 | 7390500.00 | 29872.00 | 14936000.00 | 17059.00 | 8529500.00 | 10230.00 | 5115000.00 | 27093.00 | 13546500.00 | 23250.00 | 11625000.00 | 7428.00 | 3714000.00 | 3714000.00 | Ocean Lifespaces India Private Limited
206.00 | Supplying and fixing two layers of glass fiber dipped with epoxy paint of approved make and shade, filling up of the joint between liner and concrete face with epoxy sand mortar and application of 2 coat of epoxy paint with the total coating thickness of 250 micron including all tools and tackles, consumables, scaffolding etc., complete as per drawing and specification. | 100.00 | Sq. Meter |  | 647.00 | 64700.00 | 896.00 | 89600.00 | 7150.00 | 715000.00 | 4000.00 | 400000.00 | 661.00 | 66100.00 | 620.00 | 62000.00 | 833.00 | 83300.00 | 62000.00 | VRC Constructions (India) Limited
207.00 | Supply and application of fire proof paint of approved make and shade for fire rating not less than 45 minutes applied over the zinc silicate primed surface, body coat of water-based intumescent fire proof paint coating consisting of polyvinyl acetate resins and inorganic fillers designed for the fire protection of interior structural steel with coating thickness as recommended by manufacturer to meet the fire rating requirement and finishing coat of high performance urethane semi-glossy coating of DFT not less than 75micron, cleaning, including all tools and tackles, consumables, scaffolding etc., complete as per construction drawing and specification. | 2000.00 | Sq. Meter |  | 1470.00 | 2940000.00 | 3465.00 | 6930000.00 | 5242.00 | 10484000.00 | 3795.00 | 7590000.00 | 463.00 | 926000.00 | 775.00 | 1550000.00 | 3588.00 | 7176000.00 | 926000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
208.00 | Providing as per requirement Supply, transportation, temperature controlled storage and applying application of undercoat - Wash primer (polyvinyl butyral resin) - of 8-10 microns DFT followed by top coat of -aliphatic polyethylene - of 60 microns (in two coats) DFT over hot dip galvanized structural steel members after cleaning the surface by compressed air /cotton waste etc., including cost of all labour, machinery, scaffolding, compressor, air less spry gun, brushes etc., for the external structural Steel members at all elevations and locations as per specification and drawing. | 200.00 | MT |  | 17640.00 | 3528000.00 | 21508.00 | 4301600.00 | 7722.00 | 1544400.00 | 14000.00 | 2800000.00 | 29075.00 | 5815000.00 | 31000.00 | 6200000.00 | 2706.00 | 541200.00 | 541200.00 | Ocean Lifespaces India Private Limited
209.00 | Providing and fixing "HILTI" make or approved equivalent anchor fasteners of various sizes and diameter as mentioned below in concrete elements / Structural steel works at all elevations and locations as per NPCIL requirement and specification with necessary tools and tackles including drilling /cutting, providing scaffolding and working platforms etc. complete.
210.00 | HST3 type
211.00 | Size M8 | 300.00 | Each |  | 191.00 | 57300.00 | 332.00 | 99600.00 | 405.00 | 121500.00 | 260.00 | 78000.00 | 192.00 | 57600.00 | 232.50 | 69750.00 | 818.00 | 245400.00 | 57300.00 | JATAN CONSTRUCTIONS PVT LTD
212.00 | Size M10 | 500.00 | Each |  | 243.00 | 121500.00 | 465.00 | 232500.00 | 405.00 | 202500.00 | 360.00 | 180000.00 | 243.00 | 121500.00 | 387.50 | 193750.00 | 880.00 | 440000.00 | 121500.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED, JATAN CONSTRUCTIONS PVT LTD
213.00 | Size M12 | 300.00 | Each |  | 390.00 | 117000.00 | 863.00 | 258900.00 | 551.00 | 165300.00 | 440.00 | 132000.00 | 332.00 | 99600.00 | 542.50 | 162750.00 | 908.00 | 272400.00 | 99600.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
214.00 | Size M16 | 100.00 | Each |  | 757.00 | 75700.00 | 1195.00 | 119500.00 | 914.00 | 91400.00 | 1050.00 | 105000.00 | 788.00 | 78800.00 | 1085.00 | 108500.00 | 923.00 | 92300.00 | 75700.00 | JATAN CONSTRUCTIONS PVT LTD
215.00 | Size M20 | 100.00 | Each |  | 1404.00 | 140400.00 | 1859.00 | 185900.00 | 1538.00 | 153800.00 | 1830.00 | 183000.00 | 1373.00 | 137300.00 | 1550.00 | 155000.00 | 1989.00 | 198900.00 | 137300.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
216.00 | HSL 4G type
217.00 | Size M8 | 200.00 | Each |  | 537.00 | 107400.00 | 1195.00 | 239000.00 | 915.00 | 183000.00 | 1010.00 | 202000.00 | 850.00 | 170000.00 | 852.50 | 170500.00 | 1624.00 | 324800.00 | 107400.00 | JATAN CONSTRUCTIONS PVT LTD
218.00 | Size M10 | 500.00 | Each |  | 845.00 | 422500.00 | 1460.00 | 730000.00 | 895.00 | 447500.00 | 1310.00 | 655000.00 | 912.00 | 456000.00 | 1085.00 | 542500.00 | 1837.00 | 918500.00 | 422500.00 | JATAN CONSTRUCTIONS PVT LTD
219.00 | Size M12 | 200.00 | Each |  | 1227.00 | 245400.00 | 1991.00 | 398200.00 | 1488.00 | 297600.00 | 1450.00 | 290000.00 | 1213.00 | 242600.00 | 1395.00 | 279000.00 | 1936.00 | 387200.00 | 242600.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
220.00 | Size M16 | 100.00 | Each |  | 2536.00 | 253600.00 | 2390.00 | 239000.00 | 2623.00 | 262300.00 | 3240.00 | 324000.00 | 2716.00 | 271600.00 | 2480.00 | 248000.00 | 3355.00 | 335500.00 | 239000.00 | P AND C PROJECTS PRIVATE LIMITED
221.00 | Size M20 | 100.00 | Each |  | 4785.00 | 478500.00 | 2257.00 | 225700.00 | 4069.00 | 406900.00 | 5450.00 | 545000.00 | 4563.00 | 456300.00 | 4185.00 | 418500.00 | 4935.00 | 493500.00 | 225700.00 | P AND C PROJECTS PRIVATE LIMITED
222.00 | HDA-T type
223.00 | Size M10 | 100.00 | Each |  | 5880.00 | 588000.00 | 6638.00 | 663800.00 | 5146.00 | 514600.00 | 9020.00 | 902000.00 | 7582.00 | 758200.00 | 6200.00 | 620000.00 | 8804.00 | 880400.00 | 514600.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
224.00 | Size M12 | 100.00 | Each |  | 7791.00 | 779100.00 | 8099.00 | 809900.00 | 7099.00 | 709900.00 | 12030.00 | 1203000.00 | 10118.00 | 1011800.00 | 8525.00 | 852500.00 | 11489.00 | 1148900.00 | 709900.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
225.00 | Size M16 | 100.00 | Each |  | 13862.00 | 1386200.00 | 9957.00 | 995700.00 | 12534.00 | 1253400.00 | 22370.00 | 2237000.00 | 18821.00 | 1882100.00 | 15500.00 | 1550000.00 | 19716.00 | 1971600.00 | 995700.00 | P AND C PROJECTS PRIVATE LIMITED
226.00 | HUS Screw anchor 6x60 | 4000.00 | Each |  | 59.00 | 236000.00 | 199.00 | 796000.00 | 67.00 | 268000.00 | 60.00 | 240000.00 | 862.00 | 3448000.00 | 170.50 | 682000.00 | 346.00 | 1384000.00 | 236000.00 | JATAN CONSTRUCTIONS PVT LTD
227.00 | Carrying out Machining by suitable means to required surface of specified embedment parts in true line and level as per the tolerance specified in the drawing / work procedure and protecting the EP during concrete placement and applying suitable peel off coat after post concrete for protection etc., at all levels and locations complete. | 100.00 | Sq. Meter |  | 750.00 | 75000.00 | 438.00 | 43800.00 | 7800.00 | 780000.00 | 3000.00 | 300000.00 | 661.00 | 66100.00 | 3100.00 | 310000.00 | 384.00 | 38400.00 | 38400.00 | Ocean Lifespaces India Private Limited
228.00 | Non-destructive inspection of weld joints: Development of procedure & technique sheets for RT, UT, DPT, MPT, KLT, identification of weld joints, cleaning, providing and cutting the films to the required dimensions, providing and shifting of radiographic cameras, films, UT machine, equipment and its accessories, etc., to location, placing the joint identification markings on the film cassette, carrying out radiographic examination of the weld joint, cleaning of weld joints, flush grinding, application of coupling agent and carrying out ultra-sonic examination on pipe and plate weld joints, application of cleaning agent, penetron and developer for carrying out DPT examination as per applicable codes and standards, drawings and technical specifications for following items. This work also includes processing the films, providing consumables, coupling agent for UT, interpretation of results, preparation of reports and submission for acceptance, radiography cameras, radiographic sources, establishing storage facilities for RT sources as per applicable guide lines, dark room facility, RT film storage racks, ISNT/ ASNT level-II qualified personnel, tools & tackles, preparation of reports and submission for acceptance. Carrying out NDT tests for the welded joints of structural steel and EP works as per the drawing and approved QAP at fabrication shop / at site all levels, locations including all consumables, equipment with calibration, scaffolding, platforms, preparation and submission of report etc., complete.
229.00 | Dye Penetrate Test (DPT) | 500.00 | RM |  | 128.00 | 64000.00 | 2655.00 | 1327500.00 | 390.00 | 195000.00 | 2000.00 | 1000000.00 | 364.00 | 182000.00 | 4650.00 | 2325000.00 | 641.00 | 320500.00 | 64000.00 | JATAN CONSTRUCTIONS PVT LTD
230.00 | Radiographic Test (RT) on weld joints | 100.00 | RM |  | 750.00 | 75000.00 | 3319.00 | 331900.00 | 1950.00 | 195000.00 | 7000.00 | 700000.00 | 3229.00 | 322900.00 | 6200.00 | 620000.00 | 2403.00 | 240300.00 | 75000.00 | JATAN CONSTRUCTIONS PVT LTD
231.00 | Ultrasonic Test (UT) | 100.00 | RM |  | 128.00 | 12800.00 | 6638.00 | 663800.00 | 1300.00 | 130000.00 | 2000.00 | 200000.00 | 5795.00 | 579500.00 | 6200.00 | 620000.00 | 353.00 | 35300.00 | 12800.00 | JATAN CONSTRUCTIONS PVT LTD
232.00 | Kerosene testing for weld joints of various configurations other than pipe joints (KLT) | 500.00 | RM |  | 128.00 | 64000.00 | 119.00 | 59500.00 | 455.00 | 227500.00 | 2000.00 | 1000000.00 | 396.00 | 198000.00 | 3100.00 | 1550000.00 | 641.00 | 320500.00 | 59500.00 | P AND C PROJECTS PRIVATE LIMITED
233.00 | ALUMINIUM WORK
234.00 | Supply and fixing aluminium doors, hinged /sliding windows, ventilators, louvers (fixed & adjustable) and partitions with extruded built up standard tubular and other sections of JINDAL / INDAL / HINDALCO or approved equivalent, fixed with raw plugs and screws or with fixing clips or with anchor fasteners, filling up of gap at junctions, top, bottom and sides with PVC/neoprene felt, mitered and jointed mechanically wherever required, sections are prepared to receive the glass or particle board/FRP shutter of specified thickness, aluminium snap beading, CP brass/stainless steel screws, including supply and fixing all powder coated fixtures and fittings all complete as per drawing and specifications.
235.00 | Using 50 micron powder coated sections of specified colour. | 15000.00 | Kg |  | 750.00 | 11250000.00 | 627.00 | 9405000.00 | 621.00 | 9315000.00 | 630.00 | 9450000.00 | 694.00 | 10410000.00 | 852.50 | 12787500.00 | 802.00 | 12030000.00 | 9315000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
236.00 | Using anodized aluminium sections with sulphuric anodizing not less than 8 micron / hard anodizing not less than 60 micron of specified colour. | 5000.00 | Kg |  | 823.00 | 4115000.00 | 639.00 | 3195000.00 | 662.00 | 3310000.00 | 700.00 | 3500000.00 | 859.00 | 4295000.00 | 806.00 | 4030000.00 | 1071.00 | 5355000.00 | 3195000.00 | P AND C PROJECTS PRIVATE LIMITED
237.00 | Supply and fixing semi unitized structural glazing fixed /openable (glazing visible from exterior surface) using heat strengthened reflective type 2 Hr fire rating glass of SAINT GOBAIN / AIS / MODI make or approved equivalent with frame work using extruded anodized aluminium section (20 micron) JINDAL / INDAL / HINDALCO or approved equivalent making necessary opening arrangement, fixing the aluminium grid work in to the masonry / RCC with fixing SS brackets or clips or anchor fasteners, including fixtures required for fixing glass such as double side adhesive tape, silicon sealant, weather strip, weather sealant etc. at all elevations with necessary scaffolding arrangements etc., all as per drawing and specification. Note: 1.The rate is inclusive of design, preparation of supporting drawings, all material, labour, and scaffolding etc., the measurement shall be paid as per the finished area. 2.The aluminium grid work for structural glazing shall be designed for wind pressure 200kg/m2, seismic loads as per relevant code of practices. 3.Weight of aluminium grid work shall not be less than 7.5kg/m2 with arrangements for arresting rain water ingress.
238.00 | Aluminium structural glazing with 5.5 mm to 6.3 mm thick heat strengthened toughened transparent / reflective type glass 2 hr fire rating. | 2000.00 | Sq. Meter |  | 17273.00 | 34546000.00 | 20313.00 | 40626000.00 | 4253.00 | 8506000.00 | 5500.00 | 11000000.00 | 13877.00 | 27754000.00 | 11780.00 | 23560000.00 | 23300.00 | 46600000.00 | 8506000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
239.00 | Supply and fixing tray type aluminium composite panel cladding, using Alucomat / Alucobond / Durabuild or approved equivalent of approved colour with standard section of 4 mm thick aluminium composite panel cladding consisting two skins of 0.5 mm thick aluminium and 3 mm sandwich polyethylene core, PVDF coating with protective film on front side, mill finish on rear side as per manufacturer's specification including preparation and submission of shop drawings, soppy of all materials, consumables, frame work made up of extruded anodized aluminium sections and structural steel with two coats of approved quality synthetic enamel paint over a coat of primer, scaffolding, application of sealant etc., complete at all elevations as per drawing and specification. | 1500.00 | Sq. Meter |  | 4704.00 | 7056000.00 | 4182.00 | 6273000.00 | 4556.00 | 6834000.00 | 6000.00 | 9000000.00 | 3304.00 | 4956000.00 | 6200.00 | 9300000.00 | 6408.00 | 9612000.00 | 4956000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
240.00 | Supply and fixing frosted/clear/float glass 4 to 6.3 mm thick glazed heat strengthened, having 2 hr fire rating, SAINT GOBAIN / AIS / MODI make or approved equivalent for aluminium windows and ventilator shutters fixed glazing, with PVC / neoprene gasket, aluminium snap beading etc., complete as per drawings and specifications. Note: The aluminium snap beadings shall be paid under aluminium item. | 3200.00 | Sq. Meter |  | 6064.00 | 19404800.00 | 4302.00 | 13766400.00 | 608.00 | 1945600.00 | 1580.00 | 5056000.00 | 17181.00 | 54979200.00 | 3100.00 | 9920000.00 | 20970.00 | 67104000.00 | 1945600.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
241.00 | Supply and fixing 35 mm FRP shutter or 12 mm thick Pre-laminated particle board with veneer finish, both sides decorative lamination, flat pressed 3 layer & graded (medium density) Grade I, Type II conforming to IS : 12823 (exterior grade), 2 hr fire rating or as per specified requirement in drawings, premium quality of approved equivalent for aluminium windows and ventilator shutters fixed glazing, with PVC/neoprene gasket, aluminium snap beading etc., complete as per drawings and specifications. Note: The aluminium snap beadings shall be paid under aluminium item. | 1200.00 | Sq. Meter |  | 6174.00 | 7408800.00 | 1135.00 | 1362000.00 | 3038.00 | 3645600.00 | 2230.00 | 2676000.00 | 991.00 | 1189200.00 | 3720.00 | 4464000.00 | 8155.00 | 9786000.00 | 1189200.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
242.00 | Supply and fixing sun control polyester film of Modi /Garware / 3M make or approved equivalent for the glazed surfaces. | 2000.00 | Sq. Meter |  | 889.00 | 1778000.00 | 777.00 | 1554000.00 | 654.00 | 1308000.00 | 1000.00 | 2000000.00 | 859.00 | 1718000.00 | 2325.00 | 4650000.00 | 291.00 | 582000.00 | 582000.00 | Ocean Lifespaces India Private Limited
243.00 | Supply and fixing 5.5 to 6.3 mm thick plain glazing, Modi guard/Saint Gobain make toughened glass 2 hr fire rating for doors, windows and ventilator shutters fixed glazing, with PVC/neoprene gasket, snap beading etc. all complete as per drawings and specifications (Cost of snap beadings will be paid in relevant item). | 1500.00 | Sq. Meter |  | 5917.00 | 8875500.00 | 1314.00 | 1971000.00 | 878.00 | 1317000.00 | 2000.00 | 3000000.00 | 1520.00 | 2280000.00 | 3720.00 | 5580000.00 | 20970.00 | 31455000.00 | 1317000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
244.00 | SANITARY AND PIPING WORK
245.00 | Rain Water Downcomers
246.00 | Supply fixing and testing UPVC rain water pipes of below specified diameter as per IS-13592 Type A of "Prince/ Jain/ Kitec/ Finolex/Supreme" make with necessary fittings and fixtures, such as bottom shoe, MS grating, GI clamps, screws/nails, wooden packing pieces at minimum 1m spacing, cost inclusive of fixing the shoes in brick masonry in CM 1:6 and plastering the same with CM 1:4 etc., complete all as per drawings and specifications. Note: Payment for MS grating will be done under relevant item.
247.00 | 110-120 mm diameter | 2500.00 | RM |  | 571.00 | 1427500.00 | 430.00 | 1075000.00 | 896.00 | 2240000.00 | 900.00 | 2250000.00 | 727.00 | 1817500.00 | 620.00 | 1550000.00 | 1117.00 | 2792500.00 | 1075000.00 | P AND C PROJECTS PRIVATE LIMITED
248.00 | 160-170 mm diameter | 3000.00 | RM |  | 795.00 | 2385000.00 | 633.00 | 1899000.00 | 1199.00 | 3597000.00 | 1100.00 | 3300000.00 | 991.00 | 2973000.00 | 1007.50 | 3022500.00 | 1709.00 | 5127000.00 | 1899000.00 | P AND C PROJECTS PRIVATE LIMITED
249.00 | Supply and fixing approved cast iron manhole/catch pit/inspection pit covers of grade designation LD/MD/HD conforming to IS 1726 of various shapes and sizes with frames including lifting arrangement, fixing the frame to the manhole/catch pit/inspection pit with cement concrete, finishing smooth etc., complete. Note: The form work, reinforcement and concrete for fixing the frame shall be measured under relevant B.O.Q items. | 10000.00 | Kg |  | 198.00 | 1980000.00 | 115.00 | 1150000.00 | 145.00 | 1450000.00 | 150.00 | 1500000.00 | 150.00 | 1500000.00 | 139.50 | 1395000.00 | 254.00 | 2540000.00 | 1150000.00 | P AND C PROJECTS PRIVATE LIMITED
250.00 | Supply and fixing in position approved European/Universal type water closet of "Hindware/Cera/Nycer/Parryware" or approved equivalent comprising of a) Wash down EWC in white glazed vitreous chinaware with integral "P" of "S" trap with or without vent and jointing the trap with soil pipe in CM 1:1 b) Hindware/Cera/Nycer/Parryware make PVC 10 litters capacity low level flushing cistern with all symphonic fittings. c) White solid plastic seat cover with CP pillar hinges and rubber buffers etc., complete as per drawing and specifications. | 200.00 | Each |  | 4484.00 | 896800.00 | 4290.00 | 858000.00 | 10530.00 | 2106000.00 | 7500.00 | 1500000.00 | 25745.00 | 5149000.00 | 12400.00 | 2480000.00 | 4315.00 | 863000.00 | 858000.00 | P AND C PROJECTS PRIVATE LIMITED
251.00 | Supply and fixing in position best quality vitreous chinaware hand wash basin of 550x400mm size, white colour, of "Hindware/Cera/Nycer/Parryware" or approved equivalent and fixing with rug bolt of approved size and make etc., complete as per drawing and specifications. | 150.00 | Each |  | 2214.00 | 332100.00 | 1301.00 | 195150.00 | 2025.00 | 303750.00 | 4000.00 | 600000.00 | 15733.00 | 2359950.00 | 7750.00 | 1162500.00 | 1766.00 | 264900.00 | 195150.00 | P AND C PROJECTS PRIVATE LIMITED
252.00 | Supply and fixing in position porcelain oval shape white colour counter sunk wash basin of "Hindware/Cera/Nycer/Parryware" or approved equivalent on Granite counter etc., complete as per drawing and specifications. (The other civil works items for counter base shall be measured under relevant B.O.Q items.) | 150.00 | Each |  | 2940.00 | 441000.00 | 2084.00 | 312600.00 | 5184.00 | 777600.00 | 6000.00 | 900000.00 | 10699.00 | 1604850.00 | 9300.00 | 1395000.00 | 2696.00 | 404400.00 | 312600.00 | P AND C PROJECTS PRIVATE LIMITED
253.00 | Supply and fixing heavy quality PTMT 32 mm nominal bore bottle trap, "Prayag" or approved equivalent of self-cleaning design for wash basin. | 150.00 | Each |  | 1542.00 | 231300.00 | 1287.00 | 193050.00 | 891.00 | 133650.00 | 2000.00 | 300000.00 | 818.00 | 122700.00 | 2325.00 | 348750.00 | 601.00 | 90150.00 | 90150.00 | Ocean Lifespaces India Private Limited
254.00 | Supply and fixing heavy quality CP brass bottle trap, guar/Crabtree/Kohler or approved equivalent of self-cleaning design for counter countersunk wash basin. | 150.00 | Each |  | 1985.00 | 297750.00 | 1325.00 | 198750.00 | 2025.00 | 303750.00 | 3000.00 | 450000.00 | 913.00 | 136950.00 | 3875.00 | 581250.00 | 2268.00 | 340200.00 | 136950.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
255.00 | Supply and fixing PTMT seemed waste coupling 32mm diameter half threaded for wash basin "Prayag" or approved equivalent with rubber plug ball chain with necessary check nut etc., complete as per drawing and specifications. | 300.00 | Each |  | 551.00 | 165300.00 | 414.00 | 124200.00 | 365.00 | 109500.00 | 350.00 | 105000.00 | 138.00 | 41400.00 | 387.50 | 116250.00 | 61.00 | 18300.00 | 18300.00 | Ocean Lifespaces India Private Limited
256.00 | Supply and fixing heavy quality PTMT waste coupling 38mm diameter for kitchen sink "Prayag" or approved equivalent approved make with or without overflow with rubber plug CP brass ball chain with necessary check nut etc., complete as per drawing and specifications. | 300.00 | Each |  | 287.00 | 86100.00 | 450.00 | 135000.00 | 486.00 | 145800.00 | 365.00 | 109500.00 | 220.00 | 66000.00 | 465.00 | 139500.00 | 104.00 | 31200.00 | 31200.00 | Ocean Lifespaces India Private Limited
257.00 | Supply and fixing heavy quality 32mm CP brass waste coupling for Wash basin ADSON/CERA/PARRYWARE or approved equivalent with or without overflow with rubber plug ball chain with necessary check nut etc., complete as per drawing and specifications. | 300.00 | Each |  | 485.00 | 145500.00 | 885.00 | 265500.00 | 324.00 | 97200.00 | 700.00 | 210000.00 | 220.00 | 66000.00 | 387.50 | 116250.00 | 287.00 | 86100.00 | 66000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
258.00 | Providing as per requirement and fixing heavy quality 38mm CP brass waste coupling for Kitchen sink PRINCE/SUPREME /ADSON/CERA or approved equivalent with or without overflow with rubber plug ball chain with necessary check nut etc., complete as per drawing and specifications. | 300.00 | Each |  | 720.00 | 216000.00 | 909.00 | 272700.00 | 405.00 | 121500.00 | 950.00 | 285000.00 | 283.00 | 84900.00 | 465.00 | 139500.00 | 602.00 | 180600.00 | 84900.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
259.00 | Supply and fixing of 600 mm x 20 mm CP brass towel rod of ADSON/PARRY WARE/CERA or approved equivalent with a pair of CP brass brackets and wall flanges fixed to wall with CP brass screws screwed on to wooden plugs embedded in wall etc., complete as per drawing and specifications. | 150.00 | Each |  | 1169.00 | 175350.00 | 1323.00 | 198450.00 | 2916.00 | 437400.00 | 1630.00 | 244500.00 | 535.00 | 80250.00 | 1240.00 | 186000.00 | 735.00 | 110250.00 | 80250.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
260.00 | Supply and fixing in position MIRROR of size 600mm x 450mm and above as per NPCIL approval, made of premium glass 6mm thick manufactured by "M/s Hindustan Pilkington / Modi Guard/Saint Gobain" or approved equivalent, factory silvered, with PVC backing 4mm thick, frame etc., complete as per drawings and specifications. | 200.00 | Each |  | 676.00 | 135200.00 | 1153.00 | 230600.00 | 1296.00 | 259200.00 | 1700.00 | 340000.00 | 6923.00 | 1384600.00 | 1550.00 | 310000.00 | 802.00 | 160400.00 | 135200.00 | JATAN CONSTRUCTIONS PVT LTD
261.00 | Supply and fixing white glazed vitreous china recess type toilet paper roll holder of size 200 x 100 mm with CP rod, "Parry ware /Cera/Adson" or approved equivalent including making necessary chases in wall for fixing and making good the same etc., complete as per drawings and specifications. | 150.00 | Each |  | 1323.00 | 198450.00 | 839.00 | 125850.00 | 1377.00 | 206550.00 | 1050.00 | 157500.00 | 818.00 | 122700.00 | 1550.00 | 232500.00 | 650.00 | 97500.00 | 97500.00 | Ocean Lifespaces India Private Limited
262.00 | Supply and fixing in position white vitreous china flat back lipped front urinal basin of size 430 x260 x 350 mm or as approved by NPCIL with integral flushing rim PARRYWARE/CERA/HINDWARE or approved equivalent, CI concealed brackets including CP brass spreader "PARRYWARE/CERA/HINDWARE or approved equivalent with complete fittings including painting of bracket etc., complete as per drawings and specifications. | 200.00 | Each |  | 2205.00 | 441000.00 | 1343.00 | 268600.00 | 4050.00 | 810000.00 | 3800.00 | 760000.00 | 9440.00 | 1888000.00 | 9300.00 | 1860000.00 | 1993.00 | 398600.00 | 268600.00 | P AND C PROJECTS PRIVATE LIMITED
263.00 | Supply and fixing approved type of hardware fittings and fixtures with all screws, nails and nuts bolts etc., complete as per drawing and specifications.
264.00 | Rack bolt screw for European WC cover. | 200.00 | Each |  | 44.00 | 8800.00 | 358.00 | 71600.00 | 972.00 | 194400.00 | 40.00 | 8000.00 | 283.00 | 56600.00 | 542.50 | 108500.00 | 188.00 | 37600.00 | 8000.00 | DEE VEE PROJECTS LIMITED
265.00 | PTMT float valve 25mm with PVC ball 150mm diameter and aluminium rod 250 mm long. | 200.00 | Each |  | 1911.00 | 382200.00 | 358.00 | 71600.00 | 810.00 | 162000.00 | 400.00 | 80000.00 | 818.00 | 163600.00 | 542.50 | 108500.00 | 565.00 | 113000.00 | 71600.00 | P AND C PROJECTS PRIVATE LIMITED
266.00 | Brass Lever for 25mm ball valve. | 200.00 | Each |  | 294.00 | 58800.00 | 577.00 | 115400.00 | 243.00 | 48600.00 | 690.00 | 138000.00 | 157.00 | 31400.00 | 310.00 | 62000.00 | 148.00 | 29600.00 | 29600.00 | Ocean Lifespaces India Private Limited
267.00 | Supply and fixing telescope pipe 32mm diameter approved quality PVC pipe for Cistern/Urinal. | 200.00 | Each |  | 750.00 | 150000.00 | 221.00 | 44200.00 | 57.00 | 11400.00 | 130.00 | 26000.00 | 378.00 | 75600.00 | 310.00 | 62000.00 | 48.00 | 9600.00 | 9600.00 | Ocean Lifespaces India Private Limited
268.00 | Supply and fixing polyethylene - aluminium polyethylene (PE-AL-PE) composite pressure pipe, UV stabilized, with carbon black, confirming to IS:15450-2004 for water supply including supply and fixing box clamps at 1000mm spacing for external works and laying under floor wherever required, cutting walls as required for concealed installation including cutting and making good the walls for internals and supply and fixing all the required specials/ fittings etc., wherever required at all elevations including cost of scaffolding/machinery etc., complete as per drawings and specifications. Note: 1.The Earthwork excavation will be paid under relevant item. 2. The length of pipes measured shall exclude the specials/ fittings. 3. The specials/ fittings shall be paid under relevant items.
269.00 | 12-16mm OD | 500.00 | RM |  | 160.00 | 80000.00 | 226.00 | 113000.00 | 146.00 | 73000.00 | 440.00 | 220000.00 | 165.00 | 82500.00 | 263.50 | 131750.00 | 115.00 | 57500.00 | 57500.00 | Ocean Lifespaces India Private Limited
270.00 | 17-20mm OD | 250.00 | RM |  | 196.00 | 49000.00 | 274.00 | 68500.00 | 190.00 | 47500.00 | 500.00 | 125000.00 | 205.00 | 51250.00 | 341.00 | 85250.00 | 143.00 | 35750.00 | 35750.00 | Ocean Lifespaces India Private Limited
271.00 | 21-25mm OD | 250.00 | RM |  | 257.00 | 64250.00 | 348.00 | 87000.00 | 253.00 | 63250.00 | 600.00 | 150000.00 | 231.00 | 57750.00 | 449.50 | 112375.00 | 192.00 | 48000.00 | 48000.00 | Ocean Lifespaces India Private Limited
272.00 | 26-32mm OD | 200.00 | RM |  | 355.00 | 71000.00 | 502.00 | 100400.00 | 390.00 | 78000.00 | 820.00 | 164000.00 | 262.00 | 52400.00 | 682.00 | 136400.00 | 297.00 | 59400.00 | 52400.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
273.00 | 33-40mm OD | 200.00 | RM |  | 485.00 | 97000.00 | 656.00 | 131200.00 | 532.00 | 106400.00 | 1020.00 | 204000.00 | 284.00 | 56800.00 | 930.00 | 186000.00 | 405.00 | 81000.00 | 56800.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
274.00 | 41-50mm OD | 200.00 | RM |  | 603.00 | 120600.00 | 958.00 | 191600.00 | 800.00 | 160000.00 | 1400.00 | 280000.00 | 312.00 | 62400.00 | 1395.00 | 279000.00 | 609.00 | 121800.00 | 62400.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
275.00 | Supply and fixing 15 mm size heavy quality CP brass pillar cock easy clean type as per relevant IS for wash basin with capstan head "ADSON/CERA/ PARRYWARE or approved equivalent etc., complete as per drawings and specifications. | 200.00 | Each |  | 1661.00 | 332200.00 | 739.00 | 147800.00 | 1754.00 | 350800.00 | 1740.00 | 348000.00 | 1520.00 | 304000.00 | 2325.00 | 465000.00 | 1153.00 | 230600.00 | 147800.00 | P AND C PROJECTS PRIVATE LIMITED
276.00 | Supply and fixing heavy quality 15mm diameter CP brass angle cock as per relevant IS, "ADSON/CERA/PARRYWARE "or approved equivalent etc., complete as per drawings and specifications. | 200.00 | Each |  | 786.00 | 157200.00 | 536.00 | 107200.00 | 718.00 | 143600.00 | 1300.00 | 260000.00 | 463.00 | 92600.00 | 1550.00 | 310000.00 | 626.00 | 125200.00 | 92600.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
277.00 | Supply and fixing heavy quality 15 mm diameter, CP brass screw down long bodied bib tap with CP brass flanges as per relevant IS, "ADSON/CERA/ PARRYWARE "or approved equivalent etc., complete as per drawings and specifications. | 200.00 | Each |  | 1404.00 | 280800.00 | 1151.00 | 230200.00 | 1082.00 | 216400.00 | 1520.00 | 304000.00 | 1652.00 | 330400.00 | 1550.00 | 310000.00 | 1269.00 | 253800.00 | 216400.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
278.00 | Supply and fixing 15mm diameter CP brass screw down stop COCK concealed type with female ends as per relevant IS code, "Parry ware / Cera / Adson" or approved equivalent etc., complete as per drawings and specifications. | 200.00 | Each |  | 1544.00 | 308800.00 | 576.00 | 115200.00 | 1225.00 | 245000.00 | 1860.00 | 372000.00 | 859.00 | 171800.00 | 1240.00 | 248000.00 | 1168.00 | 233600.00 | 115200.00 | P AND C PROJECTS PRIVATE LIMITED
279.00 | Supply and fixing PTMT - Symet shower rose 15 mm x 50 mm easy clean type with ball and socket arrangement, "Prayag" or approved equivalent with PTMT - Symet shower arm of 300 mm length with flange etc., complete as per drawings and specifications. | 150.00 | Each |  | 1529.00 | 229350.00 | 433.00 | 64950.00 | 10044.00 | 1506600.00 | 490.00 | 73500.00 | 1123.00 | 168450.00 | 1240.00 | 186000.00 | 641.00 | 96150.00 | 64950.00 | P AND C PROJECTS PRIVATE LIMITED
280.00 | Supply and fixing C.P. brass three pronged robe hooks of "Parry ware /Cera/Adson" or approved equivalent with C.P. brass flange as directed by ENGINEER. | 100.00 | Each |  | 867.00 | 86700.00 | 603.00 | 60300.00 | 1361.00 | 136100.00 | 1660.00 | 166000.00 | 859.00 | 85900.00 | 930.00 | 93000.00 | 299.00 | 29900.00 | 29900.00 | Ocean Lifespaces India Private Limited
281.00 | Supply and fixing of 15 mm, 1m length health faucet of JAQUAR/CRABTREE/KOHLER or approved equivalent and with all necessary accessories etc., complete as per drawings and specifications. | 150.00 | Each |  | 2058.00 | 308700.00 | 845.00 | 126750.00 | 1701.00 | 255150.00 | 1320.00 | 198000.00 | 1520.00 | 228000.00 | 2325.00 | 348750.00 | 2603.00 | 390450.00 | 126750.00 | P AND C PROJECTS PRIVATE LIMITED
282.00 | Supply and fixing heavy quality 15 mm diameter PTMT long bodied bib tap as per relevant IS of "Prayag" or approved equivalent make including check nut and flange etc., complete as per drawings and specifications. | 100.00 | Each |  | 1191.00 | 119100.00 | 1151.00 | 115100.00 | 664.00 | 66400.00 | 390.00 | 39000.00 | 1256.00 | 125600.00 | 775.00 | 77500.00 | 426.00 | 42600.00 | 39000.00 | DEE VEE PROJECTS LIMITED
283.00 | Supply and fixing of 15 mm CP brass spindle for Taps, pillar cock, angle cock, stop cock, concealed stop cock etc., of JALAJ/ADSON/PARRYWARE/CERA or approved equivalent with all necessary accessories etc., complete as per drawing and specifications. | 100.00 | Each |  | 1507.00 | 150700.00 | 992.00 | 99200.00 | 405.00 | 40500.00 | 700.00 | 70000.00 | 264.00 | 26400.00 | 465.00 | 46500.00 | 148.00 | 14800.00 | 14800.00 | Ocean Lifespaces India Private Limited
284.00 | Supply and fixing isolating composite brass ball valve "Akar/Zolato/Leader" or approved equivalent with compression type integral seal end connection suitable for PE-AL-PE composite piping system as per IS-15450, suitable for hot and cold water Providing as per requirement etc., complete as per drawings and specifications
285.00 | 50mm diameter | 50.00 | Each |  | 10149.00 | 507450.00 | 1796.00 | 89800.00 | 6983.00 | 349150.00 | 4910.00 | 245500.00 | 1652.00 | 82600.00 | 13950.00 | 697500.00 | 10166.00 | 508300.00 | 82600.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
286.00 | 40mm diameter | 100.00 | Each |  | 5442.00 | 544200.00 | 1723.00 | 172300.00 | 4767.00 | 476700.00 | 3480.00 | 348000.00 | 1520.00 | 152000.00 | 7750.00 | 775000.00 | 5201.00 | 520100.00 | 152000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
287.00 | 32mm diameter | 50.00 | Each |  | 3713.00 | 185650.00 | 1661.00 | 83050.00 | 3528.00 | 176400.00 | 2410.00 | 120500.00 | 1256.00 | 62800.00 | 5425.00 | 271250.00 | 3429.00 | 171450.00 | 62800.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
288.00 | 25mm diameter | 50.00 | Each |  | 2234.00 | 111700.00 | 1577.00 | 78850.00 | 2519.00 | 125950.00 | 1500.00 | 75000.00 | 991.00 | 49550.00 | 3720.00 | 186000.00 | 2050.00 | 102500.00 | 49550.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
289.00 | 20mm diameter | 50.00 | Each |  | 1474.00 | 73700.00 | 1518.00 | 75900.00 | 2426.00 | 121300.00 | 950.00 | 47500.00 | 813.00 | 40650.00 | 3100.00 | 155000.00 | 1186.00 | 59300.00 | 40650.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
290.00 | 16mm diameter | 50.00 | Each |  | 1073.00 | 53650.00 | 1350.00 | 67500.00 | 1199.00 | 59950.00 | 715.00 | 35750.00 | 694.00 | 34700.00 | 2325.00 | 116250.00 | 796.00 | 39800.00 | 34700.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
291.00 | 12mm diameter | 50.00 | Each |  | 1001.00 | 50050.00 | 1111.00 | 55550.00 | 1030.00 | 51500.00 | 700.00 | 35000.00 | 628.00 | 31400.00 | 1860.00 | 93000.00 | 758.00 | 37900.00 | 31400.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
292.00 | Supply and fixing gun metal, full way gate valve, female ends screwed bonnet integral seat, non-rising spindle, class I, marked to IS : 778 tested to 20 kg/cm2 hydraulic pressure, "LEADER/ZOLATO" or approved equivalent etc., complete as per drawing and specifications.
293.00 | 50mm diameter | 100.00 | Each |  | 6447.00 | 644700.00 | 1941.00 | 194100.00 | 3240.00 | 324000.00 | 7100.00 | 710000.00 | 1652.00 | 165200.00 | 4030.00 | 403000.00 | 4806.00 | 480600.00 | 165200.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
294.00 | 40mm diameter | 100.00 | Each |  | 4557.00 | 455700.00 | 1886.00 | 188600.00 | 2989.00 | 298900.00 | 4860.00 | 486000.00 | 1520.00 | 152000.00 | 3410.00 | 341000.00 | 3832.00 | 383200.00 | 152000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
295.00 | 32mm diameter | 100.00 | Each |  | 3437.00 | 343700.00 | 1797.00 | 179700.00 | 2377.00 | 237700.00 | 3450.00 | 345000.00 | 1256.00 | 125600.00 | 3100.00 | 310000.00 | 2924.00 | 292400.00 | 125600.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
296.00 | 25mm diameter | 150.00 | Each |  | 2496.00 | 374400.00 | 1636.00 | 245400.00 | 1920.00 | 288000.00 | 2530.00 | 379500.00 | 991.00 | 148650.00 | 2325.00 | 348750.00 | 1250.00 | 187500.00 | 148650.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
297.00 | 20mm diameter | 100.00 | Each |  | 2167.00 | 216700.00 | 1596.00 | 159600.00 | 1024.00 | 102400.00 | 1860.00 | 186000.00 | 813.00 | 81300.00 | 1782.50 | 178250.00 | 702.00 | 70200.00 | 70200.00 | Ocean Lifespaces India Private Limited
298.00 | 16mm diameter | 100.00 | Each |  | 1937.00 | 193700.00 | 1504.00 | 150400.00 | 987.00 | 98700.00 | 1350.00 | 135000.00 | 694.00 | 69400.00 | 1240.00 | 124000.00 | 650.00 | 65000.00 | 65000.00 | Ocean Lifespaces India Private Limited
299.00 | 12mm diameter | 100.00 | Each |  | 1788.00 | 178800.00 | 1504.00 | 150400.00 | 893.00 | 89300.00 | 1230.00 | 123000.00 | 628.00 | 62800.00 | 930.00 | 93000.00 | 529.00 | 52900.00 | 52900.00 | Ocean Lifespaces India Private Limited
300.00 | Supply and fixing 50mm diameter PP ball valve of approved make with all fixing accessories etc., all conforming to relevant IS etc., complete as per drawing and specifications. | 25.00 | Each |  | 5130.00 | 128250.00 | 1516.00 | 37900.00 | 664.00 | 16600.00 | 7000.00 | 175000.00 | 859.00 | 21475.00 | 1860.00 | 46500.00 | 1827.00 | 45675.00 | 16600.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
301.00 | Supply, laying/fixing in position approved PVC pipes "Jain/ Finolex/Supreme/Prince" make or approved equivalent with required specials and fixing arrangements for water supply including fixing it with approved quality nails clamps and screws for fixing as per requirements etc., complete as per drawing and specifications. Note: Earthwork excavation will be paid under relevant item.
302.00 | PVC PIPES -- 20mm dia-10kg/cm2 | 500.00 | RM |  | 132.00 | 66000.00 | 129.00 | 64500.00 | 39.00 | 19500.00 | 280.00 | 140000.00 | 377.00 | 188500.00 | 279.00 | 139500.00 | 29.00 | 14500.00 | 14500.00 | Ocean Lifespaces India Private Limited
303.00 | PVC PIPES -- 25mm dia-10kg/cm2 | 500.00 | RM |  | 134.00 | 67000.00 | 137.00 | 68500.00 | 58.00 | 29000.00 | 370.00 | 185000.00 | 496.00 | 248000.00 | 341.00 | 170500.00 | 45.00 | 22500.00 | 22500.00 | Ocean Lifespaces India Private Limited
304.00 | PVC PIPES -- 32mm dia-10kg/cm2 | 500.00 | RM |  | 168.00 | 84000.00 | 188.00 | 94000.00 | 93.00 | 46500.00 | 540.00 | 270000.00 | 548.00 | 274000.00 | 434.00 | 217000.00 | 71.00 | 35500.00 | 35500.00 | Ocean Lifespaces India Private Limited
305.00 | PVC PIPES -- 40mm dia-10kg/cm2 | 200.00 | RM |  | 221.00 | 44200.00 | 206.00 | 41200.00 | 142.00 | 28400.00 | 750.00 | 150000.00 | 615.00 | 123000.00 | 558.00 | 111600.00 | 107.00 | 21400.00 | 21400.00 | Ocean Lifespaces India Private Limited
306.00 | PVC PIPES -- 50mm dia-10kg/cm2 | 100.00 | RM |  | 297.00 | 29700.00 | 235.00 | 23500.00 | 226.00 | 22600.00 | 1100.00 | 110000.00 | 708.00 | 70800.00 | 697.50 | 69750.00 | 171.00 | 17100.00 | 17100.00 | Ocean Lifespaces India Private Limited
307.00 | PVC PIPES -- 50mm dia-6kg/cm2 | 100.00 | RM |  | 296.00 | 29600.00 | 205.00 | 20500.00 | 139.00 | 13900.00 | 700.00 | 70000.00 | 760.00 | 76000.00 | 542.50 | 54250.00 | 106.00 | 10600.00 | 10600.00 | Ocean Lifespaces India Private Limited
308.00 | PVC PIPES -- 63mm dia-6kg/cm2 | 100.00 | RM |  | 363.00 | 36300.00 | 247.00 | 24700.00 | 216.00 | 21600.00 | 1100.00 | 110000.00 | 899.00 | 89900.00 | 697.50 | 69750.00 | 164.00 | 16400.00 | 16400.00 | Ocean Lifespaces India Private Limited
309.00 | PVC PIPES -- 75mm dia-6kg/cm2 | 200.00 | RM |  | 432.00 | 86400.00 | 282.00 | 56400.00 | 304.00 | 60800.00 | 1440.00 | 288000.00 | 1004.00 | 200800.00 | 868.00 | 173600.00 | 241.00 | 48200.00 | 48200.00 | Ocean Lifespaces India Private Limited
310.00 | PVC PIPES -- 110mm dia-6kg/cm2 | 100.00 | RM |  | 644.00 | 64400.00 | 416.00 | 41600.00 | 641.00 | 64100.00 | 2830.00 | 283000.00 | 1130.00 | 113000.00 | 1007.50 | 100750.00 | 485.00 | 48500.00 | 41600.00 | P AND C PROJECTS PRIVATE LIMITED
311.00 | PVC PIPES -- 160mm dia-6kg/cm2 | 100.00 | RM |  | 1072.00 | 107200.00 | 709.00 | 70900.00 | 1371.00 | 137100.00 | 5900.00 | 590000.00 | 2445.00 | 244500.00 | 1162.50 | 116250.00 | 1042.00 | 104200.00 | 70900.00 | P AND C PROJECTS PRIVATE LIMITED
312.00 | PVC PIPES -- 300mm dia-6kg/cm2 | 100.00 | RM |  | 3710.00 | 371000.00 | 2317.00 | 231700.00 | 5663.00 | 566300.00 | 17900.00 | 1790000.00 | 4626.00 | 462600.00 | 3100.00 | 310000.00 | 4307.00 | 430700.00 | 231700.00 | P AND C PROJECTS PRIVATE LIMITED
313.00 | Supply and fixing approved quality PE -AL- PE pipe specials of KITEC/VISTA make or approved equivalent as per IS 15450 including the cost of tools, tackles, labour etc., complete as per drawing and specifications.
314.00 | Equal Tee
315.00 | Equal Tee(1216) | 100.00 | Each |  | 150.00 | 15000.00 | 125.00 | 12500.00 | 205.00 | 20500.00 | 390.00 | 39000.00 | 385.00 | 38500.00 | 279.00 | 27900.00 | 156.00 | 15600.00 | 12500.00 | P AND C PROJECTS PRIVATE LIMITED
316.00 | Equal Tee(1620) | 100.00 | Each |  | 198.00 | 19800.00 | 161.00 | 16100.00 | 269.00 | 26900.00 | 510.00 | 51000.00 | 542.00 | 54200.00 | 356.50 | 35650.00 | 205.00 | 20500.00 | 16100.00 | P AND C PROJECTS PRIVATE LIMITED
317.00 | Equal Tee(2025) | 100.00 | Each |  | 323.00 | 32300.00 | 240.00 | 24000.00 | 411.00 | 41100.00 | 780.00 | 78000.00 | 938.00 | 93800.00 | 604.50 | 60450.00 | 312.00 | 31200.00 | 24000.00 | P AND C PROJECTS PRIVATE LIMITED
318.00 | Equal Tee(2532) | 100.00 | Each |  | 531.00 | 53100.00 | 284.00 | 28400.00 | 442.00 | 44200.00 | 840.00 | 84000.00 | 2282.00 | 228200.00 | 658.75 | 65875.00 | 337.00 | 33700.00 | 28400.00 | P AND C PROJECTS PRIVATE LIMITED
319.00 | Equal Tee(3240) | 100.00 | Each |  | 742.00 | 74200.00 | 437.00 | 43700.00 | 690.00 | 69000.00 | 1300.00 | 130000.00 | 3682.00 | 368200.00 | 961.00 | 96100.00 | 524.00 | 52400.00 | 43700.00 | P AND C PROJECTS PRIVATE LIMITED
320.00 | Equal Tee(4050) | 100.00 | Each |  | 1033.00 | 103300.00 | 1243.00 | 124300.00 | 1957.00 | 195700.00 | 3720.00 | 372000.00 | 6652.00 | 665200.00 | 1860.00 | 186000.00 | 1488.00 | 148800.00 | 103300.00 | JATAN CONSTRUCTIONS PVT LTD
321.00 | Reducing Tee
322.00 | Reducing Tee(1620x1216x1620) | 100.00 | Each |  | 182.00 | 18200.00 | 174.00 | 17400.00 | 256.00 | 25600.00 | 490.00 | 49000.00 | 468.00 | 46800.00 | 341.00 | 34100.00 | 196.00 | 19600.00 | 17400.00 | P AND C PROJECTS PRIVATE LIMITED
323.00 | Reducing Tee(1620x1620x1216) | 100.00 | Each |  | 175.00 | 17500.00 | 174.00 | 17400.00 | 256.00 | 25600.00 | 490.00 | 49000.00 | 501.00 | 50100.00 | 341.00 | 34100.00 | 196.00 | 19600.00 | 17400.00 | P AND C PROJECTS PRIVATE LIMITED
324.00 | Reducing Tee(1620x1216x1216) | 100.00 | Each |  | 163.00 | 16300.00 | 164.00 | 16400.00 | 242.00 | 24200.00 | 460.00 | 46000.00 | 517.00 | 51700.00 | 341.00 | 34100.00 | 186.00 | 18600.00 | 16300.00 | JATAN CONSTRUCTIONS PVT LTD
325.00 | Reducing Tee(2025x2025x1216) | 100.00 | Each |  | 275.00 | 27500.00 | 243.00 | 24300.00 | 358.00 | 35800.00 | 680.00 | 68000.00 | 862.00 | 86200.00 | 542.50 | 54250.00 | 273.00 | 27300.00 | 24300.00 | P AND C PROJECTS PRIVATE LIMITED
326.00 | Reducing Tee(2025x2025x1620) | 100.00 | Each |  | 337.00 | 33700.00 | 253.00 | 25300.00 | 374.00 | 37400.00 | 710.00 | 71000.00 | 872.00 | 87200.00 | 465.00 | 46500.00 | 284.00 | 28400.00 | 25300.00 | P AND C PROJECTS PRIVATE LIMITED
327.00 | Reducing Tee(2025x1620x1620) | 100.00 | Each |  | 244.00 | 24400.00 | 331.00 | 33100.00 | 323.00 | 32300.00 | 610.00 | 61000.00 | 764.00 | 76400.00 | 465.00 | 46500.00 | 246.00 | 24600.00 | 24400.00 | JATAN CONSTRUCTIONS PVT LTD
328.00 | Reducing Tee(2025x1620x1216) | 100.00 | Each |  | 229.00 | 22900.00 | 243.00 | 24300.00 | 305.00 | 30500.00 | 580.00 | 58000.00 | 859.00 | 85900.00 | 449.50 | 44950.00 | 233.00 | 23300.00 | 22900.00 | JATAN CONSTRUCTIONS PVT LTD
329.00 | Reducing Tee(2025x1216x2025) | 100.00 | Each |  | 271.00 | 27100.00 | 352.00 | 35200.00 | 356.00 | 35600.00 | 675.00 | 67500.00 | 546.00 | 54600.00 | 465.00 | 46500.00 | 270.00 | 27000.00 | 27000.00 | Ocean Lifespaces India Private Limited
330.00 | Reduced Tee (2532x2532x2025) | 100.00 | Each |  | 474.00 | 47400.00 | 334.00 | 33400.00 | 505.00 | 50500.00 | 980.00 | 98000.00 | 1883.00 | 188300.00 | 736.25 | 73625.00 | 384.00 | 38400.00 | 33400.00 | P AND C PROJECTS PRIVATE LIMITED
331.00 | Reduced Tee (2532x2532x1620) | 100.00 | Each |  | 427.00 | 42700.00 | 309.00 | 30900.00 | 479.00 | 47900.00 | 910.00 | 91000.00 | 1751.00 | 175100.00 | 736.25 | 73625.00 | 363.00 | 36300.00 | 30900.00 | P AND C PROJECTS PRIVATE LIMITED
332.00 | Reduced Tee (2532x2025x1620) | 100.00 | Each |  | 376.00 | 37600.00 | 355.00 | 35500.00 | 548.00 | 54800.00 | 1040.00 | 104000.00 | 2009.00 | 200900.00 | 790.50 | 79050.00 | 418.00 | 41800.00 | 35500.00 | P AND C PROJECTS PRIVATE LIMITED
333.00 | Reduced Tee (3240x3240x2532) | 100.00 | Each |  | 697.00 | 69700.00 | 456.00 | 45600.00 | 718.00 | 71800.00 | 1360.00 | 136000.00 | 3416.00 | 341600.00 | 930.00 | 93000.00 | 545.00 | 54500.00 | 45600.00 | P AND C PROJECTS PRIVATE LIMITED
334.00 | Reduced Tee (4050x4050x3240) | 100.00 | Each |  | 845.00 | 84500.00 | 1116.00 | 111600.00 | 1757.00 | 175700.00 | 3330.00 | 333000.00 | 4705.00 | 470500.00 | 1705.00 | 170500.00 | 1336.00 | 133600.00 | 84500.00 | JATAN CONSTRUCTIONS PVT LTD
335.00 | Reduced Tee (4050x4050x2532) | 100.00 | Each |  | 992.00 | 99200.00 | 894.00 | 89400.00 | 1690.00 | 169000.00 | 3210.00 | 321000.00 | 4414.00 | 441400.00 | 2170.00 | 217000.00 | 1285.00 | 128500.00 | 89400.00 | P AND C PROJECTS PRIVATE LIMITED
336.00 | Female Tee
337.00 | Female Tee(1216x1216x1/2") | 100.00 | Each |  | 168.00 | 16800.00 | 156.00 | 15600.00 | 232.00 | 23200.00 | 440.00 | 44000.00 | 519.00 | 51900.00 | 310.00 | 31000.00 | 176.00 | 17600.00 | 15600.00 | P AND C PROJECTS PRIVATE LIMITED
338.00 | Female Tee(1620x1620x1/2") | 100.00 | Each |  | 205.00 | 20500.00 | 177.00 | 17700.00 | 258.00 | 25800.00 | 500.00 | 50000.00 | 628.00 | 62800.00 | 387.50 | 38750.00 | 197.00 | 19700.00 | 17700.00 | P AND C PROJECTS PRIVATE LIMITED
339.00 | Female Tee(2025x2025x1/2") | 100.00 | Each |  | 295.00 | 29500.00 | 248.00 | 24800.00 | 363.00 | 36300.00 | 690.00 | 69000.00 | 760.00 | 76000.00 | 480.50 | 48050.00 | 277.00 | 27700.00 | 24800.00 | P AND C PROJECTS PRIVATE LIMITED
340.00 | Female Tee(2025x2025x1") | 100.00 | Each |  | 345.00 | 34500.00 | 248.00 | 24800.00 | 369.00 | 36900.00 | 700.00 | 70000.00 | 1176.00 | 117600.00 | 488.25 | 48825.00 | 281.00 | 28100.00 | 24800.00 | P AND C PROJECTS PRIVATE LIMITED
341.00 | Female Tee(2532x2532x1/2") | 100.00 | Each |  | 443.00 | 44300.00 | 260.00 | 26000.00 | 404.00 | 40400.00 | 770.00 | 77000.00 | 1626.00 | 162600.00 | 542.50 | 54250.00 | 308.00 | 30800.00 | 26000.00 | P AND C PROJECTS PRIVATE LIMITED
342.00 | Female Tee(2532x2532x1") | 100.00 | Each |  | 488.00 | 48800.00 | 253.00 | 25300.00 | 395.00 | 39500.00 | 750.00 | 75000.00 | 2181.00 | 218100.00 | 542.50 | 54250.00 | 302.00 | 30200.00 | 25300.00 | P AND C PROJECTS PRIVATE LIMITED
343.00 | Female Tee(2532x2532x1.25") | 100.00 | Each |  | 595.00 | 59500.00 | 251.00 | 25100.00 | 433.00 | 43300.00 | 820.00 | 82000.00 | 648.00 | 64800.00 | 697.50 | 69750.00 | 330.00 | 33000.00 | 25100.00 | P AND C PROJECTS PRIVATE LIMITED
344.00 | Female Tee(3240x3240x1.25") | 100.00 | Each |  | 662.00 | 66200.00 | 414.00 | 41400.00 | 653.00 | 65300.00 | 1340.00 | 134000.00 | 760.00 | 76000.00 | 930.00 | 93000.00 | 496.00 | 49600.00 | 41400.00 | P AND C PROJECTS PRIVATE LIMITED
345.00 | Equal Elbow
346.00 | Equal Elbow(1216) | 100.00 | Each |  | 109.00 | 10900.00 | 110.00 | 11000.00 | 191.00 | 19100.00 | 320.00 | 32000.00 | 303.00 | 30300.00 | 248.00 | 24800.00 | 146.00 | 14600.00 | 10900.00 | JATAN CONSTRUCTIONS PVT LTD
347.00 | Equal Elbow(1620) | 100.00 | Each |  | 144.00 | 14400.00 | 130.00 | 13000.00 | 193.00 | 19300.00 | 370.00 | 37000.00 | 378.00 | 37800.00 | 248.00 | 24800.00 | 148.00 | 14800.00 | 13000.00 | P AND C PROJECTS PRIVATE LIMITED
348.00 | Equal Elbow(2025) | 100.00 | Each |  | 226.00 | 22600.00 | 200.00 | 20000.00 | 256.00 | 25600.00 | 560.00 | 56000.00 | 794.00 | 79400.00 | 341.00 | 34100.00 | 195.00 | 19500.00 | 19500.00 | Ocean Lifespaces India Private Limited
349.00 | Equal Elbow(3240) | 100.00 | Each |  | 510.00 | 51000.00 | 268.00 | 26800.00 | 423.00 | 42300.00 | 810.00 | 81000.00 | 2557.00 | 255700.00 | 496.00 | 49600.00 | 322.00 | 32200.00 | 26800.00 | P AND C PROJECTS PRIVATE LIMITED
350.00 | Equal Elbow(4050) | 100.00 | Each |  | 772.00 | 77200.00 | 922.00 | 92200.00 | 1451.00 | 145100.00 | 2800.00 | 280000.00 | 4734.00 | 473400.00 | 1860.00 | 186000.00 | 1103.00 | 110300.00 | 77200.00 | JATAN CONSTRUCTIONS PVT LTD
351.00 | Reduced Elbow
352.00 | Reduced Elbow(2025x1216) | 100.00 | Each |  | 173.00 | 17300.00 | 158.00 | 15800.00 | 233.00 | 23300.00 | 450.00 | 45000.00 | 751.00 | 75100.00 | 387.50 | 38750.00 | 178.00 | 17800.00 | 15800.00 | P AND C PROJECTS PRIVATE LIMITED
353.00 | Reduced Elbow(2025x1620) | 100.00 | Each |  | 188.00 | 18800.00 | 168.00 | 16800.00 | 249.00 | 24900.00 | 480.00 | 48000.00 | 1356.00 | 135600.00 | 387.50 | 38750.00 | 190.00 | 19000.00 | 16800.00 | P AND C PROJECTS PRIVATE LIMITED
354.00 | Reduced Elbow (4050x3240) | 100.00 | Each |  | 639.00 | 63900.00 | 754.00 | 75400.00 | 1186.00 | 118600.00 | 2260.00 | 226000.00 | 2313.00 | 231300.00 | 1317.50 | 131750.00 | 904.00 | 90400.00 | 63900.00 | JATAN CONSTRUCTIONS PVT LTD
355.00 | Male Connector
356.00 | Male Connector(1216x1/2") | 100.00 | Each |  | 138.00 | 13800.00 | 55.00 | 5500.00 | 81.00 | 8100.00 | 155.00 | 15500.00 | 182.00 | 18200.00 | 155.00 | 15500.00 | 62.00 | 6200.00 | 5500.00 | P AND C PROJECTS PRIVATE LIMITED
357.00 | Male Connector(1620x1/2") | 100.00 | Each |  | 156.00 | 15600.00 | 68.00 | 6800.00 | 168.00 | 16800.00 | 190.00 | 19000.00 | 252.00 | 25200.00 | 232.50 | 23250.00 | 128.00 | 12800.00 | 6800.00 | P AND C PROJECTS PRIVATE LIMITED
358.00 | Male Connector(1620x3/4") | 100.00 | Each |  | 199.00 | 19900.00 | 70.00 | 7000.00 | 105.00 | 10500.00 | 200.00 | 20000.00 | 268.00 | 26800.00 | 155.00 | 15500.00 | 79.00 | 7900.00 | 7000.00 | P AND C PROJECTS PRIVATE LIMITED
359.00 | Male Connector(2025x3/4") | 100.00 | Each |  | 242.00 | 24200.00 | 106.00 | 10600.00 | 158.00 | 15800.00 | 300.00 | 30000.00 | 1044.00 | 104400.00 | 232.50 | 23250.00 | 120.00 | 12000.00 | 10600.00 | P AND C PROJECTS PRIVATE LIMITED
360.00 | Male Connector(2025x1") | 100.00 | Each |  | 295.00 | 29500.00 | 104.00 | 10400.00 | 153.00 | 15300.00 | 290.00 | 29000.00 | 432.00 | 43200.00 | 232.50 | 23250.00 | 117.00 | 11700.00 | 10400.00 | P AND C PROJECTS PRIVATE LIMITED
361.00 | Male Connector(2532x1") | 100.00 | Each |  | 374.00 | 37400.00 | 95.00 | 9500.00 | 147.00 | 14700.00 | 280.00 | 28000.00 | 1065.00 | 106500.00 | 232.50 | 23250.00 | 113.00 | 11300.00 | 9500.00 | P AND C PROJECTS PRIVATE LIMITED
362.00 | Male Connector(2532x1.25") | 100.00 | Each |  | 499.00 | 49900.00 | 95.00 | 9500.00 | 147.00 | 14700.00 | 280.00 | 28000.00 | 1156.00 | 115600.00 | 232.50 | 23250.00 | 113.00 | 11300.00 | 9500.00 | P AND C PROJECTS PRIVATE LIMITED
363.00 | Male Connector(3240x1.25") | 100.00 | Each |  | 587.00 | 58700.00 | 144.00 | 14400.00 | 226.00 | 22600.00 | 430.00 | 43000.00 | 1690.00 | 169000.00 | 310.00 | 31000.00 | 174.00 | 17400.00 | 14400.00 | P AND C PROJECTS PRIVATE LIMITED
364.00 | Male Connector(3240x1.5") | 100.00 | Each |  | 670.00 | 67000.00 | 142.00 | 14200.00 | 225.00 | 22500.00 | 430.00 | 43000.00 | 2614.00 | 261400.00 | 310.00 | 31000.00 | 170.00 | 17000.00 | 14200.00 | P AND C PROJECTS PRIVATE LIMITED
365.00 | Male Connector (4050x2") | 100.00 | Each |  | 838.00 | 83800.00 | 319.00 | 31900.00 | 476.00 | 47600.00 | 960.00 | 96000.00 | 2637.00 | 263700.00 | 666.50 | 66650.00 | 361.00 | 36100.00 | 31900.00 | P AND C PROJECTS PRIVATE LIMITED
366.00 | Reducer
367.00 | Reducer(1620x1216) | 100.00 | Each |  | 126.00 | 12600.00 | 118.00 | 11800.00 | 174.00 | 17400.00 | 330.00 | 33000.00 | 174.00 | 17400.00 | 232.50 | 23250.00 | 133.00 | 13300.00 | 11800.00 | P AND C PROJECTS PRIVATE LIMITED
368.00 | Reducer(2025x1216) | 100.00 | Each |  | 165.00 | 16500.00 | 154.00 | 15400.00 | 226.00 | 22600.00 | 430.00 | 43000.00 | 227.00 | 22700.00 | 310.00 | 31000.00 | 174.00 | 17400.00 | 15400.00 | P AND C PROJECTS PRIVATE LIMITED
369.00 | Reducer(2025x1620) | 100.00 | Each |  | 198.00 | 19800.00 | 164.00 | 16400.00 | 242.00 | 24200.00 | 460.00 | 46000.00 | 312.00 | 31200.00 | 341.00 | 34100.00 | 186.00 | 18600.00 | 16400.00 | P AND C PROJECTS PRIVATE LIMITED
370.00 | Reducer(2532x2025) | 100.00 | Each |  | 301.00 | 30100.00 | 238.00 | 23800.00 | 367.00 | 36700.00 | 700.00 | 70000.00 | 367.00 | 36700.00 | 496.00 | 49600.00 | 278.00 | 27800.00 | 23800.00 | P AND C PROJECTS PRIVATE LIMITED
371.00 | Reducer(3240x2532) | 100.00 | Each |  | 460.00 | 46000.00 | 250.00 | 25000.00 | 395.00 | 39500.00 | 750.00 | 75000.00 | 395.00 | 39500.00 | 496.00 | 49600.00 | 299.00 | 29900.00 | 25000.00 | P AND C PROJECTS PRIVATE LIMITED
372.00 | Reducer (4050x3240) | 100.00 | Each |  | 409.00 | 40900.00 | 424.00 | 42400.00 | 669.00 | 66900.00 | 1270.00 | 127000.00 | 670.00 | 67000.00 | 852.50 | 85250.00 | 508.00 | 50800.00 | 40900.00 | JATAN CONSTRUCTIONS PVT LTD
373.00 | Straight Coupler
374.00 | Straight Coupler(1216) | 100.00 | Each |  | 108.00 | 10800.00 | 105.00 | 10500.00 | 156.00 | 15600.00 | 300.00 | 30000.00 | 156.00 | 15600.00 | 232.50 | 23250.00 | 118.00 | 11800.00 | 10500.00 | P AND C PROJECTS PRIVATE LIMITED
375.00 | Straight Coupler(1620) | 100.00 | Each |  | 143.00 | 14300.00 | 128.00 | 12800.00 | 190.00 | 19000.00 | 360.00 | 36000.00 | 189.00 | 18900.00 | 232.50 | 23250.00 | 142.00 | 14200.00 | 12800.00 | P AND C PROJECTS PRIVATE LIMITED
376.00 | Straight Coupler(2025) | 100.00 | Each |  | 225.00 | 22500.00 | 196.00 | 19600.00 | 290.00 | 29000.00 | 550.00 | 55000.00 | 289.00 | 28900.00 | 387.50 | 38750.00 | 219.00 | 21900.00 | 19600.00 | P AND C PROJECTS PRIVATE LIMITED
377.00 | Straight Coupler(2532) | 100.00 | Each |  | 367.00 | 36700.00 | 212.00 | 21200.00 | 332.00 | 33200.00 | 640.00 | 64000.00 | 332.00 | 33200.00 | 465.00 | 46500.00 | 252.00 | 25200.00 | 21200.00 | P AND C PROJECTS PRIVATE LIMITED
378.00 | Straight Coupler(3240) | 100.00 | Each |  | 516.00 | 51600.00 | 299.00 | 29900.00 | 470.00 | 47000.00 | 900.00 | 90000.00 | 472.00 | 47200.00 | 666.50 | 66650.00 | 359.00 | 35900.00 | 29900.00 | P AND C PROJECTS PRIVATE LIMITED
379.00 | Straight Coupler(4050) | 100.00 | Each |  | 501.00 | 50100.00 | 584.00 | 58400.00 | 920.00 | 92000.00 | 1750.00 | 175000.00 | 1130.00 | 113000.00 | 1178.00 | 117800.00 | 699.00 | 69900.00 | 50100.00 | JATAN CONSTRUCTIONS PVT LTD
380.00 | Female Elbow
381.00 | Female Elbow (1216x1/2") | 100.00 | Each |  | 132.00 | 13200.00 | 105.00 | 10500.00 | 153.00 | 15300.00 | 290.00 | 29000.00 | 299.00 | 29900.00 | 232.50 | 23250.00 | 117.00 | 11700.00 | 10500.00 | P AND C PROJECTS PRIVATE LIMITED
382.00 | Female Elbow (1620x1/2") | 100.00 | Each |  | 152.00 | 15200.00 | 118.00 | 11800.00 | 174.00 | 17400.00 | 330.00 | 33000.00 | 418.00 | 41800.00 | 232.50 | 23250.00 | 133.00 | 13300.00 | 11800.00 | P AND C PROJECTS PRIVATE LIMITED
383.00 | Female Elbow (2025x1/2") | 100.00 | Each |  | 196.00 | 19600.00 | 167.00 | 16700.00 | 247.00 | 24700.00 | 470.00 | 47000.00 | 518.00 | 51800.00 | 387.50 | 38750.00 | 188.00 | 18800.00 | 16700.00 | P AND C PROJECTS PRIVATE LIMITED
384.00 | Female Thread connector
385.00 | Female Thread connector (1216x1/2") | 100.00 | Each |  | 130.00 | 13000.00 | 101.00 | 10100.00 | 149.00 | 14900.00 | 290.00 | 29000.00 | 176.00 | 17600.00 | 232.50 | 23250.00 | 114.00 | 11400.00 | 10100.00 | P AND C PROJECTS PRIVATE LIMITED
386.00 | Female Thread connector (1620x1/2") | 100.00 | Each |  | 148.00 | 14800.00 | 115.00 | 11500.00 | 168.00 | 16800.00 | 320.00 | 32000.00 | 299.00 | 29900.00 | 232.50 | 23250.00 | 128.00 | 12800.00 | 11500.00 | P AND C PROJECTS PRIVATE LIMITED
387.00 | Providing as per requirement and fixing G.I Threaded Flange in polyethylene -Aluminium - polyethylene (PE-AL-PE) composite pressure pipe fittings Male threaded connector,etc. in Kitec/vista or approved equivalent including labour, tools, tackles etc, complete as per drawing and specifications.
388.00 | 40mm | 100.00 | SET |  | 853.00 | 85300.00 | 125.00 | 12500.00 | 948.00 | 94800.00 | 240.00 | 24000.00 | 2643.00 | 264300.00 | 1178.00 | 117800.00 | 721.00 | 72100.00 | 12500.00 | P AND C PROJECTS PRIVATE LIMITED
389.00 | 50mm | 100.00 | SET |  | 2061.00 | 206100.00 | 136.00 | 13600.00 | 2390.00 | 239000.00 | 300.00 | 30000.00 | 2643.00 | 264300.00 | 2170.00 | 217000.00 | 1820.00 | 182000.00 | 13600.00 | P AND C PROJECTS PRIVATE LIMITED
390.00 | Supply and fixing single/multi stainless steel nahani trap of self-cleaning design with 75 mm diameter outlet, "Supreme/Prince/ Star/Finolex/Jain/Kitec" make or approved equivalent as per relevant IS, with stainless steel grating and including necessary cement concrete 1:2:4 for embedding and making good the floor, connecting the trap to the waste pipe, forming circular hole up to floor level and rendering smooth etc., complete as per drawing and specifications. | 1000.00 | Each |  | 1344.00 | 1344000.00 | 3346.00 | 3346000.00 | 614.00 | 614000.00 | 600.00 | 600000.00 | 991.00 | 991000.00 | 2325.00 | 2325000.00 | 148.00 | 148000.00 | 148000.00 | Ocean Lifespaces India Private Limited
391.00 | Supply and fixing "Prayag" or approved equivalent PTMT Symet cockroach trap with grating without hole for bath room & toilets etc., complete as per drawing and specifications. | 100.00 | Each |  | 970.00 | 97000.00 | 128.00 | 12800.00 | 193.00 | 19300.00 | 220.00 | 22000.00 | 1520.00 | 152000.00 | 775.00 | 77500.00 | 334.00 | 33400.00 | 12800.00 | P AND C PROJECTS PRIVATE LIMITED
392.00 | Supply and fixing factory made fully solid core PVC doors using PVC door frame (single rebate) made out of single piece extruded solid PVC foam profile with homogeneous fine cellular strength having smooth outer integral skin of 60mm wide x 30mm thickness of density 600Kg/m3, frame will be mitred and joined with self-taping screws of size 50mm x8mm and PVC solvent cement or fusion heat welding process as per manufacturers specifications. | 300.00 | Sq. Meter |  | 3984.00 | 1195200.00 | 3704.00 | 1111200.00 | 10692.00 | 3207600.00 | 5630.00 | 1689000.00 | 9912.00 | 2973600.00 | 4650.00 | 1395000.00 | 3204.00 | 961200.00 | 961200.00 | Ocean Lifespaces India Private Limited
393.00 | Supply and fixing vitreous china ware recess type soap dish 200 x 100 mm size "Hindware/Cera/Nycer /Parryware" make including making necessary chases in wall for Fixing and making good the same complete as per drawings and specifications. | 100.00 | Nos. |  | 2367.00 | 236700.00 | 532.00 | 53200.00 | 1053.00 | 105300.00 | 630.00 | 63000.00 | 1123.00 | 112300.00 | 1240.00 | 124000.00 | 802.00 | 80200.00 | 53200.00 | P AND C PROJECTS PRIVATE LIMITED
394.00 | Supply and fixing rectangular stainless steel sink of type B1 as per IS 13983, including all fittings, PVC flexible connection, etc. complete as per specifications and drawings. | 10.00 | Nos. |  | 5277.00 | 52770.00 | 1464.00 | 14640.00 | 14855.00 | 148550.00 | 10180.00 | 101800.00 | 16520.00 | 165200.00 | 9300.00 | 93000.00 | 4271.00 | 42710.00 | 14640.00 | P AND C PROJECTS PRIVATE LIMITED
395.00 | Road and surface drains
396.00 | Construction of granular sub-base by providing close graded material conforming to specifications, mixing in a mechanical mix plant at OMC, carriage of mixed material by tippers to work site, for all leads & lifts, spreading in uniform layers of specified thickness with motor grader on prepared surface and compacting with vibratory power roller to achieve the desired density, complete as per specifications with material conforming to Grade-I (size range 75 mm to 0.075 mm) having CBR Value 30, as per clause 401 of MoRT&H specifications etc., complete as per construction drawings. | 4850.00 | Cu. Meter |  | 3087.00 | 14971950.00 | 2045.00 | 9918250.00 | 2110.00 | 10233500.00 | 2400.00 | 11640000.00 | 2060.00 | 9991000.00 | 3053.50 | 14809475.00 | 2614.00 | 12677900.00 | 9918250.00 | P AND C PROJECTS PRIVATE LIMITED
397.00 | Supply, laying, spreading and compacting graded stone aggregate (size range 53 mm to 0.075mm) to wet mix macadam (WMM) specification including premixing the material with water at OMC in mechanical mix plant, carriage of mixed material by tipper to site, for all leads & lifts, laying in uniform layers with mechanical paver finisher in sub- base / base course on well prepared surface and compacting with vibratory roller of 8 to 10 tonne capacity to achieve the desired density, complete as per construction drawings, specifications and clause 406 of MoRT&H specifications. | 5250.00 | Cu. Meter |  | 3410.00 | 17902500.00 | 2169.00 | 11387250.00 | 2213.00 | 11618250.00 | 2640.00 | 13860000.00 | 2048.00 | 10752000.00 | 3332.50 | 17495625.00 | 3088.00 | 16212000.00 | 10752000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
398.00 | Supply and applying prime coat using medium setting bitumen emulsion conforming to IS:8887 on prepared surface of granular base including clearing the road surface and spraying primer at the rate of 6 kg/10m2, as per clause 502 of MORT&H specifications, construction drawings and NPCIL specifications. | 20000.00 | Sq. Meter |  | 81.00 | 1620000.00 | 41.00 | 820000.00 | 64.00 | 1280000.00 | 110.00 | 2200000.00 | 73.00 | 1460000.00 | 108.50 | 2170000.00 | 97.00 | 1940000.00 | 820000.00 | P AND C PROJECTS PRIVATE LIMITED
399.00 | Supply and applying tack coat using bitumen emulsion conforming to IS: 8887 using emulsion pressure distributor including preparing the surface & cleaning with mechanical broom. with rapid settling emulsion on bitumen surface @ 0.25kg/m2 as per clause 503 of MORT&H specifications, construction drawings and NPCIL specifications. | 20000.00 | Sq. Meter |  | 26.00 | 520000.00 | 14.00 | 280000.00 | 35.00 | 700000.00 | 50.00 | 1000000.00 | 40.00 | 800000.00 | 62.00 | 1240000.00 | 64.00 | 1280000.00 | 280000.00 | P AND C PROJECTS PRIVATE LIMITED
400.00 | Supply and laying dense graded bituminous macadam 50 to 100mm thick (or thickness as specified) from hot mix plant using crushed aggregates of specified grading premixed with bituminous binder at 5% by weight of total mix and filler, transporting the hot mix to site, laid over a previously prepared surface with a hydrostatic paver finisher with sensor control to the required grade, level and alignment and rolled with smooth wheeled, vibratory and tandem rollers to achieve the desired compaction as per clause 507 of MoRT&H specifications, construction drawings and NPCIL specifications. | 1000.00 | Cu. Meter |  | 14627.00 | 14627000.00 | 11351.00 | 11351000.00 | 14040.00 | 14040000.00 | 13500.00 | 13500000.00 | 14538.00 | 14538000.00 | 12400.00 | 12400000.00 | 16211.00 | 16211000.00 | 11351000.00 | P AND C PROJECTS PRIVATE LIMITED
401.00 | Supply and laying bituminous concrete 40mm thick (or thickness as specified) from hot mix plant using crushed aggregates of specified grading premixed with bituminous binder at 5.4 to 5.6% by weight of total mix and filler, transporting the hot mix to site, laid over a previously prepared surface with a hydrostatic paver finisher with sensor control to the required grade, level and alignment and rolled with smooth wheeled, vibratory and tandem rollers to achieve the desired compaction as per clause 509 of MoRT&H specifications, construction drawings and NPCIL specifications. | 1000.00 | Cu. Meter |  | 15950.00 | 15950000.00 | 12666.00 | 12666000.00 | 16158.00 | 16158000.00 | 15000.00 | 15000000.00 | 15859.00 | 15859000.00 | 14725.00 | 14725000.00 | 17364.00 | 17364000.00 | 12666000.00 | P AND C PROJECTS PRIVATE LIMITED
402.00 | Supply and applying 2.5mm thick road marking strips (retro-reflective) of specified shade/ colour using hot thermoplastic material by fully/ semi-automatic thermoplastic paint applicator machine fitted with profile shoe, glass beads dispenser, propane tank heater and profile shoe heater, driven by experienced operator on road surface including cost of material, labour, T&P, cleaning the road surface of all dirt, seals, oil, grease and foreign material etc., complete as per drawings and specifications. | 1000.00 | Sq. Meter |  | 1308.00 | 1308000.00 | 394.00 | 394000.00 | 525.00 | 525000.00 | 900.00 | 900000.00 | 859.00 | 859000.00 | 775.00 | 775000.00 | 1089.00 | 1089000.00 | 394000.00 | P AND C PROJECTS PRIVATE LIMITED
403.00 | Supply and fixing reflective road studs of ‘category B’ raised pavement markers made out of poly carbonate/ABS moulded body and reflective panels (bi-convex reflectors) with micro prismatic lens capable of providing as per requirement total internal reflection of the light entering the lens face with retro-reflectance and chromaticity values conforming to ASTMD4280. The reflective raised pavement markers shall also confirm to the MoRT&H circular no RW/NH.33023/10/97-DO-III dt 11.06.97 and the length, height and width of the body shall not be less than 100mm, 15mm and 90mm and base of marker shall be flat within 1.3mm. The marker shall support a load of 13635Kg tested in accordance with ASTM D4280. Lenses shall be moulded of polycarbonate of methyl methacrylate conforming to ASTM D788. The area of each retro –reflector surface shall be 35+5 degree to base. Each reflector shall have a CIL not less than values specified in table2 of said MoRT &H circular and 2 cylindrical polymer shanks of not less than 20mm diameter and not less than 30mm length shall be provided for better anchorage etc, complete as per drawings and specifications. | 1000.00 | Nos. |  | 169.00 | 169000.00 | 209.00 | 209000.00 | 225.00 | 225000.00 | 830.00 | 830000.00 | 363.00 | 363000.00 | 620.00 | 620000.00 | 449.00 | 449000.00 | 169000.00 | JATAN CONSTRUCTIONS PVT LTD
404.00 | Supply and laying of P1 class RCC pipes with spigot & socket joint with rubber cord ring diameter mentioned below conforming to IS 458, joined with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing the joints etc., complete as per drawings and specifications.
405.00 | diameter - 150 mm | 1200.00 | RM |  | 1139.00 | 1366800.00 | 508.00 | 609600.00 | 1620.00 | 1944000.00 | 900.00 | 1080000.00 | 1258.00 | 1509600.00 | 542.50 | 651000.00 | 1504.00 | 1804800.00 | 609600.00 | P AND C PROJECTS PRIVATE LIMITED
406.00 | diameter - 200 mm and 250 mm | 500.00 | RM |  | 1272.00 | 636000.00 | 795.00 | 397500.00 | 1944.00 | 972000.00 | 1020.00 | 510000.00 | 1586.00 | 793000.00 | 1240.00 | 620000.00 | 2026.00 | 1013000.00 | 397500.00 | P AND C PROJECTS PRIVATE LIMITED
407.00 | diameter - 300 mm and 350 mm | 250.00 | RM |  | 1749.00 | 437250.00 | 1751.00 | 437750.00 | 2268.00 | 567000.00 | 1450.00 | 362500.00 | 2462.00 | 615500.00 | 1937.50 | 484375.00 | 2703.00 | 675750.00 | 362500.00 | DEE VEE PROJECTS LIMITED
408.00 | diameter - 400 mm and 450 mm | 150.00 | RM |  | 3072.00 | 460800.00 | 2455.00 | 368250.00 | 4212.00 | 631800.00 | 2760.00 | 414000.00 | 3448.00 | 517200.00 | 2325.00 | 348750.00 | 4601.00 | 690150.00 | 348750.00 | VRC Constructions (India) Limited
409.00 | diameter - 500 mm and 550 mm | 60.00 | RM |  | 3491.00 | 209460.00 | 2577.00 | 154620.00 | 5022.00 | 301320.00 | 2830.00 | 169800.00 | 4103.00 | 246180.00 | 3410.00 | 204600.00 | 6091.00 | 365460.00 | 154620.00 | P AND C PROJECTS PRIVATE LIMITED
410.00 | diameter - 600 mm | 500.00 | RM |  | 4359.00 | 2179500.00 | 2788.00 | 1394000.00 | 5184.00 | 2592000.00 | 3100.00 | 1550000.00 | 4651.00 | 2325500.00 | 3720.00 | 1860000.00 | 7037.00 | 3518500.00 | 1394000.00 | P AND C PROJECTS PRIVATE LIMITED
411.00 | diameter - 700 mm | 500.00 | RM |  | 4983.00 | 2491500.00 | 3843.00 | 1921500.00 | 7128.00 | 3564000.00 | 3240.00 | 1620000.00 | 6020.00 | 3010000.00 | 4650.00 | 2325000.00 | 7642.00 | 3821000.00 | 1620000.00 | DEE VEE PROJECTS LIMITED
412.00 | diameter - 800 mm | 500.00 | RM |  | 6196.00 | 3098000.00 | 4283.00 | 2141500.00 | 7452.00 | 3726000.00 | 3630.00 | 1815000.00 | 7930.00 | 3965000.00 | 5890.00 | 2945000.00 | 9609.00 | 4804500.00 | 1815000.00 | DEE VEE PROJECTS LIMITED
413.00 | diameter - 900 mm | 500.00 | RM |  | 6997.00 | 3498500.00 | 4766.00 | 2383000.00 | 9396.00 | 4698000.00 | 4030.00 | 2015000.00 | 9021.00 | 4510500.00 | 7440.00 | 3720000.00 | 11916.00 | 5958000.00 | 2015000.00 | DEE VEE PROJECTS LIMITED
414.00 | diameter – 1000 mm | 400.00 | RM |  | 7328.00 | 2931200.00 | 5733.00 | 2293200.00 | 10724.00 | 4289600.00 | 5890.00 | 2356000.00 | 8703.00 | 3481200.00 | 8990.00 | 3596000.00 | 13541.00 | 5416400.00 | 2293200.00 | P AND C PROJECTS PRIVATE LIMITED
415.00 | diameter – 1100 mm | 200.00 | RM |  | 10599.00 | 2119800.00 | 6533.00 | 1306600.00 | 10804.00 | 2160800.00 | 6520.00 | 1304000.00 | 9194.00 | 1838800.00 | 10850.00 | 2170000.00 | 16527.00 | 3305400.00 | 1304000.00 | DEE VEE PROJECTS LIMITED
416.00 | diameter – 1200 mm | 500.00 | RM |  | 10966.00 | 5483000.00 | 8029.00 | 4014500.00 | 13284.00 | 6642000.00 | 7230.00 | 3615000.00 | 9695.00 | 4847500.00 | 13020.00 | 6510000.00 | 18153.00 | 9076500.00 | 3615000.00 | DEE VEE PROJECTS LIMITED
417.00 | Supply and installation of NP -2 class RCC hume pipe of size 300 mm dia,with collars,cementing has to be done where ever collar is used etc, all as per specification. (excavation will be measured in respective item). | 125.00 | RM |  | 1161.00 | 145125.00 | 1197.00 | 149625.00 | 2446.00 | 305750.00 | 1500.00 | 187500.00 | 2238.00 | 279750.00 | 1162.50 | 145312.50 | 1520.00 | 190000.00 | 145125.00 | JATAN CONSTRUCTIONS PVT LTD
418.00 | Supply, fixing in position at all elevations on walls, under floors/ground etc., or as indicated in drawings, high density poly ethylene (HDPE) pipes of grade PE 80 as per IS 4984 sourced from NPCIL approved manufacturer or equivalent of size 160mm diameter with pressure rating of 10kg/cm2 including the specials, necessary welding and pressure testing with clean water as per standard specification and rectifying the leaks, if found etc., complete as per construction drawing and specifications. Note: Earthwork excavation, reinforcement steel shall be paid under relevant item. | 500.00 | RM |  | 2063.00 | 1031500.00 | 741.00 | 370500.00 | 1870.00 | 935000.00 | 700.00 | 350000.00 | 945.00 | 472500.00 | 1395.00 | 697500.00 | 3031.00 | 1515500.00 | 350000.00 | DEE VEE PROJECTS LIMITED
419.00 | Supply the required material and sealing joints up to 40 mm wide and up to 300 mm deep in between precast covers, in PCC / RCC at locations and levels indicated in drawing and / or as directed by ENGINEER with approved bitumen mastic filler as per IS 1834 including raking of joints etc., all complete as per construction drawings and specifications. | 1500.00 | RM |  | 2352.00 | 3528000.00 | 228.00 | 342000.00 | 675.00 | 1012500.00 | 250.00 | 375000.00 | 363.00 | 544500.00 | 558.00 | 837000.00 | 212.00 | 318000.00 | 318000.00 | Ocean Lifespaces India Private Limited
420.00 | Supply and laying M30 grade 60 mm thick coloured interlocking precast concrete paver blocks as per IS 15658 of approved shape over, laid over sand bed, to the required line, pattern etc., all as per construction drawings and specifications. | 2000.00 | Sq. Meter |  | 1227.00 | 2454000.00 | 700.00 | 1400000.00 | 1053.00 | 2106000.00 | 1000.00 | 2000000.00 | 859.00 | 1718000.00 | 930.00 | 1860000.00 | 1350.00 | 2700000.00 | 1400000.00 | P AND C PROJECTS PRIVATE LIMITED
421.00 | Supply and laying crushed stone aggregate bed of 60mm thickness (compacted thickness) for preparation of base to lay interlocking precast concrete paver blocks using 12 mm and down, graded stone aggregate including, levelling, placing, to the required slope, compacting with roller etc., as per construction drawings and specifications. (Payment shall be made only for compacted thickness). | 600.00 | Cu. Meter |  | 3014.00 | 1808400.00 | 2517.00 | 1510200.00 | 1785.00 | 1071000.00 | 2200.00 | 1320000.00 | 1771.00 | 1062600.00 | 2309.50 | 1385700.00 | 2448.00 | 1468800.00 | 1062600.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
422.00 | MISCELLANEOUS WORKS
423.00 | Supplying chain link fencing fabric (PVC coated) of 50mm mesh size of Tata or approved equivalent make and nominal diameter of mesh wire equal to 4mm as per IS 2721, fixing it to MS angle posts using PVC coated GI line wire connected to posts using M10 size GI bolts and 6 mm diameter MS stretcher rods tied vertically on posts using M8 size GI J bolt inclusive of their supply etc., complete as per drawings and specifications. Note: The MS angle posts and MS stretcher rods shall be paid under relevant item. | 5500.00 | Sq. Meter |  | 1174.00 | 6457000.00 | 232.00 | 1276000.00 | 687.00 | 3778500.00 | 800.00 | 4400000.00 | 231.00 | 1270500.00 | 852.50 | 4688750.00 | 452.00 | 2486000.00 | 1270500.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
424.00 | Dismantling either manually or with pneumatic tools or with rotary mechanical equipment the existing structures of the following materials without disturbing adjacent structures at all elevations, covering the structures / equipment adjacent to the work, cleaning and removal of debris, dust on day to day basis and disposal of the debris up to a lead of 3km. Rates shall include all labour, plant, tools, tackles, consumables, scaffolding & staging, equipment mobilisation and deployment of qualified manpower etc., complete as per drawings and specifications.
425.00 | Plain Cement Concrete of all grades | 50.00 | Cu. Meter |  | 6413.00 | 320650.00 | 1494.00 | 74700.00 | 3150.00 | 157500.00 | 1500.00 | 75000.00 | 1652.00 | 82600.00 | 1550.00 | 77500.00 | 3111.00 | 155550.00 | 74700.00 | P AND C PROJECTS PRIVATE LIMITED
426.00 | Reinforced Cement Concrete of all grades | 100.00 | Cu. Meter |  | 6980.00 | 698000.00 | 2091.00 | 209100.00 | 4200.00 | 420000.00 | 2200.00 | 220000.00 | 1982.00 | 198200.00 | 4650.00 | 465000.00 | 3778.00 | 377800.00 | 198200.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
427.00 | Brick / stone/ concrete block masonry | 100.00 | Cu. Meter |  | 10224.00 | 1022400.00 | 597.00 | 59700.00 | 2100.00 | 210000.00 | 1000.00 | 100000.00 | 1123.00 | 112300.00 | 1550.00 | 155000.00 | 1667.00 | 166700.00 | 59700.00 | P AND C PROJECTS PRIVATE LIMITED
428.00 | Reinforced Cement Concrete of all grades using electric wire saw. The surface area of dismantled concrete face shall be considered for payment. | 200.00 | Sq. Meter |  | 8701.00 | 1740200.00 | 478.00 | 95600.00 | 6300.00 | 1260000.00 | 4130.00 | 826000.00 | 24450.00 | 4890000.00 | 10850.00 | 2170000.00 | 1556.00 | 311200.00 | 95600.00 | P AND C PROJECTS PRIVATE LIMITED
429.00 | Drilling/core cutting in reinforced concrete structures of various depths in reinforced concrete walls / slabs with rotary drilling at all elevations / positions without disturbing adjacent structures at all elevation including arrangement machineries and consumables required for completion of the job, covering the structures / equipment adjacent to the work , cleaning and removal of debris, dust on day to day basis and disposal of the debris up to a lead of 3km. , finishing of the edges of the holes and the area nearby where the surface is damaged, , with cement mortar. Rates shall include all labour, plant, tools, tackles, consumables, scaffolding & staging etc., complete as per drawings and specifications. Note: The unit of measurement is mm-meter i.e. the diameter of drill hole in mm x depth of drill hole in meter.
430.00 | Less than or equal to 100 mm diameter | 15000.00 | mm-meter |  | 63.00 | 945000.00 | 1416.00 | 21240000.00 | 7.00 | 105000.00 | 230.00 | 3450000.00 | 59.00 | 885000.00 | 23.25 | 348750.00 | 524.00 | 7860000.00 | 105000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
431.00 | Above 100 mm and up to 200 mm diameter | 20000.00 | mm-meter |  | 78.00 | 1560000.00 | 2266.00 | 45320000.00 | 11.00 | 220000.00 | 450.00 | 9000000.00 | 119.00 | 2380000.00 | 31.00 | 620000.00 | 524.00 | 10480000.00 | 220000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
432.00 | Above 200mm and up to 300mm diameter | 15000.00 | mm-meter |  | 93.00 | 1395000.00 | 3540.00 | 53100000.00 | 15.00 | 225000.00 | 650.00 | 9750000.00 | 198.00 | 2970000.00 | 38.75 | 581250.00 | 524.00 | 7860000.00 | 225000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
433.00 | Chipping of finished floor/concrete : Chipping out a portion from concrete of all grades with concrete chipping power tools and restoring to the original finish including providing as per requirement of all consumables etc., after equipment / foundation plate installation and making good the surface, supply of skilled manpower and resources for the requirement, tools and tackles for carrying out the job. Note : Measurement of the chipped area will be done m2 wise.
434.00 | Chipping of above 25 mm up to 50 mm depth | 1000.00 | Sq. Meter |  | 1470.00 | 1470000.00 | 208.00 | 208000.00 | 350.00 | 350000.00 | 150.00 | 150000.00 | 1256.00 | 1256000.00 | 1550.00 | 1550000.00 | 139.00 | 139000.00 | 139000.00 | Ocean Lifespaces India Private Limited
435.00 | Chipping above 50 mm up to 100 mm depth | 500.00 | Sq. Meter |  | 2021.00 | 1010500.00 | 417.00 | 208500.00 | 560.00 | 280000.00 | 230.00 | 115000.00 | 1982.00 | 991000.00 | 1860.00 | 930000.00 | 261.00 | 130500.00 | 115000.00 | DEE VEE PROJECTS LIMITED
436.00 | Mapping the reinforcement bars in the RCC elements using specific non-destructive method such as ground penetration radar to identify position of reinforcement bars before carrying out dismantling work including mobilisation of equipment and qualified operator at various instances as required, preparation of report etc., completed as per instructions of ENGINEER and specifications. | 100.00 | Sq. Meter |  | 735.00 | 73500.00 | 428568.00 | 42856800.00 | 14000.00 | 1400000.00 | 600.00 | 60000.00 | 8590.00 | 859000.00 | 23250.00 | 2325000.00 | 16668.00 | 1666800.00 | 60000.00 | DEE VEE PROJECTS LIMITED
437.00 | Providing pre-construction anti-termite treatment using chlorpyriphos emulsifiable concentrate 20 % with 1 % concentration as per specifications. Note: The contractor shall furnish from the agency carrying out this work under this item a written guarantee in favour of NPCIL for the satisfactory performance of the treatment for a period of ten years. | 2500.00 | Sq. Meter |  | 588.00 | 1470000.00 | 84.00 | 210000.00 | 196.00 | 490000.00 | 300.00 | 750000.00 | 298.00 | 745000.00 | 193.75 | 484375.00 | 72.00 | 180000.00 | 180000.00 | Ocean Lifespaces India Private Limited
438.00 | Supplying and Fixing in position approved quality 18SWG steel rolling shutter, push and pull type made of MS girders, pressed bottom rails, brackets, extra strong door suspension shaft with fully and cage with cowl, top rolling springs, hood locking arrangements, all fittings and accessories as per approved drawings including providing and applying two coats of approved quality synthetic enamel paint over a coat of zinc chromite primer, Fixing at all levels as per drawings and specifications Note: (1) payment will be made based on the clear structural opening dimensions only and not full size of shutter. (2).The hood will not be measured for payment (3).The rolling shutter shall be designed to withstand wind pressure of 150 kg/m3.
439.00 | Mechanically operated rolling shutter with provision of gear for manual operation. | 400.00 | Sq. Meter |  | 10305.00 | 4122000.00 | 3226.00 | 1290400.00 | 8509.00 | 3403600.00 | 11000.00 | 4400000.00 | 6278.00 | 2511200.00 | 6975.00 | 2790000.00 | 13246.00 | 5298400.00 | 1290400.00 | P AND C PROJECTS PRIVATE LIMITED
440.00 | Electrically operated rolling shutter with 3-phase, 415V AC electric motor, TEFC enclosure complying to standard specifications, switches and electrical wiring including provision of gear for manual operation. | 200.00 | Sq. Meter |  | 11025.00 | 2205000.00 | 59745.00 | 11949000.00 | 14526.00 | 2905200.00 | 18000.00 | 3600000.00 | 8590.00 | 1718000.00 | 12400.00 | 2480000.00 | 20042.00 | 4008400.00 | 1718000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
441.00 | Providing and Installation of medium duty GI pipes for laying cables or otherwise including all accessories like bends, GI clamps, hardware, any cutting, drilling, welding, Providing as per requirement and application of cold galvanisation paint, etc., as directed by the ENGINEER.
442.00 | 100 mm NB | 2040.00 | RM |  | 1455.00 | 2968200.00 | 765.00 | 1560600.00 | 1654.00 | 3374160.00 | 3320.00 | 6772800.00 | 2643.00 | 5391720.00 | 1743.75 | 3557250.00 | 1735.00 | 3539400.00 | 1560600.00 | P AND C PROJECTS PRIVATE LIMITED
443.00 | 150 mm NB | 1000.00 | RM |  | 2279.00 | 2279000.00 | 797.00 | 797000.00 | 2643.00 | 2643000.00 | 5140.00 | 5140000.00 | 4295.00 | 4295000.00 | 2836.50 | 2836500.00 | 2641.00 | 2641000.00 | 797000.00 | P AND C PROJECTS PRIVATE LIMITED
444.00 | 200 mm NB | 500.00 | RM |  | 3241.00 | 1620500.00 | 860.00 | 430000.00 | 4587.00 | 2293500.00 | 8920.00 | 4460000.00 | 5286.00 | 2643000.00 | 4068.75 | 2034375.00 | 3657.00 | 1828500.00 | 430000.00 | P AND C PROJECTS PRIVATE LIMITED
445.00 | 250 mm NB | 300.00 | RM |  | 4153.00 | 1245900.00 | 895.00 | 268500.00 | 5746.00 | 1723800.00 | 10770.00 | 3231000.00 | 5947.00 | 1784100.00 | 4611.25 | 1383375.00 | 4372.00 | 1311600.00 | 268500.00 | P AND C PROJECTS PRIVATE LIMITED
446.00 | Supply and fixing broken glass pieces at the rate of 5 kg/m2 as coping over a bed of PCC in fencing works as per construction drawings and specifications. | 1507.00 | Sq. Meter |  | 397.00 | 598279.00 | 131.00 | 197417.00 | 336.00 | 506352.00 | 100.00 | 150700.00 | 1520.00 | 2290640.00 | 775.00 | 1167925.00 | 333.00 | 501831.00 | 150700.00 | DEE VEE PROJECTS LIMITED
447.00 | Supply and fixing of galvanised steel barbed wire of Tata Steel or approved equivalent make as per IS 278 of size and galvanisation requirement as per specifications and drawings. | 10000.00 | RM |  | 44.00 | 440000.00 | 106.00 | 1060000.00 | 25.00 | 250000.00 | 570.00 | 5700000.00 | 10.00 | 100000.00 | 27.90 | 279000.00 | 19.00 | 190000.00 | 100000.00 | BRIDGE AND ROOF COMPANY INDIA LIMITED
448.00 | Supply and installation of cast iron manhole steps conforming to IS5455 at locations specified in the drawing. | 8000.00 | kg |  | 132.00 | 1056000.00 | 118.00 | 944000.00 | 146.00 | 1168000.00 | 250.00 | 2000000.00 | 152.00 | 1216000.00 | 186.00 | 1488000.00 | 134.00 | 1072000.00 | 944000.00 | P AND C PROJECTS PRIVATE LIMITED
449.00 | Supply and fixing CONSE ZAL Super Razor punched barb tape (SRPBT) aluminium base helix coil of 610mm diameter (before stretch) i.e., concertina wire, including necessary fixing clips for securing, complete as per following specification: - (i) Diameter of coil (upstretched)- 610mm (ii) No of circles:- 51 turns per coil (iii) Coverage in length:- 6 m per coil (iv) Weight of each coil with hessian pack - 8.00 kg (±0.5). (v) Central core wire - Made from 2.60mm diameter H.T.S.S wire as per IS - 4454 galvanised as per IS- 2629. (vi) Razor Punched strip:-Razor Punched tape is CONSEC-ZAL steel comprising of aluminium base with zinc alloy @ 150 g/m² confirming to ASTM A-792/A-792M with additional primer treatment of Epoxy/Polyurethane and final paint top coat of Caulfield green shade (BSL 139) by Hot dipping process & barb tape length - 23.50mm, barb width - 18.60 mm, barb spacing 36.00mm, Centre Width -7.40 mm, etc., complete as per drawings and specifications. | 2200.00 | RM |  | 451.00 | 992200.00 | 1054.00 | 2318800.00 | 173.00 | 380600.00 | 700.00 | 1540000.00 | 393.00 | 864600.00 | 465.00 | 1023000.00 | 482.00 | 1060400.00 | 380600.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
450.00 | Supply and fixing stainless steel handrail of grade SS 304 made from 50mm diameter or any other size, 16 gauge thick round pipes, brush finish, with machine bent edges for snap fitting including stainless steel balusters and shoes including supply and fixing hand rail support using stainless steel flat with necessary fixing arrangement, preparation of hand railing design and installation drawings, all complete as per drawings and specifications. | 6000.00 | kg |  | 735.00 | 4410000.00 | 496.00 | 2976000.00 | 505.00 | 3030000.00 | 900.00 | 5400000.00 | 859.00 | 5154000.00 | 666.50 | 3999000.00 | 389.00 | 2334000.00 | 2334000.00 | Ocean Lifespaces India Private Limited
451.00 | Electrical Works
452.00 | Providing Construction Power supply to POLAR crane and Lighting network system
453.00 | Supply as per requirement, Installation, testing and commissioning of outdoor type 3-Ø Transformer of rating 1.6MVA, 11/0.400 KV, 50 HZ, +/- 7.5% OFF load tap changer suitable for feeding power supply to Polar crane along with all protection devices and necessary hardwares and accessories, confirming to latest edition of IS standard & as approved. Note: Tyepe of cooling - ONAN type scope includes Installation and assembly of loose items, transformer positioning, welding, all type of testing and commissioning etc, all as per specification mentioned in Technical specifications. (LT side termination cable box suitable for connecting 12 Nos - 3.5x400Sqmm aluminimum cable) | 2.00 | Nos. |  | 10034000.00 | 20068000.00 | 10696001.00 | 21392002.00 | 6237000.00 | 12474000.00 | 9035320.00 | 18070640.00 | 6173460.00 | 12346920.00 | 4650000.00 | 9300000.00 | 3457672.00 | 6915344.00 | 6915344.00 | Ocean Lifespaces India Private Limited
454.00 | Providing as per requirement, installation, testing and commissioning of LT Outdoor panel for ploar crane , working on 440V AC, 3-Phase & Neutral , 50Hz. It shall be extendable at both ends,copper bus bars , fully compartmentalized , dust-proof and vermin proof , 14/16 gauge, CRCA sheet steel enclosure, powder coated & along with necessary hardware’s and accessories and all as per specification , conforming to latest edition of relevant IS & as approved. (Incoming cable chamber Suitable for connecting 14nos,3.5Cx400Sqmm cable) Incomer: 3200A 4P 50KA EDO ACB with CT & PT, control fuses, ammeter, voltmeter and microprocessor numeric relay for transformer protection complete 1.6 MVA ONAN type transformer complete as per IS - 1 No. Bus bar - 3200A Cu, TPN tinned copper Busbar suitable for 50kA for 1 Sec. Outgoing Feeders: 630A TPN SFU -4Nos 400A TPN SFU -4Nos 250A TPN SFU -1No 100A TPN SFU - 1No Note: Scope includes installation of panel positioning in existing concrete pedestal, alignment, panel welding, painting, Bolt nut accessories and all as required at site and all as per specification. (rate for making concrete pedestal will be covered in relavent item) | 2.00 | Nos. |  | 3262500.00 | 6525000.00 | 2624493.00 | 5248986.00 | 4515923.00 | 9031846.00 | 3630000.00 | 7260000.00 | 4389180.00 | 8778360.00 | 5347500.00 | 10695000.00 | 3381753.00 | 6763506.00 | 5248986.00 | P AND C PROJECTS PRIVATE LIMITED
455.00 | Providing as per requirement, Installation, testing and commissioning of outdoor type 3-Ø Transformer of rating 1.6 MVA, 11/0.433 KV, 50 HZ, +/- 7.5% OFF load tap changer along with all protection devices and necessary hardwares and accessories, confirming to latest edition of IS standard & as approved. Note: Tyepe of cooling - ONAN type scope includes Installation and assembly of loose items, transformer positioning, welding, all type of testing and commissioning etc, all as per specification mentioned in Technical specifications. (LT side termination cable box suitable for connecting 12 Nos - 3.5x400Sqmm aluminimum cable) | 2.00 | Nos. |  | 10034000.00 | 20068000.00 | 10672927.00 | 21345854.00 | 6237000.00 | 12474000.00 | 9035320.00 | 18070640.00 | 6293333.00 | 12586666.00 | 4650000.00 | 9300000.00 | 3457672.00 | 6915344.00 | 6915344.00 | Ocean Lifespaces India Private Limited
456.00 | Providing as per requirement,installation and commissioning of LT Indoor Main construction power panel working on 440V 3-Phase & Neutral , 50Hz , AC . It shall be extendable at both ends,copper bus bars , fully compartmentalized , dust-proof and vermin proof , 14/16 gauge, CRCA sheet steel enclosure, powder coated & along with necessary hardware’s and accessories and all as per specification , conforming to latest edition of relevant , Bureau of Indian Standards & as approved. (Suitable for connecting 13nos,3.5Cx400Sqmm cable) Incomer : 2000A, 4P 50KA EDO ACB Microprocessor based LSIG Release , with S/C protection , adjustable , O/L & E/F release, with communication port RS 485, CTs with ammeter & selector switch and voltmeter & selector switch Indication lamps (LED type) and control fuses - 1 No. Bus bar - 2000A Cu, TPN tinned copper Busbar suitable for 50kA for 1 Sec Outgoing Feeders: 1.1250A 4P 50KA EDO ACB Microprocessor based LSIG Release, with S/C protection, adjustable , O/L & E/F release, with communication port RS 485 -2 Nos 2. 800A 4P 50KA EDO ACB Microprocessor based LSIG Release , with protection S/C, adjustable , O/L & E/F release, with communication port RS 485 -2 Nos. 3. 630A TPN SFU -2Nos, 4. 400A TPN SFU -2Nos; 5. 250A TPN SFU-1No ; 6.100A TPN SFU - 1No; Note : scope includes installation of panel positioning in existing support structure , alignment,panel welding,painting, Bolt nut accessories and all as required at site and all as per specification. (rate for making support structure will be covered in relevant item) | 2.00 | Nos. |  | 4060000.00 | 8120000.00 | 3315149.00 | 6630298.00 | 3063600.00 | 6127200.00 | 3267000.00 | 6534000.00 | 4706889.00 | 9413778.00 | 5208000.00 | 10416000.00 | 3879693.00 | 7759386.00 | 6127200.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
457.00 | Providing as per requirement,Installation and commissioning, of LT Outdoor Construction power weather proof panel working on 440V 3-Phase & Neutral ,50 Hz, AC Providing as per requirement confirming to IP 55. It shall be extendable at both ends, with copper bus bars, fully compartmentalized dust-proof and vermin proof, 14/16 gauge, CRCA sheet steel enclosure,powder coated & along with necessary hardware’s and accessories and all as per specification , conforming to latest edition of relevant IS & as approved. (Suitable for connecting 4nos,3.5Cx400Sqmm cable). Incomer-1 No : 1250A 4P 50KA EDO ACB Microprocessor based LSIG Release , with protection S/C, adjustable , O/L & E/F release, with communication port RS 485, CTs with ammeter & selector switch and voltmeter & selector switch ,frequency meter, Pf meter, Indication lamps ( LED type) and control fuses -1 No Bus bar - 1250A Cu, TPN tinned copper Busbar suitable for 50kA for 1 Sec Outgoing feeders : 630A TPN SFU with HRC fuses - 6 Nos 400A TPN SFU with HRC fuses - 5 Nos 250A TPN SFU with HRC fuses - 2 Nos 100A TPN SFU with HRC fuses - 2Nos 63A TPN SFU with HRC fuses - 2 Nos Note: Scope includes installation of panel positioning in existing concrete pedastal / support structure ,alignment,panel welding,painting,hardware accessories and all as required at site and all as per specification. (making concrete pedastal / support structure will be covered in relevant item) | 2.00 | Nos. |  | 2624500.00 | 5249000.00 | 1971731.00 | 3943462.00 | 1949216.00 | 3898432.00 | 3267000.00 | 6534000.00 | 3439546.00 | 6879092.00 | 3487500.00 | 6975000.00 | 2405968.00 | 4811936.00 | 3898432.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
458.00 | Providing as per requirement, Installation and commissioning 320 KVA DG set along with Standard Manual control Panel & all Standard Accessories & acoustic Enclosure as per latest CPCB-IV Norms. Note : Scope includes, 1.550 Ltrs day tank capacity for diesel 2.exhaust piping outside the accoustic enclosure 3.ventilation duct 4.fuel pipe line and all other required accessories. 5.power and control cabling b/w Alternator and DG panel, DG panel to buyer PCC 6. DG set body earthing and DG neutral earthing. 7. Freight,Insurance and unloading. 8. Suggested Make : Crompton/Cummins/leroy somer or equivalent. positioning at Location, assembling, alignment,laying of disel pipe line , anchor fastner for support erection, welding etc all as per specification. (Making foundation for DG set will be covered in relevant item) | 2.00 | sets |  | 5583443.00 | 11166886.00 | 10129812.00 | 20259624.00 | 9034583.00 | 18069166.00 | 5505500.00 | 11011000.00 | 5361021.00 | 10722042.00 | 5425000.00 | 10850000.00 | 3323697.00 | 6647394.00 | 6647394.00 | Ocean Lifespaces India Private Limited
459.00 | Providing maintenance and support as directed by EIC along with one new standalone copy, single user perpetual license of 300 bus capability Electrical Transient Analysis Program (ETAP) software compatible with Windows 10 pro or latest version, with one Year of free upgrade and technical Support of following component modules
460.00 | Base Package- Equipment Evaluation, Cable Ampacity and Sizing (IEEE, NEC) Load Flow / Voltage Drop, Panel Studies and Single Phase Systems, Short-Circuit (ANSI / IEC), Arc Flash (IEEE 1584 / NFPA70E), Motor Acceleration - Dynamic / Static, Load Analyzer, Harmonics | 1.00 | Nos. |  | 2204000.00 | 2204000.00 | 1477882.00 | 1477882.00 | 2874534.00 | 2874534.00 | 200000.00 | 200000.00 | 2637404.00 | 2637404.00 | 93000.00 | 93000.00 | 167469.00 | 167469.00 | 93000.00 | VRC Constructions (India) Limited
461.00 | Cable Capacity, Sizing and Shock Protection (IEC 60502 and IEC 60364), Star - Protective Device Coordination and Sequence of Operation, Ground Grid Systems, DC Short Circuit, DC Arc Flash, DC Load Flow, Unbalanced AC Short Circuit (ANSI, IEC) | 1.00 | Nos. |  | 1522500.00 | 1522500.00 | 1477882.00 | 1477882.00 | 2832768.00 | 2832768.00 | 200000.00 | 200000.00 | 2763792.00 | 2763792.00 | 93000.00 | 93000.00 | 167469.00 | 167469.00 | 93000.00 | VRC Constructions (India) Limited
462.00 | Transient Stability, User-Defined Dynamic Models, Generator Start-Up | 1.00 | Nos. |  | 1522500.00 | 1522500.00 | 323287.00 | 323287.00 | 2959959.00 | 2959959.00 | 200000.00 | 200000.00 | 2857249.00 | 2857249.00 | 93000.00 | 93000.00 | 111646.00 | 111646.00 | 93000.00 | VRC Constructions (India) Limited
463.00 | Unbalanced load flow, contingency analysis, data Import / Export from MS Excel. | 1.00 | Nos. |  | 725000.00 | 725000.00 | 461839.00 | 461839.00 | 1181603.00 | 1181603.00 | 200000.00 | 200000.00 | 1596137.00 | 1596137.00 | 93000.00 | 93000.00 | 55824.00 | 55824.00 | 55824.00 | Ocean Lifespaces India Private Limited
464.00 | Providing as per requirement,Installation,testing and commissioning of LT Indoor Auto Change Over Panel working on 440V 3-Phase & Neutral ,50 Hz, AC Providing as per requirement . It shall be extendable at both ends, with copper bus bars, fully compartmentalized dust-proof and vermin proof, 14/16 gauge, CRCA sheet steel enclosure and powder coated . DG side Panel with protection microprocessor based combined instantaneous O/L,REF relay,Earth Fault relay ,suitable size of CTs and Provision for auto change over to DG Providing as per requirement within 0 to 60sec suitable for 320KVA DG, if EB side power failure. EB side Panel protection with microprocessor based combined instantaneous O/L & E/F relay with suitable size of CTs and all as per specification and drawing conforming to latest edition of relevant Indian Standards & as approved. incommer -1 EB supply : 800A 4P 50KA EDO ACB Microprocessor based LSIG Release , with protection S/C, adjustable , O/L & E/F release, with communication port RS 485, CTs with ammeter & selector switch and voltmeter & selector switch ,frequency meter, Pf meter, Indication lamps ( LED type) and control fuses - 1 No (Suitable for connecting 2nos,3.5Cx400Sqmm cable) incomer -2 DG supply : 800A 4P 50KA EDO ACB Microprocessor based LSIG Release , with protection S/C, adjustable , O/L & E/F release, with communication port RS 485, CTs with ammeter & selector switch and voltmeter & selector switch ,frequency meter, Pf meter, Indication lamps ( LED type) and control fuses - 1 No (Suitable for connecting 2nos,3.5Cx400Sqmm cable) ; Bus bar 800A Cu, TPN tinned copper - 50kA for 1 Sec Provision for outgoing Busbar termination suitable for 3Rx 3.5Cx400Sqmm AL cable. Scope includes installation of panel positioning in place,alignment,panel weding, painting,hardware accessories,panel welding and all as required at site and all as per specification. | 2.00 | Nos. |  | 1522500.00 | 3045000.00 | 801894.00 | 1603788.00 | 1148850.00 | 2297700.00 | 1888000.00 | 3776000.00 | 1567895.00 | 3135790.00 | 1410500.00 | 2821000.00 | 1139904.00 | 2279808.00 | 1603788.00 | P AND C PROJECTS PRIVATE LIMITED
465.00 | Providing as per requirement, Installation and commissioning of 3-Ø, 425 KVAR, 415 V,50 Hz Microprocessor based Automatic Power Factor Controller (APFC) panel with all protections as per relevant IS and all as per specifications. Requirements: 1.No.of stages - 9 Stages ( 9x 50 KVAr ) 2.Type of enclosure- Powder coated steel enclosure IP55. 3.Dimensions of the panel is approximately (800x1600x400) mm (WXHXD) 4.Ventilation - Forced Ventilation . (making concrete pedastal / support structure will be covered in relevant item) | 2.00 | Nos. |  | 1531200.00 | 3062400.00 | 1693024.00 | 3386048.00 | 1187145.00 | 2374290.00 | 1099000.00 | 2198000.00 | 1879759.00 | 3759518.00 | 1798000.00 | 3596000.00 | 1017876.00 | 2035752.00 | 2035752.00 | Ocean Lifespaces India Private Limited
466.00 | Providing as per requirement, installation and commissioning of LT Indoor Sub Constructtion power panel working on 440V 3-Phase & Neutral , 50Hz , AC. It shall be extendable at both ends,copper bus bars , fully compartmentalized, dust-proof and vermin proof , 14/16 gauge, CRCA sheet steel enclosure,powder coated & along with necessary hardware’s and accessories and all as per specification , conforming to latest edition of relevant IS & as approved. Incomer : 630A TPN SFU with HRC fuse links,CTs with ammeter & selector switch and voltmeter & selector switch Indication lamps ( LED type) and control fuses - 1 No Bus bar : 630 A TPN + Tinned copper busbars suitable for 35kA for 1 sec. Outgoing feeders : 400A TPN SFU with HRC fuses - 3 Nos ; 250A TPN SFU with HRC Fuses - 2 Nos ; 100A TPN SFU with HRC Fuses - 2 Nos ; 63A TPN SFU with HRC fuses - 2 Nos ; Scope includes 1.installation of panel positioning in existing support structure, alignment,panel welding,painting,hardware accessories and all as required at site. 2.Shifting of panel (for polar crane) at 21mtrs elevation (UJA Building ) and Bolt nut accessories and all as required at site and all as per specification. (making concrete pedastal / support structure will be covered in relevant item) | 6.00 | Nos. |  | 1246826.00 | 7480956.00 | 556192.00 | 3337152.00 | 689310.00 | 4135860.00 | 1573000.00 | 9438000.00 | 1110234.00 | 6661404.00 | 1054000.00 | 6324000.00 | 485659.00 | 2913954.00 | 2913954.00 | Ocean Lifespaces India Private Limited
467.00 | Providing as per requirement,Installation and commissioning of LT Outdoor Main Lighting weather proof panel working on 440V 3-Phase & Neutral ,50 Hz, AC confirming to IP 55. It shall be extendable at both ends, with copper bus bars, fully compartmentalized dust-proof and vermin proof, 14/16 gauge, CRCA sheet steel enclosure,powder coated & along with necessary hardware’s and accessories and all as per specification , conforming to latest edition of relevant IS & as approved. (Suitable for connecting 3nos,3.5Cx400Sqmm cable). Incomer- 1 No : 800A 4P 50KA EDO ACB Microprocessor based LSIG Release , with protection S/C, adjustable , O/L & E/F release, with communication port RS 485, CTs with ammeter & selector switch and voltmeter & selector switch ,frequency meter, Pf meter, Indication lamps ( LED type) and control fuses - 1 No Bus bar - 800A Cu, TPN tinned copper Busbar suitable for 50kA for 1 Sec. Outgoing feeders : 400A TPN SFU with HRC fuses -4Nos 250A TPN SFU with HRC fuses - 6Nos 100A TPN SFU with HRC fuses - 4Nos 63A TPN SFU with HRC fuses - 2 Nos Note: Scope includes the installation of panel positioning in existing concrete pedastal / support structure ,alignment,panel welding,painting,hardware accessories and all as required at site and all as per specification. (making concrete pedastal / support structure will be covered in relevant item) | 2.00 | Nos. |  | 1377500.00 | 2755000.00 | 1200397.00 | 2400794.00 | 1531800.00 | 3063600.00 | 2723000.00 | 5446000.00 | 2144828.00 | 4289656.00 | 2247500.00 | 4495000.00 | 1356497.00 | 2712994.00 | 2400794.00 | P AND C PROJECTS PRIVATE LIMITED
468.00 | Providing as per requirement,installation and commissioning of LT Indoor Sub Lighting panel working on 440V 3-Phase & Neutral , 50Hz , AC. It shall be extendable at both ends,copper bus bars , fully compartmentalized , dust-proof and vermin proof , 14/16 gauge, CRCA sheet steel enclosure,powder coated & along with necessary hardware’s and accessories and all as per specification, conformi-ng to latest edition of relevant IS & as approved. Incomer : 400A TPN SFU with HRC fuse links,CTs with ammeter & selector switch and voltmeter & selector switch Indication lamps ( LED type) and control fuses - 1 No. Bus bar - 400 A TPN + Tinned copper busbars suitable for 35kA for 1 sec. Outgoing feeders : 250A TPN SFU with HRC fuses - 7Nos ; 100A TPN SFU with HRC Fuses - 1No ; 63A TPN SFU with HRC fuses - 1No; Note: Scope includes installation of panel positioning in existing support structure, alignment,panel welding,painting,hardware accessories and all as required at site and all as per specification. (rate for making support structure will be covered in relevant item) | 8.00 | Nos. |  | 640900.00 | 5127200.00 | 508518.00 | 4068144.00 | 555278.00 | 4442224.00 | 188800.00 | 1510400.00 | 650551.00 | 5204408.00 | 759500.00 | 6076000.00 | 449932.00 | 3599456.00 | 1510400.00 | DEE VEE PROJECTS LIMITED
469.00 | Providing as per requirement, installation and commissionig of LT Indoor Wall mounted Lighing panel working on 440V 3-Phase & Neutral , 50Hz , AC. It shall be extendable at both ends,copper bus bars , fully compartmentalized , dust-proof and vermin proof , 14/16 gauge, CRCA sheet steel enclosure, powder coated & along with necessary hardware’s and accessories and all as per specification , conforming to latest edition of relavant IS & as approved. Incomer: 1No.250A TPN SFU with HRC fuse links, Indication lamps (LED type) and control fuses - 1 No Bus bar : 250 A TPN + Tinned copper busbars suitable for 35kA for 1 sec. Outgoing feeders : 1.100A TPN Thermal magnetic MCCB with protection S/C, adjustable O/L and Earth fault release - 4 Nos ; 2.63A TPN Thermal magnetic MCCB with protection S/C, adjustable O/L and Earth fault release - 5 Nos; ; Scope includes installation of panel positioning in existing support structureo or wall by using Providing as per requirement of 4 nos of required Size anchor fastener ,alignment,panel welding,painting,hardware accessories and all as required at site and all as per specification. | 30.00 | Nos. |  | 311750.00 | 9352500.00 | 372832.00 | 11184960.00 | 381035.00 | 11431050.00 | 30250.00 | 907500.00 | 367624.00 | 11028720.00 | 658750.00 | 19762500.00 | 367314.00 | 11019420.00 | 907500.00 | DEE VEE PROJECTS LIMITED
470.00 | Fabrication, Supply, installation, testing and commissioning of wall mounted LT motor DOL stater panel working on 440V 3-Phase & Neutral , 50Hz , AC supply. It shall be extendable at ends, copper bus bars , fully compartmentalized , dust-proof and vermin proof , 14/16 gauge, CRCA sheet steel enclosure, powder coated & along with necessary hardwares and accessories and all as per specification, conforming to latest edition of relevant , Bureau of Indian Standards & as approved. Incomer : 400A TPN Thermal magnetic MCCB -1No Bus bar - 400A Cu, TPN tinned copper Busbar suitable for 50kA for 1 Sec Outgoing feeders : Feeder to DOL starter arrangement for 132KW Motor with required rating of CTs, OLR , contactor, LT motor protection relay, single phase preventor ,Voltmeter, ammeter, LED indication lamps, ON/OFFpush button, outgoing busbar arrangement for two separate cable connection and other hardware accessories etc scope includes installation of panel on wall/existing support structure, required size of anchnor fasteners Bolt nut accessories, panel alignment with existing panel, panel welding, painting, earth connection and all as required at site and all as per specification. | 4.00 | Nos. |  | 304935.00 | 1219740.00 | 293376.00 | 1173504.00 | 402098.00 | 1608392.00 | 30250.00 | 121000.00 | 277746.00 | 1110984.00 | 294500.00 | 1178000.00 | 274091.00 | 1096364.00 | 121000.00 | DEE VEE PROJECTS LIMITED
471.00 | LT Power and Control cables
472.00 | Providing as per requirement & laying the following sizes of 1100V grade XLPE insulated, galvanized steel armored, extruded PVC inner sheathed and outer Sheath Aluminium armoured cables conforming to IS 7098 (Part -1). Scope includes laying of following size of Al cable in excavated trench / Hume pipes/wall/support structure,using Lead rawl plugs for clamping of cable ,cable laying without any kinks and bend,etc and Installation heat shirnkable straight through kits if cable length is more than drum length and all as per specifications directed by EIC. (suggested makes : NICCO / Gloster / Universal satna / Torrent/Polycab/Havells or equivalent) Note: 1.Excavation and laying of bricks will be covered in relevant item.
473.00 | 3.5C x 400 Sqmm XLPE Aluminium Armoured Cable | 10000.00 | RM |  | 3712.00 | 37120000.00 | 2604.00 | 26040000.00 | 2973.00 | 29730000.00 | 2430.00 | 24300000.00 | 3364.00 | 33640000.00 | 2712.50 | 27125000.00 | 2446.00 | 24460000.00 | 24300000.00 | DEE VEE PROJECTS LIMITED
474.00 | 3.5C x 150 Sqmm XLPE Aluminium Armoured Cable | 5000.00 | RM |  | 1486.00 | 7430000.00 | 1100.00 | 5500000.00 | 1188.00 | 5940000.00 | 980.00 | 4900000.00 | 1403.00 | 7015000.00 | 1240.00 | 6200000.00 | 1056.00 | 5280000.00 | 4900000.00 | DEE VEE PROJECTS LIMITED
475.00 | 4C x 50 Sqmm XLPE Aluminium Armoured Cable | 5000.00 | RM |  | 674.00 | 3370000.00 | 513.00 | 2565000.00 | 607.00 | 3035000.00 | 440.00 | 2200000.00 | 601.00 | 3005000.00 | 558.00 | 2790000.00 | 452.00 | 2260000.00 | 2200000.00 | DEE VEE PROJECTS LIMITED
476.00 | 4C x 25 Sqmm XLPE Aluminium Armoured Cable | 5000.00 | RM |  | 392.00 | 1960000.00 | 342.00 | 1710000.00 | 332.00 | 1660000.00 | 250.00 | 1250000.00 | 348.00 | 1740000.00 | 341.00 | 1705000.00 | 272.00 | 1360000.00 | 1250000.00 | DEE VEE PROJECTS LIMITED
477.00 | 4C x 16 Sqmm XLPE Aluminium Armoured Cable | 9000.00 | RM |  | 297.00 | 2673000.00 | 281.00 | 2529000.00 | 261.00 | 2349000.00 | 195.00 | 1755000.00 | 273.00 | 2457000.00 | 248.00 | 2232000.00 | 219.00 | 1971000.00 | 1755000.00 | DEE VEE PROJECTS LIMITED
478.00 | 4C x 2.5 Sqmm XLPE Aluminium Armoured Cable | 1000.00 | RM |  | 139.00 | 139000.00 | 257.00 | 257000.00 | 114.00 | 114000.00 | 105.00 | 105000.00 | 153.00 | 153000.00 | 139.50 | 139500.00 | 118.00 | 118000.00 | 105000.00 | DEE VEE PROJECTS LIMITED
479.00 | Providing and laying as per requirement of 1100 V PVC insulated FRLS multi-strand flexible copper cable as per specifications. laying the cable using GI saddles, lead rawl plugs, spacer, screws and other consumables. Scope includes; 1.Providing of all consumables mentioned above,suitable Polyamide UV resistant glands of approved make, installation of Glands in looping JBs, LDB and fittings, termination of the cables in terminal blocks provided in the LDBs / JBs / Lighting fixtures using appropriate type of tinned copper lugs as per the specifications. 2.Laying of cables as per Engineer instructions with medium duty double compresion brass cable glands , Glanding and termination ,clamping of cable , suitable size copper Lugs, bolt / nut accessories etc, all as required at site , cable laying without any kinks and bend,etc and all as per specification .
480.00 | 3 C x 2.5 sq mm | 52790.00 | RM |  | 244.00 | 12880760.00 | 220.00 | 11613800.00 | 169.00 | 8921510.00 | 160.00 | 8446400.00 | 185.00 | 9766150.00 | 232.50 | 12273675.00 | 131.00 | 6915490.00 | 6915490.00 | Ocean Lifespaces India Private Limited
481.00 | 4 C x 2.5 sq mm | 3000.00 | RM |  | 287.00 | 861000.00 | 257.00 | 771000.00 | 229.00 | 687000.00 | 220.00 | 660000.00 | 231.00 | 693000.00 | 279.00 | 837000.00 | 177.00 | 531000.00 | 531000.00 | Ocean Lifespaces India Private Limited
482.00 | 5 C x 2.5 sq mm | 3000.00 | RM |  | 326.00 | 978000.00 | 318.00 | 954000.00 | 302.00 | 906000.00 | 270.00 | 810000.00 | 287.00 | 861000.00 | 348.75 | 1046250.00 | 220.00 | 660000.00 | 660000.00 | Ocean Lifespaces India Private Limited
483.00 | Providing and laying of 3C x 150 Sqmm,11KV grade 3 Core Aluminium armoured cable in already excavated cable trenches, RCC hume pipes,cable covered by cement slab and testing ,commissioning of the above cables. Scope includes clamping, laying of cable without any kinks and bend and all as per specification. (Excavation will be covered in relevant item) | 1000.00 | RM |  | 2320.00 | 2320000.00 | 2611.00 | 2611000.00 | 1437.00 | 1437000.00 | 1530.00 | 1530000.00 | 2673.00 | 2673000.00 | 1860.00 | 1860000.00 | 1586.00 | 1586000.00 | 1437000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
484.00 | Providing and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for 3Cx150 Sq.mm 11KV XLPE Aluminium armed concuctor cable. | 20.00 | Nos. |  | 1958.00 | 39160.00 | 2029.00 | 40580.00 | 18525.00 | 370500.00 | 35000.00 | 700000.00 | 28126.00 | 562520.00 | 9300.00 | 186000.00 | 8597.00 | 171940.00 | 39160.00 | JATAN CONSTRUCTIONS PVT LTD
485.00 | Glanding and termination of following size Aluminium armoured Cables. Scope includes Providing as per requirement and installation of double compresion heavy duty brass cable gland with nickel plated and suitable size Aluminium Lugs,connection,bolt nut accessories etc, and all as required at site and all as per specification.
486.00 | 3.5C x400 Sqmm XLPE Aluminium Armoured Cable | 200.00 | Nos. |  | 5075.00 | 1015000.00 | 3300.00 | 660000.00 | 5393.00 | 1078600.00 | 1720.00 | 344000.00 | 8915.00 | 1783000.00 | 4185.00 | 837000.00 | 3965.00 | 793000.00 | 344000.00 | DEE VEE PROJECTS LIMITED
487.00 | 3.5C x150 Sqmm XLPE Aluminium Armoured Cable | 20.00 | Nos. |  | 1958.00 | 39160.00 | 1589.00 | 31780.00 | 2889.00 | 57780.00 | 1450.00 | 29000.00 | 4187.00 | 83740.00 | 1937.50 | 38750.00 | 1753.00 | 35060.00 | 29000.00 | DEE VEE PROJECTS LIMITED
488.00 | 4C x50 Sqmm XLPE Aluminium Armoured Cable | 70.00 | Nos. |  | 1523.00 | 106610.00 | 978.00 | 68460.00 | 1416.00 | 99120.00 | 600.00 | 42000.00 | 2326.00 | 162820.00 | 1085.00 | 75950.00 | 1040.00 | 72800.00 | 42000.00 | DEE VEE PROJECTS LIMITED
489.00 | 4C x25 Sqmm XLPE Aluminium Armoured Cable | 150.00 | Nos. |  | 1523.00 | 228450.00 | 856.00 | 128400.00 | 915.00 | 137250.00 | 400.00 | 60000.00 | 1636.00 | 245400.00 | 775.00 | 116250.00 | 906.00 | 135900.00 | 60000.00 | DEE VEE PROJECTS LIMITED
490.00 | 4C x16 Sqmm XLPE Aluminium Armoured Cable | 350.00 | Nos. |  | 1233.00 | 431550.00 | 672.00 | 235200.00 | 675.00 | 236250.00 | 400.00 | 140000.00 | 1485.00 | 519750.00 | 697.50 | 244125.00 | 826.00 | 289100.00 | 140000.00 | DEE VEE PROJECTS LIMITED
491.00 | 4C x 2.5 Sqmm XLPE Aluminium Armoured Cable | 50.00 | Nos |  | 1233.00 | 61650.00 | 306.00 | 15300.00 | 590.00 | 29500.00 | 400.00 | 20000.00 | 659.00 | 32950.00 | 542.50 | 27125.00 | 391.00 | 19550.00 | 15300.00 | P AND C PROJECTS PRIVATE LIMITED
492.00 | 5C x150 Sqmm copper Un Armoured Cable | 5.00 | Nos. |  | 1233.00 | 6165.00 | 5347.00 | 26735.00 | 2880.00 | 14400.00 | 27960.00 | 139800.00 | 8263.00 | 41315.00 | 2325.00 | 11625.00 | 4132.00 | 20660.00 | 6165.00 | JATAN CONSTRUCTIONS PVT LTD
493.00 | Erection of supports for cable trays as per NPCIL requirement for laying of cable on external vertical walls of buildings suit to site. Scope includes erection of Fabricated supports of 1 meter length at every 0.75 meter interval by using suitable size of anchor fasteners, providing clamps for cabling, scaffolding arrangement for erection up to 25 m elevation, all safety precautions, welding, cutting / drilling, painting with single coat of red oxide primer & double coats of silver enamel paint, Providing necessary hardware as per specification or as directed by EIC. Note: 1. Payment will be made for No. of vertical supports installed. 2. Supply of cable and laying is covered under relevant item | 500.00 | Nos. |  | 2175.00 | 1087500.00 | 3650.00 | 1825000.00 | 1439.00 | 719500.00 | 1460.00 | 730000.00 | 3596.00 | 1798000.00 | 620.00 | 310000.00 | 3908.00 | 1954000.00 | 310000.00 | VRC Constructions (India) Limited
494.00 | Providing as per requirement and installation of 300mmx300mmx150mm size Hot dip GI junction boxes with 8 nos of 25 Sqmm size ring type terminal blocks with mounting rail (Ring type) for incomming and outgoing cable connections, bothside provide earth connetion for external earth connection and knock out opening etc. Note : scope includes installation of JBs with suitable anchor fasteners,bolt nut accessories,welding of existing support etc, all as required at site and all as per specification. | 100.00 | Nos. |  | 8065.00 | 806500.00 | 15866.00 | 1586600.00 | 3135.00 | 313500.00 | 29950.00 | 2995000.00 | 2997.00 | 299700.00 | 1085.00 | 108500.00 | 1955.00 | 195500.00 | 108500.00 | VRC Constructions (India) Limited
495.00 | Providing and installation as per requirement of thermoplastic junction boxes with dimensiones 135x115x70mm (suggested makes:Hensel / Spelsburg/ OBO / Scame or equivalent ) suitable for terminating the cables up to 4 sq.mm mounted inside the box. Terminal block shall be of Connectwell/ WAGO / ELMEX / Phonex make mounted on C-channel with end plates / clamps along with including providing and installation of anchor fastener of approved make and all other hardware required for completing the job in all respect on all types of walls / ceilings etc.
496.00 | 10 Numbers terminal blocks for 3- phase | 4500.00 | Nos. |  | 3118.00 | 14031000.00 | 4632.00 | 20844000.00 | 1547.00 | 6961500.00 | 2400.00 | 10800000.00 | 6615.00 | 29767500.00 | 542.50 | 2441250.00 | 1374.00 | 6183000.00 | 2441250.00 | VRC Constructions (India) Limited
497.00 | 6 Numbers terminal blocks for 1- phase | 1500.00 | Nos. |  | 2393.00 | 3589500.00 | 4388.00 | 6582000.00 | 1125.00 | 1687500.00 | 1820.00 | 2730000.00 | 6615.00 | 9922500.00 | 387.50 | 581250.00 | 1308.00 | 1962000.00 | 581250.00 | VRC Constructions (India) Limited
498.00 | Lighting related works
499.00 | Providing and installation as per requirement of LED street light luminaries including design of 11 m height Hot dip galvanised Octagonal pole with bottom 210mm A/F, top 90mm A/F made of 3mm think HT sheet steel plate along with 300x300x20mm base plate, 1500mm long single arm bracket, Foundation Bolts, back lite street with 1no NS type HRC fuse base & fuse holder and 2A HRC fuse links, for LILO cable termination complete all as per specification. Next generation LED Street light with pressure die-cast housing, high performance polycarbonate optics and IP 66 ingress protection.4 kV inbuilt surge protection with top opening driver cover for easy maintenance. Note: 1.Casting of RCC foundation for street light poles will be covered in relvant item. 2.scope includes black Bitumen paint of concrete as per specification, painting of poles with single coat of Aluminum paint, pole numbering, supply and Laying 3Cx1.5 Sqmm 1100 V grade PVC insulated FR multistrand copper flexiable cables -15 mtrs, supply and installation of 1Mtr length 100 mm GI bend pipe for cable entry all as per specification 3.Sueggested Make: Philips / Bajaj / Crompton greaves / GE / Osram/Wipro/Havells or equivalent. 4.Installation of street light fitting on fabricated street light bracket which is to be fixed on wall including providing of 4 nos of 6 mm anchor fasteners. Contractor has to Provide the materials and anchor fasteners as per the NPCIL approved make and type. (fabrication of street light bracket single/double ,excavation of poles pits in any type of soil / dis intgrated rock/PCC/shuttering work/ RCC concreting with M-20 mix will be covered in relavant item)
500.00 | 4000 lumens (100 lm/watt) with CCT 5700 K | 150.00 | Nos. |  | 61625.00 | 9243750.00 | 89603.00 | 13440450.00 | 79575.00 | 11936250.00 | 33370.00 | 5005500.00 | 79355.00 | 11903250.00 | 38750.00 | 5812500.00 | 39936.00 | 5990400.00 | 5005500.00 | DEE VEE PROJECTS LIMITED
501.00 | 8000 lumens (100 lm/watt) with CCT 5700 K | 110.00 | Nos. |  | 76350.00 | 8398500.00 | 93351.00 | 10268610.00 | 86129.00 | 9474190.00 | 34230.00 | 3765300.00 | 83442.00 | 9178620.00 | 43400.00 | 4774000.00 | 41299.00 | 4542890.00 | 3765300.00 | DEE VEE PROJECTS LIMITED
502.00 | Providing and installation as per requirement of LED well glass luminaries with minimum 4000 lumens as per the specifications given in Technical specifications. Suggested Make: Philips / Bajaj / Crompton greaves / GE / Osram/Wipro/Havells or equivalent. scope includes providing and Installation of of wellglass light fitting using 1 no of 6 mm hook type / bolt type anchor fastener as per the specifications. | 350.00 | Nos. |  | 12325.00 | 4313750.00 | 3396.00 | 1188600.00 | 19020.00 | 6657000.00 | 6500.00 | 2275000.00 | 6458.00 | 2260300.00 | 4650.00 | 1627500.00 | 2200.00 | 770000.00 | 770000.00 | Ocean Lifespaces India Private Limited
503.00 | Providing and installation as per requirement of LED bulk head luminaries with minimum 4000 lumens as per the specifications given in Technical specifications. Suggested Make: Philips / Bajaj /Crompton greaves / GE / Osram/Wipro/ Havells or equivalent . including providing and Installation of of wellglass light fitting using 2 nos of 6 mm hook type / bolt type anchor fastener as per the specifications. | 500.00 | Nos |  | 1523.00 | 761500.00 | 1691.00 | 845500.00 | 19019.00 | 9509500.00 | 1800.00 | 900000.00 | 4966.00 | 2483000.00 | 2480.00 | 1240000.00 | 1061.00 | 530500.00 | 530500.00 | Ocean Lifespaces India Private Limited
504.00 | Providing and installation as per requirement of LED Flood Light luminaries with 1.superior poly carbonate optics, pressure die cast housing along with IP 66 ingress protection. 2. 4 kV in-built surge protection. 3. Efficacy is 110 lm/watt and minimum 5500 lumens as per specifications given in technical specifications. Make: Philips / Bajaj / Crompton greaves / GE / Osram/Wipro/Havells. including providing and Installation of fitting using 2 nos of 6 mm anchor fastener as per the specifications. | 120.00 | Nos. |  | 13775.00 | 1653000.00 | 11762.00 | 1411440.00 | 23993.00 | 2879160.00 | 6500.00 | 780000.00 | 8283.00 | 993960.00 | 7750.00 | 930000.00 | 2647.00 | 317640.00 | 317640.00 | Ocean Lifespaces India Private Limited
505.00 | Providing and installation as per requirement of seven compartment 3-Ø, 4 way Lighting Distribution board with IP 42 protection and following components of approved make. 1. 1 no. of 4 pole 63 A MCB as incomer 2. 5 Numbers of 25 sqmm terminal blocks for incomer cable connection 3. 3 nos of 32A, 100 mA 230 V double pole RCCB for each phase ( 3 nos) 4. 4 nos of 1 ph 230 V and 10A MCB (single pole) per phase for outgoing supply. (total 12 nos of MCBs) along with all accessories such as insulated copper bus bars, neutral link & earth bus bars, supporting insulators, inner plates. Installation of the components inside the LDB in total as per the Technical Specification. Scope: The scope of work includes, fixing of brackets with anchor fasteners (4 nos x 6 mm) drilling the holes, installation of LDBs on the brackets with nut & bolt as per the tech specifications and as per the drawings given in the tender. The LDB shall be earthed to nearest Earth main grid. | 100.00 | Nos. |  | 26825.00 | 2682500.00 | 62342.00 | 6234200.00 | 38333.00 | 3833300.00 | 50000.00 | 5000000.00 | 58825.00 | 5882500.00 | 14260.00 | 1426000.00 | 26461.00 | 2646100.00 | 1426000.00 | VRC Constructions (India) Limited
506.00 | Earthing and Grounding related works
507.00 | Providing as per requirement and installation of 40 mm dia MS rod - 3 mtr long, directly driven into the earth, Hole should be filled with bendonite powder. Scope includes welding connection between the rod and earth flat, welding area painting, 2X2 feet RCC concrete chamber with top cover for earth pit, painting of earth pit chamber,identification and all as per specification. (Excavation will be covered in relevant items separately) | 60.00 | Nos. |  | 7975.00 | 478500.00 | 34434.00 | 2066040.00 | 19125.00 | 1147500.00 | 20000.00 | 1200000.00 | 23079.00 | 1384740.00 | 6200.00 | 372000.00 | 12840.00 | 770400.00 | 372000.00 | VRC Constructions (India) Limited
508.00 | Providing as per requirement and installation of 40 mm MS rod Horizontally in the earth at a depth of 500 mm from the ground level. Scope includes connection between the rods in trenches and earth flats will be done with welding and all as per specification,drawings. (Excavation will be covered in relevant items separately) | 450.00 | RM |  | 12325.00 | 5546250.00 | 2035.00 | 915750.00 | 1425.00 | 641250.00 | 14000.00 | 6300000.00 | 1514.00 | 681300.00 | 1240.00 | 558000.00 | 1308.00 | 588600.00 | 558000.00 | VRC Constructions (India) Limited
509.00 | Providing and installation of Test link boxes using 4 nos. of 6/8 mm dia anchor fasteners for Earthing / Lightning Protection System. Hot dip galvanised Test link boxes with test links for grounding/lightning protection system as per the tender specifications. The work shall be complete in all respects as per relevant documents, working drawings/tender specifications, relevant standards and practices and as directed by the Engineer. Scope includes Providing as per requirement and installation of all the welding/brazing consumables, anchor fasteners, bimettalic washers, hot dip galvanised hardware required to complete the job in all respects. Tinned Copper conductor coming from the outdoor grounding grid/indoor ground shall be brazed on copper strip of test link box and 12/10 mm GI rod coming from roof shall be welded/exothermically jointed to steel strip of test link box and both the strips has to be linked with copper link, consumables required for the brazing & welding as described above, requirement & application of anti - corrosive paint over brazed / welded joint.
510.00 | approximate size 250 x 200 x 180 mm size or as per drawing | 410.00 | Nos. |  | 5075.00 | 2080750.00 | 6920.00 | 2837200.00 | 1788.00 | 733080.00 | 5300.00 | 2173000.00 | 15701.00 | 6437410.00 | 2480.00 | 1016800.00 | 1731.00 | 709710.00 | 709710.00 | Ocean Lifespaces India Private Limited
511.00 | Providing and Installation of GI Flats / strips - hot dip galvanized with DFT 120 micron on the floor / wall / ceiling as per the technical specifications / drawings . Steel shall be Grade A (IS 2062) and as directed by the Enginner and fixing the flats using NPCIL approved anchor fasteners of size 6mm / 8 mm per every meter length. The Scope includes,wherever GI flat is to be installed over floor, the corresponding area , as directed by the Engineer shall be chipped to install the flat in flush with floor surface and the chipped area shall be restored with appropriate white cement mixture. it also includes the providing as per requirement & arrangements of hardware accessories such as nut & bolt, anchor fastners , welding consumables for welding the earth flats together, testing,anticorosive paint, applying touch up paint on the welded area for earthing/lightning protection system or for providing earthing to light channels/ marshalling junction boxes/ multiplexers/control panel/work station to the nearest earth Pads/Conductoretc.. to complete the installation works. Job involves working at higher elevations and the Contractor has to arrange approach platforms/sling arrangement & strict supervision.
512.00 | 75X10 mm GI Flat | 500.00 | RM |  | 1958.00 | 979000.00 | 1154.00 | 577000.00 | 751.00 | 375500.00 | 1000.00 | 500000.00 | 1422.00 | 711000.00 | 930.00 | 465000.00 | 922.00 | 461000.00 | 375500.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
513.00 | 50X10 mm GI Flat | 500.00 | RM |  | 1305.00 | 652500.00 | 799.00 | 399500.00 | 500.00 | 250000.00 | 880.00 | 440000.00 | 1155.00 | 577500.00 | 620.00 | 310000.00 | 621.00 | 310500.00 | 250000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
514.00 | 50X6 mm GI Flat | 4000.00 | RM |  | 783.00 | 3132000.00 | 531.00 | 2124000.00 | 300.00 | 1200000.00 | 470.00 | 1880000.00 | 670.00 | 2680000.00 | 372.00 | 1488000.00 | 386.00 | 1544000.00 | 1200000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
515.00 | 40 X 4 mm GI Flat | 12300.00 | RM |  | 418.00 | 5141400.00 | 435.00 | 5350500.00 | 160.00 | 1968000.00 | 310.00 | 3813000.00 | 434.00 | 5338200.00 | 232.50 | 2859750.00 | 198.00 | 2435400.00 | 1968000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
516.00 | 25x4 mm GI Flat | 5000.00 | RM |  | 261.00 | 1305000.00 | 286.00 | 1430000.00 | 100.00 | 500000.00 | 160.00 | 800000.00 | 303.00 | 1515000.00 | 131.75 | 658750.00 | 129.00 | 645000.00 | 500000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
517.00 | 75x12 mm GI Flat | 200.00 | RM |  | 2433.00 | 486600.00 | 1357.00 | 271400.00 | 901.00 | 180200.00 | 240.00 | 48000.00 | 2157.00 | 431400.00 | 1116.00 | 223200.00 | 1151.00 | 230200.00 | 48000.00 | DEE VEE PROJECTS LIMITED
518.00 | 40x5 mm GI Flat | 1000.00 | RM |  | 577.00 | 577000.00 | 435.00 | 435000.00 | 200.00 | 200000.00 | 240.00 | 240000.00 | 561.00 | 561000.00 | 248.00 | 248000.00 | 273.00 | 273000.00 | 200000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
519.00 | 25x5 mm GI Flat | 1000.00 | RM |  | 336.00 | 336000.00 | 286.00 | 286000.00 | 125.00 | 125000.00 | 240.00 | 240000.00 | 387.00 | 387000.00 | 155.00 | 155000.00 | 198.00 | 198000.00 | 125000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
520.00 | Providing and Installation of 12 mm dia Galvanized Iron (G.I.) rod with min. galvanisation thickness of 120 microns on the roof and outside the building and for vertical risers or wall / floor crossings inside the building as directed by the Engineer for earthing/lightning protection system.For lightning protection system. The rod shall be cut, bend ,welded, painted with anti corrosive paints suitable for out door application in the welded joints, clamping on the wall ,clamping on the concrete block on the roof top, fixing with GI clamps till connection by welding of GI rod to test link boxes .Also protruding conductors from wall are to be welded to the nearest down conductors. All the hardwares/anchor fastners , electorde for welding, accessories , and consumables required for erection as per lay out drawing are in the scope of contractors. Scope: 1.includes fabrication, welding, testing, installation, painting (including supply of paint) ,clamps, saddles, spacers,conductor holder ,supports of hot dip galvanised/FRP/SMC , providing clamps for fixing 12 MM G.I rod on wall and on roof of the buildings as indicated in the drawings. 2. supply and fixing in position Concrete Blocks of size ~ 200 X 200 X100 mm M30 grade with cement content 350kg per cu.m, at all levels and locations as per drawing for install the 12 mm GI rod on the roof top.
521.00 | 12 mm dia | 10000.00 | RM |  | 993.00 | 9930000.00 | 264.00 | 2640000.00 | 195.00 | 1950000.00 | 350.00 | 3500000.00 | 357.00 | 3570000.00 | 186.00 | 1860000.00 | 102.00 | 1020000.00 | 1020000.00 | Ocean Lifespaces India Private Limited
522.00 | 10 mm dia | 1000.00 | RM |  | 812.00 | 812000.00 | 202.00 | 202000.00 | 150.00 | 150000.00 | 330.00 | 330000.00 | 291.00 | 291000.00 | 139.50 | 139500.00 | 71.00 | 71000.00 | 71000.00 | Ocean Lifespaces India Private Limited
523.00 | Providing and Installation of MS Rod (ISRO-10) in the floors as a equipotentional conductor. The rod shall be cut, bend ,welded. Also protruding conductors from wall are to be welded to the nearest down conductors. All the hardwares/anchor fastners, providing clamps every meter electorde for welding, accessories , and consumables required for erection as per lay out drawing are in the scope of contractors. Scope includes fabrication, welding and installation of the same as per tender specifications.
524.00 | 10mm dia | 12000.00 | RM |  | 508.00 | 6096000.00 | 182.00 | 2184000.00 | 150.00 | 1800000.00 | 320.00 | 3840000.00 | 254.00 | 3048000.00 | 108.50 | 1302000.00 | 71.00 | 852000.00 | 852000.00 | Ocean Lifespaces India Private Limited
525.00 | Providing and installation of bare tinned Copper conductor to be laid over the PCC and below the water proofing, vertical risers of the wall . The formation grid/ mesh shall be as per layout drawings.The necessary arrangements required to intact placing of mesh in its position before water proofing made to avoid displacement of conductors. The joints made for formation grid shall be through exo thermic weldings and the joints should be qualified with resistance measurement. The risers from the different locations around buidlings as per drawnngs are to be brought to the ground level through pvc pipes/or any other methods as per WD with required clampings. The risers brought to ground level should have sufficent length for termination in test link boxes and ensure that risers should be free from cement slurry and loose strands. The clamps and hardwares used for erection purpose should be cadmium coated type. The scope also includes measuremnt of weld resistance with Micro ohm meter and Mould and kits/consumables used for straight joints/T joints/X joints for exo thermic welding of conductors in line with the IEEE- 837 and NPCIL approved make. The exotheric welding required for stright joints/X-joints/T- joints or in case brazing required depends upon the field conditions are to be carried out under the scope of this work.
526.00 | 70 sq.mm | 4850.00 | RM |  | 1668.00 | 8089800.00 | 2329.00 | 11295650.00 | 1475.00 | 7153750.00 | 3400.00 | 16490000.00 | 1667.00 | 8084950.00 | 1085.00 | 5262250.00 | 1105.00 | 5359250.00 | 5262250.00 | VRC Constructions (India) Limited
527.00 | Providing and installation of bare tinned Copper conductor, for outdoor grounding grid including materials / accessories required for the exothermic welding of grounding conductor joints and brazing in case of interconnection with test link boxes / flats. Laying of tinned copper conductor at a depth of not less than 0.5 m from the ground level and compacting of the soil after backfilling. The scope includes levelling and filling soft soil below the conductor to prevent any damage to the grounding conductors. All the above jobs shall be carried out as per the relevant working drawings/tender specifications, standards and practices and as directed by the Engineer. All the required consumables for exothermic welding & brazing activity, such as test joints for welds/brazing, welding/brazing equipments, electrodes, all required hardware have to provided by the contractor. The qualification of the welding/brazing, welder/brazer is also included in the scope.supply & application of anti- corrosive paint is also included in the scope of the above works for its application over the condcutor joints, where tinned coating will be lost on account of welding / brazing. (The scope of excavation will be covered in relevant item)
528.00 | 70 sq.mm | 19000.00 | RM |  | 1958.00 | 37202000.00 | 2329.00 | 44251000.00 | 1332.00 | 25308000.00 | 1500.00 | 28500000.00 | 1677.00 | 31863000.00 | 1085.00 | 20615000.00 | 1106.00 | 21014000.00 | 20615000.00 | VRC Constructions (India) Limited
529.00 | 95 sq.mm | 500.00 | RM |  | 2741.00 | 1370500.00 | 3133.00 | 1566500.00 | 1743.00 | 871500.00 | 2400.00 | 1200000.00 | 2230.00 | 1115000.00 | 1395.00 | 697500.00 | 1378.00 | 689000.00 | 689000.00 | Ocean Lifespaces India Private Limited
530.00 | 185 sq mm | 200.00 | RM |  | 12325.00 | 2465000.00 | 5971.00 | 1194200.00 | 3377.00 | 675400.00 | 12000.00 | 2400000.00 | 4076.00 | 815200.00 | 2945.00 | 589000.00 | 2669.00 | 533800.00 | 533800.00 | Ocean Lifespaces India Private Limited
531.00 | As per NPCIL requirement Providing and installation of bare tinned flexible Copper multistranded conductor for indoor equipment / pipe line / Metal structure earthing :Installation, Site testing & termination of grounding grid conductor including supply & installation of suitable solderless tinned copper lugs with suitable washers at both ends , clamping the coductor by suitable material of Purchaser approved make for grounding of equipment / panel / motor body / any other structure etc.. as directed by the Purchaser. The scope also includes supply of hardware and clamping accessories, drilling of holes in the nearby gounding flat / strip for connecting the flexible with suitable nut & bolts and bi-metallic washers etc..as recommended by the Purchaser. The length of flexible connection around 0.75 m - 1.5 m.
532.00 | 70 sq. mm | 200.00 | Nos. |  | 1523.00 | 304600.00 | 2008.00 | 401600.00 | 1290.00 | 258000.00 | 400.00 | 80000.00 | 1948.00 | 389600.00 | 1085.00 | 217000.00 | 391.00 | 78200.00 | 78200.00 | Ocean Lifespaces India Private Limited
533.00 | 35 sq. mm | 250.00 | Nos. |  | 945.00 | 236250.00 | 903.00 | 225750.00 | 641.00 | 160250.00 | 280.00 | 70000.00 | 1259.00 | 314750.00 | 589.00 | 147250.00 | 257.00 | 64250.00 | 64250.00 | Ocean Lifespaces India Private Limited
534.00 | 16 sq. mm | 500.00 | Nos. |  | 365.00 | 182500.00 | 622.00 | 311000.00 | 328.00 | 164000.00 | 470.00 | 235000.00 | 867.00 | 433500.00 | 294.50 | 147250.00 | 123.00 | 61500.00 | 61500.00 | Ocean Lifespaces India Private Limited
535.00 | 10 sq. mm | 500.00 | Nos. |  | 168.00 | 84000.00 | 535.00 | 267500.00 | 221.00 | 110500.00 | 150.00 | 75000.00 | 583.00 | 291500.00 | 186.00 | 93000.00 | 79.00 | 39500.00 | 39500.00 | Ocean Lifespaces India Private Limited
536.00 | 6 sq. mm | 500.00 | Nos. |  | 142.00 | 71000.00 | 526.00 | 263000.00 | 143.00 | 71500.00 | 110.00 | 55000.00 | 392.00 | 196000.00 | 108.50 | 54250.00 | 45.00 | 22500.00 | 22500.00 | Ocean Lifespaces India Private Limited
537.00 | As per NPCIL requirement Providing and installation of Copper earth electrode as per relevant IS 3043 through boring of holes in the required locations and as directed by the engineer - in charge. The scope also includes arrangement of boring machines required for the above job
538.00 | 25 mm dia - 3 meter length | 10.00 | Nos. |  | 26825.00 | 268250.00 | 45665.00 | 456650.00 | 10500.00 | 105000.00 | 15730.00 | 157300.00 | 29393.00 | 293930.00 | 21700.00 | 217000.00 | 15520.00 | 155200.00 | 105000.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
539.00 | 54 mm dia-2.1 thick copper pipe – 3 meter length | 10.00 | Nos |  | 23925.00 | 239250.00 | 66639.00 | 666390.00 | 21000.00 | 210000.00 | 29040.00 | 290400.00 | 42579.00 | 425790.00 | 16275.00 | 162750.00 | 17529.00 | 175290.00 | 162750.00 | VRC Constructions (India) Limited
540.00 | As per NPCIL requirement Brazing Joint of Grounding copper conductors to Copper / GI flats, including site testing, using brazing rods, as per the Purchaser approved Brazing Procedure & tender specifications, complete in all respects . The scope includes all the works such as arrrangement of brazing electrodes, brazing as well as providing and application of anti-corrosive paint over the brazed portion along with any other materials required to complete the job in all respects.
541.00 | 70 sq mm - 70 sq mm | 50.00 | Nos. |  | 5075.00 | 253750.00 | 2686.00 | 134300.00 | 1995.00 | 99750.00 | 1940.00 | 97000.00 | 12660.00 | 633000.00 | 930.00 | 46500.00 | 1407.00 | 70350.00 | 46500.00 | VRC Constructions (India) Limited
542.00 | 95 sq.mm - 95 sq. mm | 30.00 | Nos. |  | 5075.00 | 152250.00 | 3223.00 | 96690.00 | 2708.00 | 81240.00 | 2300.00 | 69000.00 | 17155.00 | 514650.00 | 1085.00 | 32550.00 | 1474.00 | 44220.00 | 32550.00 | VRC Constructions (India) Limited
543.00 | 185 sq mm - 185 sq mm | 20.00 | Nos. |  | 5075.00 | 101500.00 | 4476.00 | 89520.00 | 5273.00 | 105460.00 | 3630.00 | 72600.00 | 32613.00 | 652260.00 | 1550.00 | 31000.00 | 1742.00 | 34840.00 | 31000.00 | VRC Constructions (India) Limited
544.00 | 40x4 mm GI Flat - 70 sq mm | 50.00 | Nos. |  | 5075.00 | 253750.00 | 1433.00 | 71650.00 | 2138.00 | 106900.00 | 1090.00 | 54500.00 | 12660.00 | 633000.00 | 930.00 | 46500.00 | 1742.00 | 87100.00 | 46500.00 | VRC Constructions (India) Limited
545.00 | 50x10 mm GI Flat - 70 sq mm | 25.00 | Nos. |  | 5075.00 | 126875.00 | 2149.00 | 53725.00 | 2280.00 | 57000.00 | 1090.00 | 27250.00 | 16906.00 | 422650.00 | 1085.00 | 27125.00 | 2010.00 | 50250.00 | 27125.00 | VRC Constructions (India) Limited
546.00 | As per NPCIL requirement Exothermic welding T Joint of the Grounding copper conductor, including site testing, using exothermic moulds, as per the Purchaser approved exothermic welding Procedure & tender specifications. The scope includes all the works such as arrrangement of moulds, welding compound, electrodes, welding etc.. as well as providing and application of anti-corrosive paint over the welded portion along with any other materials required to complete the job in all respects.
547.00 | 70 sq mm - 70 sq mm | 50.00 | Nos. |  | 2175.00 | 108750.00 | 2686.00 | 134300.00 | 2594.00 | 129700.00 | 2300.00 | 115000.00 | 4917.00 | 245850.00 | 1705.00 | 85250.00 | 1407.00 | 70350.00 | 70350.00 | Ocean Lifespaces India Private Limited
548.00 | 95 sq mm - 95 sq mm | 30.00 | Nos. |  | 2175.00 | 65250.00 | 3223.00 | 96690.00 | 2021.00 | 60630.00 | 2900.00 | 87000.00 | 5646.00 | 169380.00 | 1860.00 | 55800.00 | 1474.00 | 44220.00 | 44220.00 | Ocean Lifespaces India Private Limited
549.00 | 185 sq mm - 185 sq mm | 20.00 | Nos. |  | 2175.00 | 43500.00 | 4476.00 | 89520.00 | 6840.00 | 136800.00 | 4360.00 | 87200.00 | 8066.00 | 161320.00 | 2325.00 | 46500.00 | 1742.00 | 34840.00 | 34840.00 | Ocean Lifespaces India Private Limited
550.00 | As per NPCIL requirement Exothermic welding CROSS Joint of the Grounding copper conductor, including site testing, using exothermic moulds, as per the Purchaser approved exothermic welding Procedure. The scope includes all the works such as arrrangement of moulds, welding compound, electrodes, welding etc.. as well as providing and application of anti-corrosive paint over the welded portion along with any other materials required to complete the job in all respects.
551.00 | 70 sq mm - 70 sq mm | 50.00 | Nos. |  | 2175.00 | 108750.00 | 2686.00 | 134300.00 | 2600.00 | 130000.00 | 1940.00 | 97000.00 | 5991.00 | 299550.00 | 1705.00 | 85250.00 | 1407.00 | 70350.00 | 70350.00 | Ocean Lifespaces India Private Limited
552.00 | 95 sq mm - 95 sq mm | 30.00 | Nos. |  | 2175.00 | 65250.00 | 3223.00 | 96690.00 | 3528.00 | 105840.00 | 2300.00 | 69000.00 | 6719.00 | 201570.00 | 1860.00 | 55800.00 | 1474.00 | 44220.00 | 44220.00 | Ocean Lifespaces India Private Limited
553.00 | 185 sq mm -185 sq mm | 20.00 | Nos. |  | 2175.00 | 43500.00 | 4476.00 | 89520.00 | 6869.00 | 137380.00 | 4360.00 | 87200.00 | 8935.00 | 178700.00 | 2325.00 | 46500.00 | 1742.00 | 34840.00 | 34840.00 | Ocean Lifespaces India Private Limited
554.00 | As per NPCIL requirement Exothermic welding STRAIGHT Joint of the Grounding copper conductor using exothermic moulds, as per the Purchaser approved exothermic welding Procedure. The scope includes all the works such as arrrangement of moulds, welding compound, electrodes, welding etc.. as well as providing and application of anti-corrosive paint over the welded portion.
555.00 | 70 sq mm - 70 sq mm | 50.00 | Nos. |  | 3625.00 | 181250.00 | 2686.00 | 134300.00 | 2678.00 | 133900.00 | 1940.00 | 97000.00 | 3759.00 | 187950.00 | 1705.00 | 85250.00 | 1407.00 | 70350.00 | 70350.00 | Ocean Lifespaces India Private Limited
556.00 | 95 sq mm - 95 sq mm | 30.00 | Nos. |  | 3625.00 | 108750.00 | 3223.00 | 96690.00 | 3635.00 | 109050.00 | 2300.00 | 69000.00 | 4488.00 | 134640.00 | 1860.00 | 55800.00 | 1474.00 | 44220.00 | 44220.00 | Ocean Lifespaces India Private Limited
557.00 | 185 sq mm -185 sq mm | 20.00 | Nos. |  | 3625.00 | 72500.00 | 4476.00 | 89520.00 | 7077.00 | 141540.00 | 4360.00 | 87200.00 | 6782.00 | 135640.00 | 2325.00 | 46500.00 | 1742.00 | 34840.00 | 34840.00 | Ocean Lifespaces India Private Limited
558.00 | Miscelleneous Works
559.00 | Providing and applying as per requirement of Fire coating material on laid cable. The scope includes cleaning and opening the cable trench covers, application of coating, removal of excess material, cleaning the area, restoration of the cable trench covers, dispose the empty cans etc. all as required at site and all as per specification. | 800.00 | litre |  | 3524.00 | 2819200.00 | 4615.00 | 3692000.00 | 3824.00 | 3059200.00 | 1730.00 | 1384000.00 | 3920.00 | 3136000.00 | 2325.00 | 1860000.00 | 1675.00 | 1340000.00 | 1340000.00 | Ocean Lifespaces India Private Limited
560.00 | As per NPCIL requirement Providing and Installation of the cable route marker by embedding in a precast 250 x 250 x 250 mm 1:4:8 PCC cube, curing and placing in cable trench and painting with one coat of red oxide primer and one coat bright red enamel paint , to complete the job in all respects as directed by the Purchaser. | 400.00 | Nos. |  | 1233.00 | 493200.00 | 1577.00 | 630800.00 | 264.00 | 105600.00 | 1200.00 | 480000.00 | 2692.00 | 1076800.00 | 1240.00 | 496000.00 | 558.00 | 223200.00 | 105600.00 | Dineshchandra R Agrawal Infracon Pvt. Ltd.
561.00 | As per NPCIL requirement Providing and installing GI flexible conduit sizes 20 mm to 32 mm as required in lengths of 1 m to 2 m including providing suitable GI adaptors and check nuts for both ends | 4000.00 | RM |  | 80.00 | 320000.00 | 285.00 | 1140000.00 | 263.00 | 1052000.00 | 360.00 | 1440000.00 | 187.00 | 748000.00 | 139.50 | 558000.00 | 76.00 | 304000.00 | 304000.00 | Ocean Lifespaces India Private Limited
562.00 | As per NPCIL requirement Providing and installing photo luminescent self adhessive flexible/rigid sheet auto glow Danger / EXIT , Direction marking sign boards at different areas reputed make or approved equivalent of150 x150 mm to 150x300 mm sizes with Danger symbol (Red) / Exit with direction (Green) or any marking inscriptions as directed by the Purchaser. | 1000.00 | Nos. |  | 3625.00 | 3625000.00 | 515.00 | 515000.00 | 608.00 | 608000.00 | 540.00 | 540000.00 | 4371.00 | 4371000.00 | 1472.50 | 1472500.00 | 727.00 | 727000.00 | 515000.00 | P AND C PROJECTS PRIVATE LIMITED
563.00 | As per NPCIL requirement Providing and Installing HT - 11 kV grade heat shrinkable straight through joint kits of required sizes of cores as per the recommended procedure and guidelines issued by the manufacturer and specifications and as directed by the Purchaser | 10.00 | Nos. |  | 18125.00 | 181250.00 | 61071.00 | 610710.00 | 71250.00 | 712500.00 | 39600.00 | 396000.00 | 100921.00 | 1009210.00 | 23250.00 | 232500.00 | 14347.00 | 143470.00 | 143470.00 | Ocean Lifespaces India Private Limited
564.00 | As per NPCIL requirement Providing and Installing LT - 1.1 kV grade heat shrinkable straight through joint kits of required sizes of cores as per the recommended procedure and guidelines issued by the manufacturer and specifications and as directed by the Purchaser | 30.00 | Nos. |  | 9425.00 | 282750.00 | 29218.00 | 876540.00 | 9975.00 | 299250.00 | 26400.00 | 792000.00 | 35858.00 | 1075740.00 | 8525.00 | 255750.00 | 14347.00 | 430410.00 | 255750.00 | VRC Constructions (India) Limited
565.00 | Up keeping of completely Handed over Rooms, providing temporary doors of metal sheet and angle frame in areas with lock and key including cleaning , sweeping & mopping of floors and installed equipment by means of providing vacuum cleaners, other cleaning aids, dust collection bins, tools & tackles, consumables etc and disposal of waste materials to waste collection boxes at designated places by providing suitable manpower and resources as per approved house keeping procedures. Note: (UOM is Operation Day, One Operation day means deployment of 1 resource performing the above tasks with cleaning aids for 9 hrs in a day including the lunch hours.) | 2368.00 | Operation-day |  | 1559.00 | 3691712.00 | 4803.00 | 11373504.00 | 1923.00 | 4553664.00 | 770.00 | 1823360.00 | 1762.00 | 4172416.00 | 1937.50 | 4588000.00 | 2144.00 | 5076992.00 | 1823360.00 | DEE VEE PROJECTS LIMITED
566.00 | As per NPCIL requirement Providing and installing at location weather resistant Fire sealing Mortar Compound for cable entry openings at walls / floors, Make HILTI CP-636, Shaliseal PS (Gun grade) or NPCIL approved Equivalent | 1000.00 | Kg |  | 892.00 | 892000.00 | 1724.00 | 1724000.00 | 680.00 | 680000.00 | 820.00 | 820000.00 | 1864.00 | 1864000.00 | 496.00 | 496000.00 | 727.00 | 727000.00 | 496000.00 | VRC Constructions (India) Limited
567.00 | As per NPCIL requirement Providing and correcting the Embedded plates up to 25 mm thick to finished level in the concrete floor / wall, having undulations as per requirement of NPCIL to bring the EP to the required level / height / depth for installation of equipment / panel. The scope includes cleaning / removal of extra concrete over the EP, grinding of EP, making the EP good by placing of fabricated steel channels, angles, plates including cutting, grinding, drilling, welding, painting etc., to the required finish as per requirement including providing all required resources and consumables (to be measured in cm of weld length). | 1500.00 | RM |  | 189.00 | 283500.00 | 2309.00 | 3463500.00 | 543.00 | 814500.00 | 1250.00 | 1875000.00 | 623.00 | 934500.00 | 1550.00 | 2325000.00 | 1072.00 | 1608000.00 | 283500.00 | JATAN CONSTRUCTIONS PVT LTD
568.00 | As per NPCIL requirement Providing and fixing low voltage class A Insulating mat as per IS 15652, 2 mm thick blue colour, preparation / cleaning of the floor prior to installation, levelling of the floor by providing Plaster of paris for any undulation to make the area levelled along with providing PEDILITE fevicol SR / 998 Resin Adhesives or any approved adhesive as per the instructions of the EIC, Disposal of the waste materials from the work site at scrap yard as directed. | 2600.00 | Sq. Meter |  | 1813.00 | 4713800.00 | 3568.00 | 9276800.00 | 845.00 | 2197000.00 | 2400.00 | 6240000.00 | 1786.00 | 4643600.00 | 930.00 | 2418000.00 | 670.00 | 1742000.00 | 1742000.00 | Ocean Lifespaces India Private Limited
569.00 | As per NPCIL requirement Providing and fixing medium voltage class B Insulating mat as per IS 15652, 2.5 mm thick blue colour, preparation / cleaning of the floor prior to installation, levelling of the floor by providing Plaster of paris for any undulation to make the area levelled along with providing PEDILITE fevicol SR / 998 Resin Adhesives or any approved adhesive as per the instructions of the EIC, Disposal of the waste materials from the work site at scrap yard as directed. | 1600.00 | Sq. Meter |  | 1733.00 | 2772800.00 | 4148.00 | 6636800.00 | 950.00 | 1520000.00 | 2640.00 | 4224000.00 | 2165.00 | 3464000.00 | 1007.50 | 1612000.00 | 950.00 | 1520000.00 | 1520000.00 | Ocean Lifespaces India Private Limited, Dineshchandra R Agrawal Infracon Pvt. Ltd.
570.00 | As per NPCIL requirement Providing and Installation of 1.5 mm thick anodised Aluminum Tags around 110 mm x 25 mm with two nos. 5 mm holes at both end, tieing with 0.5 mm SS wire on cables or screwing on panels / JBs with engraved letters / Numbers / symbols of size as per specification provided by NPCIL | 5000.00 | Nos. |  | 363.00 | 1815000.00 | 147.00 | 735000.00 | 180.00 | 900000.00 | 350.00 | 1750000.00 | 50.00 | 250000.00 | 38.75 | 193750.00 | 26.00 | 130000.00 | 130000.00 | Ocean Lifespaces India Private Limited
571.00 | Applicable GST Rate (%) Included in the Quoted Price
| Total in Figures |  |  |  |  | 4012651788.00 |  | 4221273386.00 |  | 3966300000.00 |  | 3978296590.00 |  | 3868280488.00 |  | 4183989725.50 |  | 3929353335.00
Lowest Amount Quoted BY: BRIDGE AND ROOF COMPANY INDIA LIMITED(3868280488.00)

## BOQ Summary
BOQ Summary Details Tender Title: NPCIL/KK5and6/CIVIL/PT/2025/27 Construction of Balance of Plant (BoP) Buildings and Structures of KKNPP 5and6 Tender ID: 2025_NPCIL_229149_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | BRIDGE AND ROOF COMPANY INDIA LIMITED (BID ID -835864) | 3868280488.00 | L1
| 2 | Ocean Lifespaces India Private Limited (BID ID -833197) | 3929353335.00 | L2
| 3 | Dineshchandra R Agrawal Infracon Pvt. Ltd. (BID ID -840028) | 3966300000.00 | L3
| 4 | DEE VEE PROJECTS LIMITED (BID ID -837242) | 3978296590.00 | L4
| 5 | JATAN CONSTRUCTIONS PVT LTD (BID ID -836380) | 4012651788.00 | L5
| 6 | VRC Constructions (India) Limited (BID ID -839500) | 4183989725.50 | L6
| 7 | P AND C PROJECTS PRIVATE LIMITED (BID ID -838817) | 4221273386.00 | L7