## BoQ1
Government eProcurement System Created By: RAGHU L Created Date/Time: 30-Oct-2025 04:30 PM Tender Title: Supply, installation, testing and commissioning of independent air conditioner units Tender ID: 2025_NPCIL_240572_1
Tender Inviting Authority: PD, KK-3to6
Name of Work: Supply, installation, testing and commissioning of independent air conditioner units & associated ventilation ducting, structural supports, copper tubing & carbon steel piping, communication & power cabling, anti corrosive painting, ventilation equipments, valves & dampers in various main plant buildings of KKNPP-3&4
Contract No: NPCIL/KK-3&4/CONST/MECH/PT/2025/101
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ULTRA TECH ENGINEERS (GSTN-08AABFU5279L2ZK) BID ID -882243 |  | Om Engineering and Construction Company (GSTN-NA) BID ID -885566
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, installation and commissioning of wall mounted/ cassette type Independent split Air conditioner units meeting the technical requirements specified in technical specification & rated cooling capacity, given below; The scope of work includes a) supply and installation of copper tube (min 3 meter length - liquid & gas lines individually) with insulation material and power & communication cable, comsumables such as fasteners and ODU bracket, b) pressure testing, vacuumising, refrigerant charging and commissioning of the units c) Supply of IDU LCD remote controller, voltage stablizer of required rating as per technical specification. The work also includes transportation, storage, shifting to the location, providing tools and tackles, manpower, machineries, scaffoldings, consumables including fasteners, leveling, aligning with base frame/ flanges, erection, fixing of vibro-isolators, bolting as per manufacturer documents, inspection, preparation and handing over of as built drawing & commissioning reports as per technical specifications for acceptance of NPCIL.
1.10 | 1 TR - -5 star rating (inverter type), Wall mounted | 40.00 | Set | 10.00 | 49900.00 | 1996000.00 | 47101.00 | 1884040.00 | 1884040.00 | Om Engineering and Construction Company
1.20 | 1.5 TR - 5 star rating (inverter type) Wall mounted | 220.00 | Set | 10.00 | 54100.00 | 11902000.00 | 51101.00 | 11242220.00 | 11242220.00 | Om Engineering and Construction Company
1.30 | 1.5 TR - 5 star rating (inverter type) 4 way cassette type | 2.00 | Set | 10.00 | 68000.00 | 136000.00 | 72601.00 | 145202.00 | 136000.00 | ULTRA TECH ENGINEERS
1.40 | 2 TR - 5 star rating (inverter type) Wall mounted | 40.00 | Set | 10.00 | 69250.00 | 2770000.00 | 74101.00 | 2964040.00 | 2770000.00 | ULTRA TECH ENGINEERS
2.00 | VRF Outdoor Units: Supply & installation and commissioning of Digital/ Invertor based compressor with Variable Refrigerant Flow [VRF] system (with R-410 A) connectable to multiple indoor units. Outdoor unit shall be factory assembled weather proof casing constructed from heavy gauge mild steel panels with epoxy coated painting. The unit shall be completely factory wired and tested with necessary controls. The compressor shall be highly efficeint Digital scroll type controller. The aluminium fins shall be covered with anti-corrosion resin. Unit shall be equipped with oil recovery system to ensure stable operation with long refrigerant piping. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B . The COP of the system shall be greater than 4 under ARI conditions for 100% load . The unit shall be compatible for BMS operation, as per Specifications and as directed by Engineer incharge.
2.10 | 11 HP Nominal or higher | 3.00 | Nos. | 10.00 | 460000.00 | 1380000.00 | 450101.00 | 1350303.00 | 1350303.00 | Om Engineering and Construction Company
2.20 | 8 HP Nominal or higher | 3.00 | Nos. | 10.00 | 410000.00 | 1230000.00 | 431101.00 | 1293303.00 | 1230000.00 | ULTRA TECH ENGINEERS
3.00 | VRF Indoor Units: Supply & installation and commissioning of Indoor floor standing unit. The indoor unit shall have independent electronic control valve to control the refrigerant folw rate respond to variations of the airconditioning load of the room. The fan shall be aerodynamically designed turbo multiblade type. Statically and dynamically balanced to ensure lowest noise. The cooling coil shall be made of seamless copper tube. The tube shall be Hydraulically or mechanically expanded and tested for 21Kg/cm2. The minimum Energy Efficiency Ratio shall be as per ASHRAE STANDARDS 90.1 -2001 table 6.2.1B. The cassette/ ducted type indoor unit shall have the inbuilt drain pump arrangement. Indoor units shall have a wireless/ wired remote control, as per Specifications and as directed by Engineer incharge.
3.10 | Floor standing type nominal capacity of 3 TR or higher | 8.00 | Nos. | 10.00 | 92500.00 | 740000.00 | 94101.00 | 752808.00 | 740000.00 | ULTRA TECH ENGINEERS
3.20 | Floor standing type nominal capacity of 4 TR or higher | 6.00 | Nos. | 10.00 | 98500.00 | 591000.00 | 96101.00 | 576606.00 | 576606.00 | Om Engineering and Construction Company
4.00 | Installation and commissioning of air conditioner and ventilation equipments, valves/ dampers; Receipt of Air conditioner and other ventilation equipment, valves & dampers from stores, handling, transportation and erection as per manufacturer recommendation, guidelines & technical specification. The work also includes transportation, storage, shifting to the location, providing tools and tackles, manpower, machineries, scaffoldings, consumables including fasteners leveling, aligning with base frame/ flanges, fixing of vibro-isolators, bolting as per manufacturer documents, inspection, commissioning of units, preparation and handing over of as built drawing & commissioning reports as per technical specifications for acceptance of NPCIL. | 70.00 | MT | 10.00 | 95000.00 | 6650000.00 | 95000.00 | 6650000.00 | 6650000.00 | ULTRA TECH ENGINEERS, Om Engineering and Construction Company
5.00 | Supply, Installation, Testing, vacuuming, refrigerant charging of suction & discharge lines of 16G Copper tube conforming ASTM B280 with 19mm thick insulation by nitril rubber tubular covered by polyshield tape connecting the indoor units and outdoor units with supports like clamp,threaded rod ,anchor fastner,nut ,bolt & washers as directed by engineer. The work also includes providing pressure testing of tubing with nitrogen, arrangement of consumables, necessary tools, tackle, manpower, scaffolding, supply of clamp supports along with rubber pad,tray, brazing gases, filler wire, flux etc. for completion of work. The work also includes preparation and submission of erection reports for acceptance of NPCIL.
5.10 | 6.35mm (OD) | 2500.00 | Rmt | 10.00 | 920.00 | 2300000.00 | 850.00 | 2125000.00 | 2125000.00 | Om Engineering and Construction Company
5.20 | 9.53mm (OD) | 300.00 | Rmt | 10.00 | 958.00 | 287400.00 | 900.00 | 270000.00 | 270000.00 | Om Engineering and Construction Company
5.30 | 12.70mm (OD) | 2500.00 | Rmt | 10.00 | 1100.00 | 2750000.00 | 1000.00 | 2500000.00 | 2500000.00 | Om Engineering and Construction Company
5.40 | 15.88mm (OD) | 2100.00 | Rmt | 10.00 | 1260.00 | 2646000.00 | 1130.00 | 2373000.00 | 2373000.00 | Om Engineering and Construction Company
5.50 | 22.23mm (OD) | 1600.00 | Rmt | 10.00 | 1600.00 | 2560000.00 | 1510.00 | 2416000.00 | 2416000.00 | Om Engineering and Construction Company
5.60 | 28.58mm (OD) | 2800.00 | Rmt | 10.00 | 1980.00 | 5544000.00 | 1800.00 | 5040000.00 | 5040000.00 | Om Engineering and Construction Company
6.00 | Supply and Installation of Refnet joints / branch distributors for indoor and outdoor units. | 20.00 | Nos. | 10.00 | 6100.00 | 122000.00 | 5200.00 | 104000.00 | 104000.00 | Om Engineering and Construction Company
7.00 | Supply and erection of condensate water drain pipes of PVC with nitryl rubber insulation , pipe fittings, accessories, bends, elbows, tees, flanges, tapings, wall sleeves, hangers, supports, anchor fasteners etc for completion of work. The work also includes tools and tackles, manpower, machineries, scaffoldings, consumables, inspection, preparation and handing over of as built drawing & reports as per technical specifications for acceptance of NPCIL.
7.10 | 25 mm dia | 1900.00 | RM | 10.00 | 540.00 | 1026000.00 | 510.00 | 969000.00 | 969000.00 | Om Engineering and Construction Company
7.20 | 40 mm dia | 6000.00 | RM | 10.00 | 772.00 | 4632000.00 | 700.00 | 4200000.00 | 4200000.00 | Om Engineering and Construction Company
8.00 | Supply and Installation of G.I. Tray to support and organize the copper tube/power and communication cables/drain pipe and Covered with G.I. Sheet for exposed copper tube at terrace level. The work also includes arrangement of consumables, necessary tools, tackle, materials, manpower, scaffolding, supply of clamp supports along with rubber pad,tray, filler wire, flux etc. for completion of work. The work also includes preparation and submission of erection reports for acceptance of NPCIL. | 2500.00 | RM | 10.00 | 1700.00 | 4250000.00 | 1501.00 | 3752500.00 | 3752500.00 | Om Engineering and Construction Company
9.00 | Supply and erection of power and communication cable as per technical specification
9.10 | 4C*2.5 sqm | 2100.00 | RM | 10.00 | 660.00 | 1386000.00 | 420.00 | 882000.00 | 882000.00 | Om Engineering and Construction Company
9.20 | 4C*4 sqm | 1400.00 | RM | 10.00 | 440.00 | 616000.00 | 721.00 | 1009400.00 | 616000.00 | ULTRA TECH ENGINEERS
9.30 | 4C*1.5 sqm | 6000.00 | RM | 10.00 | 310.00 | 1860000.00 | 290.00 | 1740000.00 | 1740000.00 | Om Engineering and Construction Company
10.00 | Supply of Refrigerant as per technical specification
10.10 | R410A | 2000.00 | Kg. | 10.00 | 1280.00 | 2560000.00 | 1351.00 | 2702000.00 | 2560000.00 | ULTRA TECH ENGINEERS
10.20 | R32 | 500.00 | Kg. | 10.00 | 1600.00 | 800000.00 | 1751.00 | 875500.00 | 800000.00 | ULTRA TECH ENGINEERS
10.30 | R407 | 248.00 | Kg. | 10.00 | 1100.00 | 272800.00 | 1151.00 | 285448.00 | 272800.00 | ULTRA TECH ENGINEERS
11.00 | Identification, marking, mounting and setting up machine, performing core cutting of reinforced concrete wall/floor using diamond core drilling of required size, removing and disposal of debris & cleaning the area. The work also includes providing tools, tackles, manpower, machineries, scaffolding for completion of work. | 10000.00 | mm-meter | 10.00 | 190.00 | 1900000.00 | 225.00 | 2250000.00 | 1900000.00 | ULTRA TECH ENGINEERS
12.00 | Making/ Enlarging/ Closing of Wall opening for passing of Duct/ Pipe: The work also includes providing tools, tackles, manpowers, machinaries, scaffolding for completion of work
12.10 | Making Wall opening in Brick Wall. This work also includes, finishing of openings with suitable approved cement - mortar. | 7500.00 | mm-meter | 10.00 | 150.00 | 1125000.00 | 130.00 | 975000.00 | 975000.00 | Om Engineering and Construction Company
12.20 | Closing of gap between drain pipe, tube and wall penetration with fire stop sealant compound as per technical specification. The work also includes Supply of UL rated Fire stop sealant, Mortar for filling of gap, arrangement of necessary tools & tackles, consumables, machinaries for completing the work. | 6000.00 | Litres | 10.00 | 1100.00 | 6600000.00 | 900.00 | 5400000.00 | 5400000.00 | Om Engineering and Construction Company
13.00 | Supply, fabrication and Erection of GI Ducting and fittings: Supply of Galvanized steel sheets confirming to IS: 277-2008, designation GPD, grade of zinc coating 275 of 1.0 mm thick sheets, transportation, preparation and submission of Incoming material inspection report (IMIR), storage, preparation of duct/ fitting fabrication drawings for engineer’s acceptance, cutting of sheets to required size & shape, bending, rolling, edge preparation pitts burg lock seam/ grooved seam, spiral seam for circular ducts and rectangular ducts & fittings such as bends, elbows, taps, T-joints, reducers of various sizes, collar piece, erection of ducts & fittings at site with metal flanged connection. This work also includes supply and joining by GI rivets, fasteners, nut-washers as per IS 1363 & IS 1367 of property class 5.6, 5 mm thick EPDM/ Neoprene self adhesive gasket of equal flange width for flange connection, supply and application of silicon duct sealant, inspection as per specification and drawings, providing tools & tackles, machineries, manpower, preparation and handing over of as built drawings, reports, construction completion certificate (CCC) for following items. | 2790.00 | Sq. meter | 10.00 | 7000.00 | 19530000.00 | 7100.00 | 19809000.00 | 19530000.00 | ULTRA TECH ENGINEERS
14.00 | Modification in erected GI Ducting: Dismantling of erected duct, fittings, cutting, drilling, re fabrication as per the modified drawing and re erection at site for following items. The work also involves providing tools & tackles, machinaries, manpower, consumables required for execution of work. (a) Dismantling of erected GI ducts and fittings and depositing the material as per instruction of EIC. | 4000.00 | Kg. | 10.00 | 115.00 | 460000.00 | 95.00 | 380000.00 | 380000.00 | Om Engineering and Construction Company
15.00 | Supply, fabrication and erection of structural steel: Supply of carbon steel structures angle/ flats, beams, channels, box sections, rods, plates of various sizes as per Indian Standard and material grade as per IS 2062-2011 Grade E-250 Quality-A, sheet up to 2 mm thickness as per IS 513 designation - CR-3, plates as per IS 2062-2011 Grade E-250 Quality-BR, cutting, drilling, fabrication of equipment/ base frames/ ducting supports/Piping supports/ flanges and stiffeners for ducts and other structural's, welding, visual inspection and erection at various locations & elevation, preparation and submission of erection reports for acceptance as per specification. This work also involves supply and erection of bolt nut washers as per IS 1363 property class 5.6, 8.8 providing tools & tackles, manpower, scaffolding, electrodes to complete the work. | 40000.00 | Kg. | 10.00 | 280.00 | 11200000.00 | 280.00 | 11200000.00 | 11200000.00 | ULTRA TECH ENGINEERS, Om Engineering and Construction Company
16.00 | Modification of Erected structurals and supports: Dismantling of erected structural and ducting supports, cutting, drilling, re fabrication as per the modified drawing and re erection at site for following items. The work also involves providing tools & tackles, machinaries, manpower, scaffolding, consumables required for execution of work.
16.10 | Dismantling of Erected structurals and ducting supports as per revised drawings and specification and depositing the material as per instruction of EIC. | 5000.00 | Kg. | 10.00 | 32.00 | 160000.00 | 31.00 | 155000.00 | 155000.00 | Om Engineering and Construction Company
16.20 | Re-erection of dis-assembled ducting supports/ Pre fabricated supports This work includes welding of dismantled structures and touch up painting, arrangement of tools & tackles, machineries, consumables, fasteners, manpower, P&M required for execution of work. | 2500.00 | Kg. | 10.00 | 94.00 | 235000.00 | 97.00 | 242500.00 | 235000.00 | ULTRA TECH ENGINEERS
17.00 | Supply and application of Paint on Pipes, fittings and Structural Steel: The work includes a) Surface preparation by grit blasting, supply and application of zinc rich epoxy primer of thickness 75 to 80 microns as per technical specification b) Supply and applicationof High build Epoxy finish paint in two coats (150 to 160 microns) and to get overall DFT (including primer) of 230 to 240 microns on pipes, pipe fittings and structural steel surfaces as per the instructions given in the working drawings. | 50.00 | MT | 10.00 | 70000.00 | 3500000.00 | 72000.00 | 3600000.00 | 3500000.00 | ULTRA TECH ENGINEERS
18.00 | Fabrication & Erection of CS pipes & fittings: The work involves a) study of working drawings, inspection of wall openings at site b) CS pipes, fittings, flanges, including transportation, temporary storage, unloading & uncrating the box, inspection, temporary storage, shifting to the location. c) fabrication, erection of CS pipes, fittings and flanges over supports, as per drawings and technical specification d) Preparation of CRR, erection reports, as built drawing, pressure testing(pneumatic/ hydrotest), visual inspection, providing tools & tackles and manpower, setup for pressure test (pneumatic/ hydro) and manpower, CCC required for completion of work as per the technical specifications and drawing. Note: payment for welding of pipes will be measured and paid under relevant BOQ item | 15000.00 | Kg. | 10.00 | 175.00 | 2625000.00 | 250.00 | 3750000.00 | 2625000.00 | ULTRA TECH ENGINEERS
19.00 | Welding of CS pipes & fittings: The work involves a)Welding of CS pipes by GTAW/SMAW technique, pipe fittings and flanges including the edge preparation, grinding, fit up, Cleaning of weld joints using approved cleaning agents, performing non destructive testing such as DPT, root & final dye penetrant testing of weld joint, deploying NDT qualified personnel in ISNT/ ASNT leval-2 and post cleaning of weld joint. b)The work also includes arrangement of manpower, plant & machineries, scaffolding, tools & tackles, consumables, gas, preparation & submission of reports, as built drawing, CCC required for completion of work as per the technical specifications and drawing. | 5000.00 | Inch Dia | 10.00 | 1500.00 | 7500000.00 | 2000.00 | 10000000.00 | 7500000.00 | ULTRA TECH ENGINEERS
20.00 | Manpower supply for various miscellaneous works related to HVAC, chilled water and Fire water systems which are not included in BOQ such as shifting of miscellaneous free issue materials from store, inspection and record keeping of already preserved equipments at site, assisting during pre commissioning checks of ventilation/ Chilled water/ Fire water systems, periodic checking of operability of electric actuators ventilation dampers etc. The work also involves providing necessary hand tools, tackles, safety gears required for the work. [1 Shift operation = 9 Hrs. of work by 1 person of relevant category including lunch break]
20.10 | High Skilled [foreman/ electrician/ duct welder/ AC Mechanic] | 2504.00 | Shift | 10.00 | 1400.00 | 3505600.00 | 1400.00 | 3505600.00 | 3505600.00 | ULTRA TECH ENGINEERS, Om Engineering and Construction Company
20.20 | Skilled [Fitter/ Structural Welder/ AC operator/Rigger] | 2504.00 | Shift | 10.00 | 1350.00 | 3380400.00 | 1300.00 | 3255200.00 | 3255200.00 | Om Engineering and Construction Company
20.30 | Un Skilled [Helper] | 2504.00 | Shift | 10.00 | 1200.00 | 3004800.00 | 1200.00 | 3004800.00 | 3004800.00 | ULTRA TECH ENGINEERS, Om Engineering and Construction Company
21.00 | Applicable GST Rate (%) Included in the Quoted Price
| Total in Figures |  |  |  |  | 125733000.00 |  | 125629470.00
Lowest Amount Quoted BY: Om Engineering and Construction Company(125629470.00)

## BOQ Summary
BOQ Summary Details Tender Title: Supply, installation, testing and commissioning of independent air conditioner units Tender ID: 2025_NPCIL_240572_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Om Engineering and Construction Company (BID ID -885566) | 125629470.00 | L1
| 2 | ULTRA TECH ENGINEERS (BID ID -882243) | 125733000.00 | L2