## BoQ1
Government eProcurement System Created By: HASTI MAL NAHAR Created Date/Time: 03-Feb-2026 11:57 AM Tender Title: Supply, installation, testing and commissioning of main distribution electrical system Tender ID: 2025_NPCIL_250903_1
Tender Inviting Authority:
Name of Work: Supply, installation, testing & commissioning of main distribution electrical system components for Vikram Nagar & Sentab colonies including 11KV overhead line & other miscellaneous work at other RR site colonies.
Contract No: NPC/RRS/90/2025/CPT-A2887
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Aditya Techno Products Private Limited (GSTN-09AAGCA0910L1ZS) BID ID -922666 |  | Vijayvargia Electricals (GSTN-NA) BID ID -922916
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply & Installation including testing & commissioning of double door type, outdoor, Main & sub-feeder distribution panel under item No. 1.1,1.2 & 1.3.
1.10 | Supply, testing & commissioning of double door, 3 phase 4 wire, 415V, 50Hz, main distribution panel out door type IP-54, main feeder panel made of 2mm thick CRCA / GP sheet and base frame ISMC -100. a) 1 No. 3 pole, 400Amp., 415V, 50Hz, minimum breaking capacity 35KA, MCCB having adjustable thermal release setting with terminal spreaders. b) 6 nos. 3 pole, 250 Amp, 415 V, 50 Hz, minimum breaking capacity 35KA, MCCB. Make of MCCBs: Schneider/ Legrand/L&T (LK)/ Crompton Greaves make. Note: For more details refer technical specification (section-V of tender). | 4.00 | Nos. |  | 498100.00 | 1992400.00 | 446250.00 | 1785000.00 | 1785000.00 | Vijayvargia Electricals
1.20 | Supply, testing & commissioning of double door, 3 phase 4 wire, 415V, 50Hz, outdoor type distribution panel IP - 54, the sub feeder panel shall be made out of 2mm thick CRCA sheet and base frame ISMC -100. a) 1 No. 3 pole, 250Amp., 415 V, 50 Hz minimum breaking capacity 35KA, MCCB having adjustable thermal release setting with terminal spreaders. b) 7 nos. 3 pole, 100 Amp, 415 V, 50 Hz minimum breaking capacity 35KA, MCCB. Make of MCCBs: Schneider/ Legrand/L&T(LK)/ Crompton Greaves make. Note: For more details refer technical specification (section-V of tender). | 18.00 | Nos. |  | 382999.00 | 6893982.00 | 312000.00 | 5616000.00 | 5616000.00 | Vijayvargia Electricals
1.30 | Installation of main & sub-feeder panel includes preparation of 2 Nos. of RCC foundations having size- 500x300x1000 mm with required reinforcement, cement, coarse and aggregates in the ratio of 1:3:6, smooth plastering work all around the foundations with cement mortar ratio 1:4, MS EP 8 mm thick 500x300mm with legs 300 mm long and water curing etc. complete as per direction of EIC and technical specification. Note: For more details refer technical specification (section-V of tender). | 22.00 | Nos. |  | 4300.00 | 94600.00 | 6000.00 | 132000.00 | 94600.00 | Aditya Techno Products Private Limited
2.00 | Supply & Installation of ISI marked, 1.1 KV grade, PVC Insulated, Fire resistant sheathing, Aluminium Stranded Conductor, Steel Armoured (Galvanized flat steel strip) heavy duty power Cable PVC Sheathed cables confirm to IS: 1554 Part-I and laying in cable trenches/Hume pipes/GI pipes / on wall etc. The scope also includes removal of existing cable & deposit in sectional store etc. Cost of making trench and laying of GI pipes / Hume pipes have either been covered separately or already laid during construction of building/ road. Cable Make- Finolex / Polycab / Universal/ KEI / Havells/ NICCO/ RPG Note: For more details refer technical specification (section-V of tender).
2.01 | Supply of 4 C x 10 sq. mm cable. | 7000.00 | Metre |  | 140.50 | 983500.00 | 150.00 | 1050000.00 | 983500.00 | Aditya Techno Products Private Limited
2.02 | Supply of 4 C x 25 sq. mm cable. | 1000.00 | Metre |  | 201.00 | 201000.00 | 210.00 | 210000.00 | 201000.00 | Aditya Techno Products Private Limited
2.03 | Supply of 4 C x 35 sq. mm cable. | 5500.00 | Metre |  | 268.50 | 1476750.00 | 270.00 | 1485000.00 | 1476750.00 | Aditya Techno Products Private Limited
2.04 | Supply of 3.5 C x 150 sq. mm cable. | 3500.00 | Metre |  | 798.00 | 2793000.00 | 780.00 | 2730000.00 | 2730000.00 | Vijayvargia Electricals
2.05 | Supply of 3.5 C x 400 sq. mm cable. | 1750.00 | Metre |  | 1892.00 | 3311000.00 | 1935.00 | 3386250.00 | 3311000.00 | Aditya Techno Products Private Limited
2.06 | Installation of 4 C x 10 sq. mm cable. | 7000.00 | Metre |  | 15.00 | 105000.00 | 20.00 | 140000.00 | 105000.00 | Aditya Techno Products Private Limited
2.07 | Installation of 4 C x 25 sq. mm cable. | 1000.00 | Metre |  | 27.00 | 27000.00 | 30.00 | 30000.00 | 27000.00 | Aditya Techno Products Private Limited
2.08 | Installation of 4 C x 35 sq. mm cable. | 5500.00 | Metre |  | 30.00 | 165000.00 | 40.00 | 220000.00 | 165000.00 | Aditya Techno Products Private Limited
2.09 | Installation of 3.5 C x 150 sq. mm cable. | 3500.00 | Metre |  | 55.00 | 192500.00 | 50.00 | 175000.00 | 175000.00 | Vijayvargia Electricals
2.10 | Installation of 3.5 C x 400 sq. mm cable. | 1750.00 | Metre |  | 85.00 | 148750.00 | 65.00 | 113750.00 | 113750.00 | Vijayvargia Electricals
3.00 | Supply & Installation of heavy Gauge G.I. Saddle & base (Spacer) with screw for following sizes of PVC insulated Aluminium armoured cables. Note: For more details refer technical specification (section-V of tender).
3.10 | 4C x 10 sq.mm | 500.00 | Nos. |  | 24.00 | 12000.00 | 10.00 | 5000.00 | 5000.00 | Vijayvargia Electricals
3.20 | 4C x 25 sq.mm | 100.00 | Nos. |  | 32.00 | 3200.00 | 15.00 | 1500.00 | 1500.00 | Vijayvargia Electricals
3.30 | 4C x 35 sq.mm | 100.00 | Nos. |  | 42.00 | 4200.00 | 25.00 | 2500.00 | 2500.00 | Vijayvargia Electricals
4.00 | Termination and connection of PVC insulated stranded Aluminium armoured cable including supply of single compression nickel plated brass cable glands and crimping type aluminium lugs (Make- Dowells / Comet / SMI) Anti-oxidation compound and other consumables to complete the jobs in all respect. Note: For more details refer technical specification (section-V of tender).
4.10 | 4 C x 10 sq. mm cable. | 400.00 | Nos. |  | 211.00 | 84400.00 | 250.00 | 100000.00 | 84400.00 | Aditya Techno Products Private Limited
4.20 | 4 C x 25 sq. mm cable. | 128.00 | Nos. |  | 271.00 | 34688.00 | 325.00 | 41600.00 | 34688.00 | Aditya Techno Products Private Limited
4.30 | 4 C x 35 sq. mm cable. | 252.00 | Nos. |  | 298.00 | 75096.00 | 350.00 | 88200.00 | 75096.00 | Aditya Techno Products Private Limited
4.40 | 3.5 C x 150 sq. mm cable. | 46.00 | Nos. |  | 799.00 | 36754.00 | 1000.00 | 46000.00 | 36754.00 | Aditya Techno Products Private Limited
4.50 | 3.5 C x 400 sq. mm cable. | 10.00 | Nos. |  | 2250.70 | 22507.00 | 3000.00 | 30000.00 | 22507.00 | Aditya Techno Products Private Limited
5.00 | Excavation for new cable trench in all types of soil (rocky, soft, road & PCC/RCC slab) of size up to 500-600 mm deep. X 300 mm wide. No payment will be made for excavation beyond above dimensions. Scope includes removal and re-fixing of inter locking tiles (if any) and back filling with selected excavated material, watering ramming & disposing off the surplus material as per direction of EIC. (Note- Blasting is not permitted). Note: For more details refer technical specification (section-V of tender). | 1100.00 | CuM |  | 800.00 | 880000.00 | 600.00 | 660000.00 | 660000.00 | Vijayvargia Electricals
6.00 | Supply & Laying of fine river bed sand cushion 75 mm before laying and 75 mm after laying of the cable or as directed by EIC. Note: For more details refer technical specification (section-V of tender). | 270.00 | CuM |  | 2240.00 | 604800.00 | 2300.00 | 621000.00 | 604800.00 | Aditya Techno Products Private Limited
7.00 | Supply and placing of fully baked A-class standard clay bricks after laying cable and layers of sand. Sample of brick shall be approved by EIC. Note: For more details refer technical specification (section-V of tender). | 60000.00 | Nos. |  | 8.00 | 480000.00 | 10.00 | 600000.00 | 480000.00 | Aditya Techno Products Private Limited
8.00 | Supply and installation of G.I. flat for earthing of distribution panels & poles. Scope also include flat to be laid in ground 200 mm deep, (Excavation is under the scope of this item) full welding at joints by Lap /Tee/Cross type joints, Joint to be painted with 2 coats of red oxide primer and two coat of aluminium paint, Flat to be clamped on wall wherever required, @ 500mm interval with the help of GI clamps or as approved by EIC and connected at both ends using nut bolt spring and plain washer. Note: For more details refer technical specification (section-V of tender).
8.10 | 25 x 3 mm G.I. flat. | 6000.00 | Metre |  | 94.00 | 564000.00 | 90.00 | 540000.00 | 540000.00 | Vijayvargia Electricals
8.20 | 50 x 6 mm G.I. flat. | 500.00 | Metre |  | 305.00 | 152500.00 | 300.00 | 150000.00 | 150000.00 | Vijayvargia Electricals
9.00 | Supply and installation of pipe earthing pit. Scope of this work covers excavation of earth pit, removal of surplus material, installation pipe earthing station with 40 mm dia medium gauge G.I. pipe and back filling with salt, charcoal and black soil as directed. Job also include measurement of earth resistance of each pit. Note: For more details refer technical specification (section-V of tender).
9.10 | Excavation (in all type of soil i.e. rocky, soft, hard) of earth pit 1.0 x1.0 x 1.7 to 2.0 M deep size. Blasting shall not be permitted. | 100.00 | CuM |  | 800.00 | 80000.00 | 1500.00 | 150000.00 | 80000.00 | Aditya Techno Products Private Limited
9.20 | Supply of good quality black soil, filling in earth pit, watering & ramming as directed. | 100.00 | CuM |  | 805.00 | 80500.00 | 800.00 | 80000.00 | 80000.00 | Vijayvargia Electricals
9.30 | Supply of char-coal and filling in earth pit as directed. | 2500.00 | Kg |  | 23.00 | 57500.00 | 16.00 | 40000.00 | 40000.00 | Vijayvargia Electricals
9.40 | Supply of good quality ungrinded salt and filling in earth pit as directed. | 2500.00 | Kg |  | 10.00 | 25000.00 | 11.00 | 27500.00 | 25000.00 | Aditya Techno Products Private Limited
9.50 | Construction of Brick masonry (A-Class bricks) chamber 350 x 350 x 600mm (Inside clear) of wall thickness 230mm in cement mortar 1 : 4 with removable RCC precast slab of thickness not less than 75mm and plastering smooth 15 mm thick inside and outsider sides of chamber etc. complete in all respect as per EIC. | 50.00 | Nos. |  | 1850.00 | 92500.00 | 2000.00 | 100000.00 | 92500.00 | Aditya Techno Products Private Limited
9.60 | Supply and placing of 40 mm dia medium gauge G.I. Pipe 2.0-metre-long with 1 no. G.I. reducer 50mm to 40mm & perforation at maximum distance of 150 mm throughout the length (other detail as per technical specification of as per instruction of EIC). | 50.00 | Nos. |  | 1050.00 | 52500.00 | 1000.00 | 50000.00 | 50000.00 | Vijayvargia Electricals
10.00 | Making of Copping around the street light/ post top pole shall be made the size of 400mm dia and 450mm high above the ground level. Cement Concrete of 1:3:6 (1 Cement: 3 Coarse sand: 6 graded stone aggregate 20 mm nominal size) and finishing with plaster to be done on the copping surface & curing. Note: For more details refer technical specification (section-V of tender). | 150.00 | Nos. |  | 725.00 | 108750.00 | 600.00 | 90000.00 | 90000.00 | Vijayvargia Electricals
11.00 | Supply & installation of non-pressure NP2 class (light duty) 150 mm dia R.C. Hume pipe of 2-meter length having collar. Note: For more details refer technical specification (section-V of tender). | 400.00 | Metre |  | 475.00 | 190000.00 | 450.00 | 180000.00 | 180000.00 | Vijayvargia Electricals
12.00 | Supply & installation of GI Junction Boxes for Street light poles. The JBs shall be fabricated from 1.6 mm thick sheet in the size of 275 x 275 x 150 mm deep in full welded construction. Note: For more details refer technical specification (section-V of tender). | 200.00 | Nos. |  | 2150.00 | 430000.00 | 2500.00 | 500000.00 | 430000.00 | Aditya Techno Products Private Limited
13.00 | Rewinding of domestic & industrial type Single phase motors of ceiling fan / wall mounted fan, exhaust fan, desert cooler fan motor for burnt or defective winding and associated works. Material of winding must be copper. (For more details refer technical specification). Old burnt wire shall be retain by contractor etc. Note: For more details refer technical specification (section-V of tender).
13.10 | Up to 90Watt. | 1000.00 | Nos. |  | 290.00 | 290000.00 | 250.00 | 250000.00 | 250000.00 | Vijayvargia Electricals
13.20 | Above 90W & up to 200Watt. | 150.00 | Nos. |  | 490.00 | 73500.00 | 500.00 | 75000.00 | 73500.00 | Aditya Techno Products Private Limited
13.30 | Supply and replacement of shaft & bush of desert cooler fan motor. Including associated maintenance. | 100.00 | Nos. |  | 230.00 | 23000.00 | 300.00 | 30000.00 | 23000.00 | Aditya Techno Products Private Limited
13.40 | Rewinding of fan motor 500W to 600W of Duct Mounted Air / Desert Cooler including supply & replacement of bush and bearing. | 6.00 | Nos. |  | 1125.00 | 6750.00 | 1200.00 | 7200.00 | 6750.00 | Aditya Techno Products Private Limited
14.00 | Supply & Installation of B class G.I. Pipe with accessories like bend of required radius, socket long radius bends where ever required & clamping. Make PRAKASH SURYA / JINDAL. The pipe shall be of following size. Note: For more details refer technical specification (section-V of tender).
14.10 | 32mm | 900.00 | Metre |  | 450.00 | 405000.00 | 375.00 | 337500.00 | 337500.00 | Vijayvargia Electricals
14.20 | 50mm | 100.00 | Metre |  | 650.00 | 65000.00 | 560.00 | 56000.00 | 56000.00 | Vijayvargia Electricals
15.00 | Providing and laying 80mm thick factory made cement concrete interlocking pavers block of M-35 grade made by block making machine with strong vibratory compaction and of approved size and design / shape laid in required colour (Yellow, Red and other as directed) and pattern over and including 50mm thick compacted bed of course sand, filling the joints with coarse sand etc. all complete as per the direction of Engineer-in-charge. Note: For more details refer technical specification (section-V of tender). | 200.00 | SqM |  | 900.00 | 180000.00 | 800.00 | 160000.00 | 160000.00 | Vijayvargia Electricals
16.00 | Providing and laying cement concrete of 1:3:6 ( 1 Cement :3 Coarse sand : 6 graded stone aggregate 20 mm nominal size) in pole pit, columns, etc. at all level including transporting of concrete to site of laying, shuttering, cost of finishing, curing etc. Complete as per direction of Engineer-in-charge. Note: For more details refer technical specification (section-V of tender). | 100.00 | CuM |  | 6250.00 | 625000.00 | 7000.00 | 700000.00 | 625000.00 | Aditya Techno Products Private Limited
17.00 | Dismantling bituminous road for all thickness by mechanical means i.e. cutter including stacking of serviceable material and disposal of unserviceable material within 1000 metres lead as per direction of engineer-in-charge. The manual cutting of road at anywhere is not allowed. Note: For more details refer technical specification (section-V of tender). | 100.00 | Sqm |  | 415.00 | 41500.00 | 500.00 | 50000.00 | 41500.00 | Aditya Techno Products Private Limited
18.00 | Supply, transportation and installation of ISMB-200, 10-Meter-long single poles including required cross arms suitable for mounting of insulators and earth wire, metallic caution boards, anti-climbing devices for 11 KV overhead line. Painting of pole with 2 coats of red oxide followed by 2 coats of aluminium paint and black enamel paint on 2.5 Mtr height of the pole from bottom. The work of shifting of existing 11KV line conductors, insulators on newly erected poles are under the scope of contractor. Excavation and concreting shall be paid in separate item. Note: For more details refer technical specification (section-V of tender). | 38.00 | Nos. |  | 30900.00 | 1174200.00 | 35000.00 | 1330000.00 | 1174200.00 | Aditya Techno Products Private Limited
19.00 | Supply & Installation of street light poles (Make - Bajaj / Wipro / Crompton Greaves) of 07 M high hot dip galvanised octagonal pole with top 70 mm A/F, bottom 130 mm A/F made up of 3 mm thick HT steel plate having a base plate of size 220x220x12mm thick, 1500mm Long single arm brackets made up of 48.3mm dia pipe. Bakelite sheet with 1 No., 6A, Single Pole C Curve, MCB (Make: Legrand / L&T/ Schnider) and 8-Way heavy duty terminal block for 4Cx16 sq.mm cable etc. Note: For more details refer technical specification (section-V of tender). | 25.00 | Nos. |  | 14000.00 | 350000.00 | 15000.00 | 375000.00 | 350000.00 | Aditya Techno Products Private Limited
20.00 | Construction of foundation for 07 M high hot dip galvanized octagonal pole including excavation, supply & installation of M20 x 700 'J' type EN8 grade foundation bolts with template for pole, reinforcement, shuttering cement concrete M20 grade, 63mm dia PVC pipe for cable entry etc. all complete as per foundations details of manufacturer. Note: For more details refer technical specification (section-V of tender). | 25.00 | Nos. |  | 5100.00 | 127500.00 | 6000.00 | 150000.00 | 127500.00 | Aditya Techno Products Private Limited
21.00 | Supply and installation of street light fittings. Note: For more details refer technical specification (section-V of tender).
21.10 | Supply of 45W LED Street Light luminaries with high power LED, 220-240V AC operation. Die Cast Aluminum housing with UV stabilized prismatic acrylic / glass cover with minimum IP 65. The luminaries should be provided with in-built power unit & electronic driver. The luminaries should be so constructed to ensure that the gear & LED modules are replaceable, if required. The luminaries should be suitable for side entry with pole diameter of 35 mm to 60 mm. Minimum LED Efficacy > 80 Lm/W, Power Factor > 0.9, CRI > 70, Guarantee for 2 Years. Make:- Philipes / Bajaj / Wipro / CG. | 25.00 | Nos. |  | 710.00 | 17750.00 | 4000.00 | 100000.00 | 17750.00 | Aditya Techno Products Private Limited
21.20 | Installation of 45W LED street light luminieries including supply & installation 3 core x 1.5 sq mm PVC copper insulated copper cable are in the scope of the contractor. | 25.00 | Nos. |  | 960.00 | 24000.00 | 500.00 | 12500.00 | 12500.00 | Vijayvargia Electricals
22.00 | Supply & Installation of HT stay set having stay rod, anchor plate thimble, stay wire, stay clamp, turn buckle, 11Kv strain insulator etc. complete set. Excavation & concreting will be paid in separate item. (For more detail refer technical specification). Note: For more details refer technical specification (section-V of tender). | 22.00 | Nos. |  | 3800.00 | 83600.00 | 2000.00 | 44000.00 | 44000.00 | Vijayvargia Electricals
23.00 | Supply and installation by stringing, sagging and binding of 8 SWG G.I. Conductors for earthing/guarding of HT overhead line. Including providing of cradle / cross formation of G.I. wire as per direction of EIC. Note: For more details refer technical specification (section-V of tender). | 4200.00 | Metre |  | 21.00 | 88200.00 | 35.00 | 147000.00 | 88200.00 | Aditya Techno Products Private Limited
24.00 | Supply, fabrication & installation of MS cross arms / brackets / frame / clamp / flat / structural shade/ GI nut bolt washer etc. work includes cutting, welding, bending, drilling, buffing along with painting of two coats of red oxide primer and two coats of aluminium paint on fabricated items as directed by EIC. (for steel mounting other than as give under item no. 18) Note: For more details refer technical specification (section-V of tender). | 2000.00 | Kg |  | 131.00 | 262000.00 | 200.00 | 400000.00 | 262000.00 | Aditya Techno Products Private Limited
25.00 | Excavation of pole pit 1M x 1M x 1.6M to 1.7M deep in all types of ground substrata consisting of hard rock / fragmented rock / soft rock / ordinary soils / filled up ground / murrum requiring use of rock breaker, drilling, chiselling with mechanical / manual means etc. Note: For more details refer technical specification (section-V of tender). | 100.00 | CuM |  | 800.00 | 80000.00 | 2000.00 | 200000.00 | 80000.00 | Aditya Techno Products Private Limited
| Total in Figures |  |  |  |  | 26372377.00 |  | 25600500.00
Lowest Amount Quoted BY: Vijayvargia Electricals(25600500.00)

## BOQ Summary
BOQ Summary Details Tender Title: Supply, installation, testing and commissioning of main distribution electrical system Tender ID: 2025_NPCIL_250903_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Vijayvargia Electricals (BID ID -922916) | 25600500.00 | L1
| 2 | Aditya Techno Products Private Limited (BID ID -922666) | 26372377.00 | L2