## BoQ1
Government eProcurement System Created By: NELLORE BALACHANDRA Created Date/Time: 17-Feb-2026 12:47 PM Tender Title: Miscellaneous GLF works at Tirupati Airport. Tender ID: 2026_AAI_261647_1
Tender Inviting Authority: The Senior Manager(Engg-E)-II, AAI, Tirupati Airport.
Name of Work:Miscellaneous GLF works at Tirupati Airport.
Contract No: AAI/TPT/ENGG (E)/C-03-02/2025-26
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | CREATIVE TRADING CO (GSTN-07AMEPK8023F1Z9) BID ID -966324
[5 empty] | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, installation,testing and commissioning of internally illuminated LED based Mandatory/ Information /Location/VOR check point Runway / Taxiway guidance signage of various sizes made out of 4mm thick glare free poly carbonate sheet at front and body made out of 2.0mmthick powder coated aluminum profile having minimum width of 150mm and supported at back by 50mm dia (Nominal size) die cast aluminum / GI pipe at a separation as required, and frangible coupling as required. Light source shall be high luminous, long life typical 50,000 Hrs type, 0.5 Watt s LED's assembled on aluminum PCB of size 700mm X 20mm and having 11 LED’s per PCB for boards having height 800mm & 500mm X 20mm PCB having 8 LED’s per PCB for board having height 600mm respectively. The thickness of the aluminum PCB should be 2mm in order to ensure proper heat dissipation. These aluminum PCB’s should be placed not more than160mm apart across the length of the board in order to ensure uniform distribution of light across the board. Each board having length from 800mm up to 3000mm should be illuminated by a single converter & by using single isolating transformer of suitable watt age in order to save the capital cost of multiple isolating transformers. Signage shall be suitable for operation on series circuit at variable current from 2.8Amp - 6.6Amp and will give constant brightness for all current variation. All the signage shall have letters and symbols made by computerized cutting of vinyl and pasting on the polycarbonate sheet from inside/outside of the sign face of required color as per ICAO specifications. | 6.00 | Sq.Mtrs |  | 55000.00 | 330000.00 | 330000.00 | CREATIVE TRADING CO
2.00 | Supply of new 4 mm thick UV protected clear poly carbonate sheet with required inscription / vinyl film pasted on inside surface of poly carbonate sheet to enhance durability (life) with double side foam tape for fixing sheet with frame complete as required. | 8.20 | Sq.Mtrs |  | 8000.00 | 65600.00 | 65600.00 | CREATIVE TRADING CO
3.00 | Supply of FAA Certified/FAA Compliance(For Indigenous Manufacturer) INSET type all weather operation LE​D Omni-directional Taxiway light fitting suitable for aviation visual aids requirements of Apron Edge complete with 8 inch shallow base with side hole cable entry and matching body of the fitting, inner body and outer cover made of die cast aluminum alloy complete with connected heat resistant accessories, prism assembly, optical assembly, "O" ring seal, pressure relief test plug, two-pole secondary plug, hardware, lenses and all standard accessories complete etc., as required meeting the requirement of latest ICAO Annex-14 and Specifications of Aerodrome Design Manual Part - IV (Visual Aids) Latest Edition. | 18.00 | Nos |  | 35000.00 | 630000.00 | 630000.00 | CREATIVE TRADING CO
4.00 | Installation of Inset light fittings (Taxiway light) in the concrete/bitumen surface by core cutting with suitable core cutting machine tool for the required size for fixing the shallow box, alignment of the box to match with the runway surface, fixing it using Dobefil compound with hardener, fixing of top assembly on the shallow box, connecting the plug and receptacles of inset fitting with isolation transformer, making all electrical connections, making good the surface to the original finish, testing and commissioning of the whole inset fittings etc., complete as required. (Fitting, Isolation Transformer and connector kits will be supplied by department). | 15.00 | Nos |  | 5000.00 | 75000.00 | 75000.00 | CREATIVE TRADING CO
5.00 | Supply of Inset type high intensity bi-directional Runway Edge light fittings (Yellow/ Clear) suitable for use with halogen type lamp, complete with lens, support mechanism, lens clamping mechanism, gaskets, two pin secondary leads, suitable base for bottom hole entry, 200W halogen lamp and required accessories etc. and conforming to ICAO requirements complete as required. | 2.00 | Nos |  | 65000.00 | 130000.00 | 130000.00 | CREATIVE TRADING CO
6.00 | Supply of Inset type high intensity bi-directional Runway Edge light fittings (Clear /Clear) suitable for use with halogen type lamp, complete with lens, support mechanism, lens clamping mechanism, gaskets, two pin secondary leads, suitable base for bottom hole entry, 200W halogen lamp and required accessories etc. and conforming to ICAO requirements complete as required. | 3.00 | Nos |  | 65000.00 | 195000.00 | 195000.00 | CREATIVE TRADING CO
7.00 | Supply of 200 Watt 6.6/6.6 Amps 5KV grade 50Hz isolating transformer series type encapsulated in polyster resin finally moulded in neoprene type rubber with primary and secondary connections as specified in particular specifications as required. | 6.00 | Nos |  | 4000.00 | 24000.00 | 24000.00 | CREATIVE TRADING CO
8.00 | Supply of 5KV grade plug and receptacle of type I class "B" connector suitable for field attachment with 5KV grade PVC insulated sheathed single core 6 Sq.mm copper conductor cable as per ICAO/CAR compliance and complete as required. | 12.00 | Set |  | 400.00 | 4800.00 | 4800.00 | CREATIVE TRADING CO
9.00 | Supply of 5 KV grade SINGLE CORE 6 Sq.mm size Airfield Lighting Cable with Strandard Copper Conductor PVC insulated, PVC Sheathed Single Core, Unshielded, Anti-Termite & rodent treated UG Cable for use on unearthed system generally conforming to IS 1554, Part-II, 1981 with upto date amendment as required. | 300.00 | Meter |  | 150.00 | 45000.00 | 45000.00 | CREATIVE TRADING CO
10.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of grade exceeding 1.1 KV but not exceeding 11 KV of size upto 35 Sq.mm in the existing RCC/HUME/METAL/HDPE pipe as required. | 280.00 | Meter |  | 20.00 | 5600.00 | 5600.00 | CREATIVE TRADING CO
11.00 | Installation of transformer housing box with a base concrete of 1:3:6 of size 630 x 630 x 100mm thick all round concrete of 1:2:4 150mm thick. The top sloped with 1:2:4 cement concrete including providing and fixing 10" long 1/2" dia "B" class GI pipe with checknuts for drainage of water including excavation of side shoulder and re-filling (wherever the transformer are in a line the same has to be aligned in such a way that the centers fall in a straight line) etc. complete as required. | 6.00 | Job |  | 3000.00 | 18000.00 | 18000.00 | CREATIVE TRADING CO
12.00 | Providing and Fixing of top cover plate made with 5mm thick MS Sheet suitable for existing 330mm dia CI transformer housing box with 6 Nos. Stainless steel M-10 bolts, spring and plain washers including providing and fixing of rubber gasket, painting etc. complete as required. | 6.00 | Each |  | 1200.00 | 7200.00 | 7200.00 | CREATIVE TRADING CO
13.00 | Making field connections by crimping 6 Sq.mm plug and receptacle with the existing 6 Sq.mm Single core copper conductor, PVC insulated, PVC sheathed cable including filling with gap with water sealant material, applying PVC insulation tape over HT tape insulation etc. as required. | 12.00 | Set |  | 200.00 | 2400.00 | 2400.00 | CREATIVE TRADING CO
14.00 | Providing and fixing 6 SWG dia GI wire on surface or in recess for loop earthing along with the existing surface / recessed conduit / submain wiring / cable as required. | 280.00 | Meter |  | 30.00 | 8400.00 | 8400.00 | CREATIVE TRADING CO
15.00 | Supply of Run patch,Self adhesive, Cold applied made of polymer modified High Tak Bituminious Spread Sheet of 1mx10m roll having bond strength of 0.4 Mpa, nominal thickness 3.5-4.0 mm for sealing of potholes/cracks on Runway, Taxiway for both asphalt and concrete surfaces. Note:Qty 1 Number refers to 1 Roll of 1mx10m | 20.00 | Rolls |  | 8000.00 | 160000.00 | 160000.00 | CREATIVE TRADING CO
16.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 metres in width, and lift upto 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres. | 5.00 | Cub.Mtr |  | 5000.00 | 25000.00 | 25000.00 | CREATIVE TRADING CO
17.00 | Earth work in excavation by mechanical means (Hydraulic excavator)/ manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in-charge. | 10.00 | Cub.Mtr |  | 2000.00 | 20000.00 | 20000.00 | CREATIVE TRADING CO
18.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering All work upto plinth level. 1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 20mm nominal size derived from natural sources). | 10.00 | Cub.Mtr |  | 10000.00 | 100000.00 | 100000.00 | CREATIVE TRADING CO
| Total in Figures |  |  |  |  | 1846000.00
Lowest Amount Quoted BY: CREATIVE TRADING CO(1846000.00)

## BOQ Summary
BOQ Summary Details Tender Title: Miscellaneous GLF works at Tirupati Airport. Tender ID: 2026_AAI_261647_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | CREATIVE TRADING CO (BID ID -966324) | 1846000.00 | L1