## BoQ1
Government eProcurement System Created By: Sunil Waghmare Created Date/Time: 17-Mar-2026 12:23 PM Tender Title: Provision of Redundant Power Supply and Other Works in Transmitting Station at Andheri West Tender ID: 2026_AAI_261876_1
Tender Inviting Authority: AAI
Name of work: Provision of Redundant Power Supply and Other Works in Transmitting Station at Andheri (West).
Tender ID : 2026_AAI_261876_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | DOSHI ELECTRIC ENGG. CO. (GSTN-24AAEFD3355K1ZI) BID ID -986098 |  | POWER AUTOMATION AND CONTROLS (GSTN-27ABMPA1796L1Z9) BID ID -987379 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -987983 |  | ABHISHEK INTEGRATIONS LIMITED (GSTN-NA) BID ID -987792
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.10 | Supply,Installation,Testing and Commissioning of outdoor compact substation comprising of following along with (i)11kV, 630A, Horizontal Draw Out VCBs(3 Nos-One incomer and two outgoings) with 230V AC Motor Operated Spring Charging Mechanism with 24V DC Closing /Opening Shunt trip coils,Auxillary switch, Mechanical On/Off Push Button, mechanical Operating Counter with metering Cubical, Auxiliary Relay, Under Voltage Relay, 8 Window Annunciator,Battery Power Pack with 7AH Battery & in built charger for 24V Circuit,CTs,PTS,Protection relays,Indicating lamps. (ii)250 KVA, 11/0.433 KV, 3 Phase, 50HZ, ONAN Cooled Oil immersed Copper Wound Step Down “BIS Marked ” Transformer Complete with first filling of IS:335 ISI Marked Filtered & Dehydrated Transformer Oil, having 7 position Off-Circuit tap changer withtapping range +7.5% to -7.5% in steps of 2.5% each with all standard fittings & accessories including OTI, WTI & Marshalling Box .The Transformer as per comply with BIS-1180(Part-1)2014 EEL- 3 with amendment no.- 4 and Losses @50% Load - not more than 864W and Losses @100% Load - not more than 2488W. (iii)LT Panel comprising of LV Side Incomer – 01 No,400 Amp 4 Pole 35 KA four ploe 415V MCCB with thermal magnetic based release with O/L & S/C protection, RYB Indication Lamp,,Ammeter,Voltmeter - 500A/5A LT CT Cl:1.0. (iv)Enclosure Section:Space Heater with ON/OFF Switch and Thermostat, Single phase switch with socket, LT Cubical illumination Lamp with Door Limit switch and MCB’s for AC / DC Control,MS Steel Sheet enclosure suitable for Outdoor Installation with MS base channel,Provision for receiving Incoming cables through Bottom entry and out going through Bus bar to Transformer panel, Excluding Termination Kit & Glands,Provision for receiving Incoming through bus duct by bus bar and Outgoing thro cable box bottom entry Excluding Termination Kit & Glands,Bus bar and earth bus of adequate rating,Paint shade: Siemens Grey ( RAL 7032). (v)Providing RCC foundation suitable for the structural load of the compact substation,considering the site soil bearing capacity and as per OEM recommendations with provision for cable entry and foundation shall be at suitable height above ground level to avoid water entry. (vi)Provision of roofing and supporting steel structure suitable for the compact substation. (vii)All other miscellaneous works and internal connections etc for sucessful commissioning of the installation. | 1.00 | Job |  | 2950000.00 | 2950000.00 | 3170000.00 | 3170000.00 | 3105000.00 | 3105000.00 | 2898000.00 | 2898000.00 | 2898000.00 | ABHISHEK INTEGRATIONS LIMITED
1.20 | Supply of HT Three Core Power Cables of size 3 Core 120 sq.mm - Aluminium Conductor A2XFY 11 KV Earthed Cables with Stranded Compacted Circular Aluminium Conductor, Conductor Screen with Extruded Semi Conducting Compound, XLPE Insulated, Insulation Screening with Extruded Semi Conducting Compound in Combination with Copper Tape, Cores Laid Up,Innersheath of PVC, Galvanised Steel Flat Strip Armoured, & Overall PVC Sheathed Cable Conforming to IS 7098 (Part-2) 2011 with upto Date Amendments | 200.00 | Meters |  | 1200.00 | 240000.00 | 1000.00 | 200000.00 | 1400.00 | 280000.00 | 1001.00 | 200200.00 | 200000.00 | POWER AUTOMATION AND CONTROLS
1.30 | Laying of one number PVC/XLPE Insulated PVC sheathed power cable of 11 KV grade upto 120 sq.mm direct in ground including excavation,sand cushioning,protective covering,refilling the trench etc as required. | 40.00 | Meters |  | 500.00 | 20000.00 | 350.00 | 14000.00 | 560.00 | 22400.00 | 180.00 | 7200.00 | 7200.00 | ABHISHEK INTEGRATIONS LIMITED
1.40 | Laying of one number PVC/XLPE Insulated PVC sheathed power cable of 11 KV grade upto 120 sq.mm in the existing RCC/HUME/METAL pipe as required. | 80.00 | Meters |  | 80.00 | 6400.00 | 300.00 | 24000.00 | 100.00 | 8000.00 | 30.00 | 2400.00 | 2400.00 | ABHISHEK INTEGRATIONS LIMITED
1.50 | Laying of one number PVC/XLPE Insulated PVC sheathed power cable of 11 KV grade upto 120 sq.mm in the existing masonary open duct as required. | 80.00 | Meters |  | 60.00 | 4800.00 | 250.00 | 20000.00 | 80.00 | 6400.00 | 30.00 | 2400.00 | 2400.00 | ABHISHEK INTEGRATIONS LIMITED
1.60 | Supply of LT Power Cables - Aluminium stranded conductor A2XFY, XLPE Insulated, Cores Laid Up, PVC Innersheathed, Armoured with galvanised steel strip, Extruded PVC Type ST2 Outer Sheathed, 650 V(Conductor to earth)/1100 V(between conductors) grade as per IS 7098 (Part 1) 1988 with upto Date Amendments. 3.5 core 400 sq.mm | 200.00 | Meters |  | 2000.00 | 400000.00 | 1911.00 | 382200.00 | 2450.00 | 490000.00 | 1955.00 | 391000.00 | 382200.00 | POWER AUTOMATION AND CONTROLS
1.70 | Laying of one number PVC/XLPE Insulated PVC sheathed power cable of 1.1 KV grade and size above 185 Sq.mm and upto 400 sq.mm direct in ground including excavation,sand cushioning,protective covering,refilling the trench etc as required. | 20.00 | Meters |  | 500.00 | 10000.00 | 350.00 | 7000.00 | 500.00 | 10000.00 | 180.00 | 3600.00 | 3600.00 | ABHISHEK INTEGRATIONS LIMITED
1.80 | Laying of one number PVC/XLPE Insulated PVC sheathed power cable of 1.1 KV grade and size above 185 Sq.mm and upto 400 sq.mm in the existing RCC/HUME/METAL pipe as required. | 100.00 | Meters |  | 100.00 | 10000.00 | 300.00 | 30000.00 | 150.00 | 15000.00 | 80.00 | 8000.00 | 8000.00 | ABHISHEK INTEGRATIONS LIMITED
1.90 | Laying of one number PVC/XLPE Insulated PVC sheathed power cable of 1.1 KV grade and size above 185 Sq.mm and upto 400 sq.mm in the existing masonary open duct as required. | 50.00 | Meters |  | 80.00 | 4000.00 | 250.00 | 12500.00 | 120.00 | 6000.00 | 80.00 | 4000.00 | 4000.00 | DOSHI ELECTRIC ENGG. CO., ABHISHEK INTEGRATIONS LIMITED
2.00 | Laying and fixing of one number PVC/XLPE Insulated PVC sheathed power cable of 1.1 KV grade and size above 185 Sq.mm and upto 400 sq.mm(Clamped with 40 X 3 mm MS flat clamp) on wall surface as required. | 10.00 | Meters |  | 200.00 | 2000.00 | 350.00 | 3500.00 | 250.00 | 2500.00 | 80.00 | 800.00 | 800.00 | ABHISHEK INTEGRATIONS LIMITED
2.10 | Laying and fixing of one number PVC/XLPE Insulated PVC sheathed power cable of 1.1 KV grade and size above 185 Sq.mm and upto 400 sq.mm(Clamped with 40 X 3 mm MS flat clamp) on cable tray as required. | 20.00 | Meters |  | 200.00 | 4000.00 | 300.00 | 6000.00 | 200.00 | 4000.00 | 80.00 | 1600.00 | 1600.00 | ABHISHEK INTEGRATIONS LIMITED
2.20 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5 C x 400 sq mm (82 mm) | 5.00 | Each |  | 1800.00 | 9000.00 | 5225.00 | 26125.00 | 1750.00 | 8750.00 | 3255.00 | 16275.00 | 8750.00 | Awasthi Electric Works
2.30 | supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required: 120 sq. mm | 4.00 | Each |  | 7000.00 | 28000.00 | 4000.00 | 16000.00 | 8000.00 | 32000.00 | 3839.00 | 15356.00 | 15356.00 | ABHISHEK INTEGRATIONS LIMITED
2.40 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 300.00 | Meters |  | 25.00 | 7500.00 | 25.00 | 7500.00 | 45.00 | 13500.00 | 22.00 | 6600.00 | 6600.00 | ABHISHEK INTEGRATIONS LIMITED
2.50 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required. | 8.00 | Set |  | 9000.00 | 72000.00 | 6100.00 | 48800.00 | 18000.00 | 144000.00 | 9768.00 | 78144.00 | 48800.00 | POWER AUTOMATION AND CONTROLS
2.60 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 meter long etc. with charcoal/ coke and salt as required.) | 2.00 | Set |  | 19000.00 | 38000.00 | 15500.00 | 31000.00 | 26500.00 | 53000.00 | 22000.00 | 44000.00 | 31000.00 | POWER AUTOMATION AND CONTROLS
2.70 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 40.00 | Mtr |  | 200.00 | 8000.00 | 220.00 | 8800.00 | 280.00 | 11200.00 | 158.00 | 6320.00 | 6320.00 | ABHISHEK INTEGRATIONS LIMITED
2.80 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 50.00 | Mtr |  | 650.00 | 32500.00 | 2700.00 | 135000.00 | 650.00 | 32500.00 | 378.00 | 18900.00 | 18900.00 | ABHISHEK INTEGRATIONS LIMITED
2.90 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 20.00 | Mtr |  | 180.00 | 3600.00 | 175.00 | 3500.00 | 250.00 | 5000.00 | 125.00 | 2500.00 | 2500.00 | ABHISHEK INTEGRATIONS LIMITED
3.00 | Supplying and laying 25 mm X 5 mm copper strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of brass nut bolt & spring washer spaced at 50mm) | 10.00 | Mtr |  | 1400.00 | 14000.00 | 1450.00 | 14500.00 | 1800.00 | 18000.00 | 1507.00 | 15070.00 | 14000.00 | DOSHI ELECTRIC ENGG. CO.
3.10 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 15.00 | Mtr |  | 1850.00 | 27750.00 | 1400.00 | 21000.00 | 2000.00 | 30000.00 | 1727.00 | 25905.00 | 21000.00 | POWER AUTOMATION AND CONTROLS
3.20 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 10.00 | Mtr |  | 1400.00 | 14000.00 | 1300.00 | 13000.00 | 1700.00 | 17000.00 | 1480.00 | 14800.00 | 13000.00 | POWER AUTOMATION AND CONTROLS
3.30 | SITC of 400 A,415 Volt 4 Pole onload change over switch,AC23A utilization category, on surface along with sheet steel powder coated enclosure and extended handle,connections etc as required | 1.00 | Each |  | 25000.00 | 25000.00 | 67000.00 | 67000.00 | 28000.00 | 28000.00 | 39062.00 | 39062.00 | 25000.00 | DOSHI ELECTRIC ENGG. CO.
3.40 | Supply, Installation, Testing and Commissioning of Air Cooled Floor standing Tower type split Air conditioners complete with Indoor unit(IDU),Out door unit (ODU), surface / concealed copper Refrigerant piping with insulation (closed cell elastomeric nitrile rubber tubular pipe section) upto 5 Mtr (IDU to ODU), copper power cable upto 5.5 Mtr (IDU to ODU), i/c drain pipe of suitable length and size. R-32/R-410/R-407C Green Refrigerant,wireless Remote control, suitable for working between 180-260V with low &high voltage cutoff and 50 hz ,1 phase AC supply capable of performing cooling, dehumidification, air circulation of following capacity with Scroll /rotary with min 5 year Original Equipment Manufacturer (OEM) warranty both compressor and Printed Circuit Board (PCB). as specified. The system shall be able to deliver 100% of the rated capacity as per relevant IS Code.The lab testing reports as per IS: 1391 shall be submitted from National Accreditation Board for Testing and Calibration Laboratories (NABL) accredited as per International Electro technical Commission (IEC) 17025 standards / Central Power Research Institute (CPRI)/Electrical Research and Development Association (ERDA)with Original Equipment Manufacturer (OEM) etc. complete as per CPWD specification and as per IS: 1391 as required (Cooling Only 3.8 TR BEE 5 Star Rating) (CPWD DSR E&M Vol-II-2025,Item8.5.6) | 4.00 | Each |  | 165000.00 | 660000.00 | 190000.00 | 760000.00 | 135000.00 | 540000.00 | 97750.00 | 391000.00 | 391000.00 | ABHISHEK INTEGRATIONS LIMITED
3.50 | Percentage above or below on the rates of DSR(E&M)-2025 (CPWD) items worth totalling 500000/- for execution of items on requirement basis(except items mentioned above in this BOQ). The rates quoted shall be without GST. (The payment will be made after deducting GST from DSR rate and adding labour cess of 1%). (Rate to be paid = (DSR rate/1.18 x R) ie, if the quoted rate is 1.25 then R = 1.25 and if quoted rate is 0.75, R=0.75 | 1.00 | Job |  | .80 | .80 | 400000.00 | 400000.00 | 400000.00 | 400000.00 | 500000.00 | 500000.00 | .80 | DOSHI ELECTRIC ENGG. CO.
| Total in Figures |  |  |  |  | 4590550.80 |  | 5421425.00 |  | 5282250.00 |  | 4693132.00
Lowest Amount Quoted BY: DOSHI ELECTRIC ENGG. CO.(4590550.80)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Redundant Power Supply and Other Works in Transmitting Station at Andheri West Tender ID: 2026_AAI_261876_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | DOSHI ELECTRIC ENGG. CO. (BID ID -986098) | 4590550.80 | L1
| 2 | ABHISHEK INTEGRATIONS LIMITED (BID ID -987792) | 4693132.00 | L2
| 3 | Awasthi Electric Works (BID ID -987983) | 5282250.00 | L3
| 4 | POWER AUTOMATION AND CONTROLS (BID ID -987379) | 5421425.00 | L4