## BoQ1
Government eProcurement System Created By: Sachin Khangar Created Date/Time: 05-Mar-2026 01:38 PM Tender Title: Provision of Air conditioning in new CCR room and ATC substation i/c air conditioning in Aerobridge tunnels and other ancillary work at Vadodara Airport Tender ID: 2026_AAI_262135_1
Tender Inviting Authority: Joint.Gen. Manager(E-E), AAI, CA, Vadodara
Name of Work :- Provision of Air conditioning in new CCR room and ATC substation i/c air conditioning in Aerobridge tunnels and other ancillary work at Vadodara Airport.
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Aarham Engineers Pvt. Ltd. (GSTN-07AAACA8254F1ZU) BID ID -961283 |  | AIRON CORPORTION (GSTN-24AAFFA7652R1ZY) BID ID -966973 |  | M/s. PRANAM HVAC ENGINEERING PVT. LTD. (GSTN-24AAHCP2093C1ZP) BID ID -967434 |  | Variant Infratech Private Limited (GSTN-NA) BID ID -978783
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, installation, testing & commissioning of Floor Mounted AMCA standard Backward curved fan type Air Handling unit of following capacity with built in drive and drive package alongwith elect. Motor, AHU suitable for out door installation only. starter and cabling as per the specifications
2.00 | Body Construction : Supporting hollow extruded heavy-duty AL with internal coving tharmal break section. 50mmthick Puf Panel with PUF insulation with density of 40 KG/Cm2. Inner skinn 22g in 120 GSM , Outer Skinn Precoated 22g, Base Frame of Unit in GSS. In Aluminum section structure. Total Unit Height not more than 2100mm
3.00 | Fan Section : AMCA standard Backward curved fan mounted with IE1 TEFC motor with Drive Package installed on Aluminum Formed ‘C’ section with Cushy foot mount vibration pad. Fan section internally Accoustic Linned with 10 mm Open cell Insulation covered with 24 g Aluminiume perforated sheet.Fire retardant canvass connection within the units. Aluminum Aerofoil Supply air volume control Damper is part of This section
4.00 | Cooling Coil : Cooling Coil made out from Copper tube (Plain), 0.41 mm, CopperAL fins, 0.13 mm Thickness, 11-12 FP. 4 Row Deep DX cooling Coil with Single/ Multiple Circuite. Coil Area @ 500FPM insulated S.S.Drain tray in S.S.304 Construction with 18 G. Insulated with 13mm Thick Insulation
5.00 | Filter Section: Filter Frame in Aluminium Construction. Filter body from GI with minimum 50mm Depth. 7 ply 10 micron Filter down to 90%. Filter media Synthetic (Non woven type) HDPE washable type supported by rods. Not more than 500FPM
6.00 | Return Air Section : Made out From hollow extruded heavy-duty AL with internal coving tharmal break section. 50mmthick Puf Panel with PUF insulation with density of 40 KG/Cm2. Inner skinn 22g in 120 GSM , Outer Skinn Precoated 22g.Base Frame of Unit in GSS Same As other section of Unit. Return Air duct connection with Aerofoil Aluminium Damper, Fresh Air Cut out with Aerofoil Aluminium Damper are part of this Section Only.
7.00 | 8000 CFM @40 mm SP. Cooling Capacity 22 TR | 1.00 | Nos. |  | 512450.00 | 512450.00 | 378718.00 | 378718.00 | 565111.27 | 565111.27 | 740000.00 | 740000.00 | 378718.00 | AIRON CORPORTION
8.00 | Air Cooled DX type Out Door Unit
9.00 | Supply, installation, testing & commissioning of High COP DX Air Cooled Outdoor Condensing Unit consisting of high performance, low noise, scroll compressors, condenser coil, condenser fan, fan motor, microprocessor panel with display, wired remote controller with timed scheduler enclosed in a powder coated sheet metal casing, controlling the supplied indoor units. The unit shall have high static condenser fan. The unit shall have provision for control & monitoring from a central location with BACKNET/LANWORKS protocol, all enclosed in a powder coated sheet metal casing, supporting stand, coil protection mesh, vibration isolation pads, etc. out door unit suitable for 415V for outdoor, suitable for Double Skinned Air Handling Unit, set complete with Out door units, Refrigerant controllers, Tempraure Controler, Change over Timer, Powder Coated stands out door unit, accessories including fully charge refrigerant R410A as per specification only.
10.00 | Supply, Installation, Testing and Comissioning of Out-door units of following capacity in suitable configurations at design conditions (110/78 deg F) including, Isolation valves, Drier, Expation Valve, Thermostat, controling devices and as per Technical specifications with Double Skinned Air Handling Unit. Net Capacity: - Unit will Deliver Capacity @ 41 Deg.C Ambient Condition with inside Condition of 25 Deg C & 50% RH. Other Requirement: - Supply, Installation, Testing and Commissioning (SITC) of LT Panel (Sl. No. 1 & 2), wall/floor mounted type, complete with suitably rated switchgears, starters and protective devices for the proper functioning of Air Cooled DX type Outdoor Units (ODUs), including interconnection with appropriate rating of power cables between LT Panel and AHUs/ODUs, provision of control cabling for signal, interlock and control between LT Panel, Air Cooled DX type ODUs & their IDUs, insulating mats conforming to IS standards at the front and rear of LT Panels, and all other accessories required for safe and reliable operation; the scope shall be comprehensive in all respects, with the clear stipulation that all required cables (both power and control) from ODUs to VRF/IDUs shall be supplied and laid by the tenderer, who must quote accordingly for each item inclusive of cabling, terminations and associated works.
11.00 | 11.00 Tr (2 working + 1 standBy) | 3.00 | set |  | 216250.00 | 648750.00 | 175000.00 | 525000.00 | 168586.67 | 505760.01 | 402540.00 | 1207620.00 | 505760.01 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
12.00 | Ceilling Suspended Ductable type Split Air Conditioner
13.00 | Supply, installation, testing & commissioning of Ductable split unit with both inside evaporation & outside condensing units, refrigerant piping, Isolation valves, expansion valve, piping insulation & other accessories with first charge of refrigeration gas. The Actual Capacities indicated here under shall be at Ambient conditions capacity including supply, installation, testing & commissioning (SITC) of LT Panel - Wall/Floor mounted type, comprising of suitable capacity switchgears for proper functioning of Ceilling Suspended Ductable type Split Air Conditioner and their Outdoor Units, including appropriate starters, interconnecting power cable & control cabling, etc., complete in all respects as required. Supply, Installation, Testing and Commissioning (SITC) of LT Panel (at sl. no. 5), wall/floor mounted type, complete with suitably rated switchgears, starters and protective devices for the proper functioning of Ceilling Suspended Ductable type Split Air Conditioner and their Outdoor Units, including interconnection with appropriate rating of power cables between LT Panel and Ceilling Suspended Ductable type Split Air Conditioner and their Outdoor Units, provision of control cabling for signal, interlock and control between LT Panel, Ceilling Suspended Ductable type Split Air Conditioner and their Outdoor Units, insulating mats conforming to IS standards at the front and rear of LT Panels, and all other accessories required for safe and reliable operation; the scope shall be comprehensive in all respects, with the clear stipulation that all required cables (both power and control) from Ceilling Suspended Ductable type Split Air Conditioner and their Outdoor Units shall be supplied and laid by the tenderer, who must quote accordingly for each item inclusive of cabling, terminations and associated works.
14.00 | 11.00 Tr (4 working + 2 standBy) | 6.00 | set |  | 302250.00 | 1813500.00 | 216450.00 | 1298700.00 | 254028.13 | 1524168.78 | 269835.00 | 1619010.00 | 1298700.00 | AIRON CORPORTION
15.00 | 8.50 Tr (2 working + 1 standBy) | 3.00 | Set |  | 245800.00 | 737400.00 | 182900.00 | 548700.00 | 247153.87 | 741461.61 | 206654.00 | 619962.00 | 548700.00 | AIRON CORPORTION
16.00 | Net Capacity: - Unit will Deliver Capacity @ 41 Deg.C Ambient Condition with inside Condition of 25 Deg C & 50% RH.
17.00 | VRF/VRV Out Door Unit
18.00 | Supply, installation, testing & commissioning of High COP Variable Refrigerant Flow/ Variable Refrigerant Volume Air conditioning system (Cooling only) facility suitable for 380~415 V for outdoor and 230 + 5% volts for Indoor units complete with indoor and outdoor units, controllers, accessories including fully charge refrigerant R410A/non-CFC as per specification for the following configuration including Supply, Installation, Testing and Commissioning (SITC) of LT Panel (at sl. no. 5), wall/floor mounted type, complete with suitably rated switchgears, starters and protective devices for the proper functioning of Air Handling Units (AHUs) and their associated Outdoor Units (ODUs), including interconnection with appropriate rating of power cables between LT Panel and AHUs/ODUs, provision of control cabling for signal, interlock and control between LT Panel, AHUs, ODUs and VRF/Indoor Units (IDUs), insulating mats conforming to IS standards at the front and rear of LT Panels, and all other accessories required for safe and reliable operation; the scope shall be comprehensive in all respects, with the clear stipulation that all required cables (both power and control) from ODUs to VRF/IDUs shall be supplied and laid by the tenderer, who must quote accordingly for each item inclusive of cabling, terminations and associated works.
19.00 | Net Capacity: - Unit will Deliver Capacity @ 41 Deg.C Ambient Condition with inside Condition of 25 Deg C & 50% RH.
20.00 | Unit COP Minimum 3.25
21.00 | 8 HP ODU ( 6.6 TR) | 5.00 | Set |  | 219000.00 | 1095000.00 | 201600.00 | 1008000.00 | 264434.00 | 1322170.00 | 204860.00 | 1024300.00 | 1008000.00 | AIRON CORPORTION
22.00 | VRF/VRV In Door Unit
23.00 | SITC of Ceiling suspended One way Cassettes with refrigerant, 1 way flow type Fan Coil Units with energy saving Single Phase BLDC motor / EC Motor (Electronically Commuted Motor), Filter section with prefilters, Hydrophilic Al fins and Copper Cooling Coil section with minimum 2 Row and minimum 13 FPI, in-built condensate drain pump, Insulated extended L shaped Drain Pan. Unit shall be supplied with Individual or BMS compatible Digital Group Controller, necessary Networking Adapters and Gateway with interface modbus protocol to connect the DDC panel (230V operating / Power On / Off provision, 3 speed fan switch & Temp Edit facility / Digital Temp Display) and supplied with Temrature Controller, Y joint and Decorative Panel suits to FCU as required.
24.00 | Unit Capacity 2.1 Tr (For Departure VIP room) | 3.00 | Set |  | 63000.00 | 189000.00 | 34800.00 | 104400.00 | 44145.00 | 132435.00 | 65000.00 | 195000.00 | 104400.00 | AIRON CORPORTION
25.00 | SITC of Ceiling suspended TWO way Cassettes with refrigerant, 2 way flow type Fan Coil Units with energy saving Single Phase BLDC motor / EC Motor (Electronically Commuted Motor), Filter section with prefilters, Hydrophilic Al fins and Copper Cooling Coil section with minimum 2 Row and minimum 13 FPI, in-built condensate drain pump, Insulated extended L shaped Drain Pan. Unit shall be supplied with Individual or BMS compatible Digital Group Controller, necessary Networking Adapters and Gateway with interface modbus protocol to connect the DDC panel (230V operating / Power On / Off provision, 3 speed fan switch & Temp Edit facility / Digital Temp Display) and supplied with Temrature Controller, Y joint and Decorative Panel suits to FCU as required.
26.00 | Unit Capacity 2.1 Tr (For Arrival VIP room + CIP room) | 5.00 | Set |  | 58500.00 | 292500.00 | 47583.00 | 237915.00 | 55045.00 | 275225.00 | 102000.00 | 510000.00 | 237915.00 | AIRON CORPORTION
27.00 | Refrigerant Piping and Insulation
28.00 | Refrigerant Piping
29.00 | Insulated Refrigerant piping between the indoor units and the outdoor units with minimum pipe thickness of 1.6 mm. The Route length of Refrigerant piping between the outdoor units & Indoor units shall be as per the drawings furnished. The price quoted shall include liquid receiver, on-line accumulator, oil separator & other safety devices, Control valves, Accessories, Hardwares for required for total nos of circuits, if required for long distance and first charge of refrigerant & oil for the complete system including piping length required.
30.00 | Refrigerant piping with hard/soft copper tube complete with all accessories & rod supporting work etc. of following capacity
31.00 | All refrigerant pipes shall be of hard drawn pipes in straight lengths shall be used. Wall thickness of all piping shall be 16 guage, 1.6 mm thick
32.00 | The refrigerant pipes to be laid in a suitable size ladder type cable tray. The price quoted shall also include the cost of the cable tray and the supporting arrangement for the cable tray.
33.00 | Class 'O' Nitrile rubber insulation should be used to insulate the refrigerant pipes .
34.00 | The price quoted shall include cost of refrigerant & oil, necessary supports, supporting tray, pressure testing, vaccumization & commissioning, etc.
35.00 | 8 HP ODU ( 6.5 TR) | 140.00 | Rmt |  | 3900.00 | 546000.00 | 2100.00 | 294000.00 | 2201.80 | 308252.00 | 1850.00 | 259000.00 | 259000.00 | Variant Infratech Private Limited
36.00 | 8.50 TR Dx System | 90.00 | Rmt |  | 4800.00 | 432000.00 | 1908.00 | 171720.00 | 3182.80 | 286452.00 | 1850.00 | 166500.00 | 166500.00 | Variant Infratech Private Limited
37.00 | 11.00 TR Dx System | 180.00 | Rmt |  | 4800.00 | 864000.00 | 1620.00 | 291600.00 | 3182.80 | 572904.00 | 2600.00 | 468000.00 | 291600.00 | AIRON CORPORTION
38.00 | Refrigerant Pipe (Copper pipe) Make: - Mandev, RR, Rajco.
39.00 | Insulated UPVC Drain Piping
40.00 | Insulated Drain piping between the indoor units and nearest suitable drain Point with UPVC Pipe & UPVC Fitting. The Route length of drain piping shall be as per the drawings furnished. The price quoted shall include 10 mm Class O Insulation, accessories, hardwares, support system for required for leak proof piping work .
41.00 | 25 mm Dia | 80.00 | Rmt |  | 200.00 | 16000.00 | 300.00 | 24000.00 | 204.92 | 16393.60 | 200.00 | 16000.00 | 16000.00 | Aarham Engineers Pvt. Ltd., Variant Infratech Private Limited
42.00 | 32 mm Dia | 150.00 | Rmt |  | 250.00 | 37500.00 | 375.00 | 56250.00 | 245.25 | 36787.50 | 230.00 | 34500.00 | 34500.00 | Variant Infratech Private Limited
43.00 | 50 mm Dia | 75.00 | Rmt |  | 380.00 | 28500.00 | 495.00 | 37125.00 | 400.03 | 30002.25 | 290.00 | 21750.00 | 21750.00 | Variant Infratech Private Limited
44.00 | 80 mm Dia | 90.00 | Rmt |  | 590.00 | 53100.00 | 575.00 | 51750.00 | 1182.65 | 106438.50 | 340.00 | 30600.00 | 30600.00 | Variant Infratech Private Limited
45.00 | 100 mm Dia | 50.00 | Rmt |  | 730.00 | 36500.00 | 630.00 | 31500.00 | 1744.00 | 87200.00 | 380.00 | 19000.00 | 19000.00 | Variant Infratech Private Limited
46.00 | SITC of G.I. Sheet Metal Duct Work As Per IS-655
47.00 | Supply, installation, testing & commissioning of G.I. Sheet Metal Duct (Rectangular)
48.00 | 0.63 MM (24G) | 245.00 | MT² |  | 1240.00 | 303800.00 | 753.00 | 184485.00 | 1051.85 | 257703.25 | 1350.00 | 330750.00 | 184485.00 | AIRON CORPORTION
49.00 | 0.80 MM (22G) | 215.00 | MT² |  | 1430.00 | 307450.00 | 954.00 | 205110.00 | 1160.85 | 249582.75 | 1450.00 | 311750.00 | 205110.00 | AIRON CORPORTION
50.00 | 1.00 MM (20G) | 55.00 | MT² |  | 1640.00 | 90200.00 | 994.00 | 54670.00 | 1367.95 | 75237.25 | 1550.00 | 85250.00 | 54670.00 | AIRON CORPORTION
51.00 | Supply, installation, testing & commissioning of G.I. Sheet Metal Duct (Circular)
52.00 | 0.63 MM (24G) | 40.00 | MT² |  | 1270.00 | 50800.00 | 1386.00 | 55440.00 | 1689.50 | 67580.00 | 1350.00 | 54000.00 | 50800.00 | Aarham Engineers Pvt. Ltd.
53.00 | 0.80 MM (22G) | 60.00 | MT² |  | 1550.00 | 93000.00 | 1463.00 | 87780.00 | 1907.50 | 114450.00 | 1450.00 | 87000.00 | 87000.00 | Variant Infratech Private Limited
54.00 | Supply, installation, testing & commissioning of Powder Coated Extruded Aluminium Linear Grilles of required Airflow Angles with VCD
55.00 | Supply, installation, testing & commissioning of Aluminium Linear Grilles in any size without VCD | 12.00 | MT² |  | 7800.00 | 93600.00 | 4988.00 | 59856.00 | 5613.50 | 67362.00 | 10000.00 | 120000.00 | 59856.00 | AIRON CORPORTION
56.00 | Supply, installation, testing & commissioning of Aluminium Linear Grilles in any size with VCD | 25.00 | MT² |  | 11800.00 | 295000.00 | 9628.00 | 240700.00 | 10038.90 | 250972.50 | 12500.00 | 312500.00 | 240700.00 | AIRON CORPORTION
57.00 | Supply, installation, testing & commissioning of Aluminiun Aerofoil sectional Diffuser with dampers of following size
58.00 | 595 x 595 mm (Grid Diffuser) | 30.00 | Nos. |  | 2850.00 | 85500.00 | 2598.00 | 77940.00 | 4251.00 | 127530.00 | 2500.00 | 75000.00 | 75000.00 | Variant Infratech Private Limited
59.00 | Supply, installation, testing & commissioning of duct silencers to be provided in SA duct. The silencers shall be designed to attenuate noise to meet NC - 50 curve. Silencers shall consists of incombustible, inorganic, inert non shedding glass fibre of sufficient density as acoustic fill to obtain above noise reduction. IN 900 MM LENGTH | 10.00 | MT² |  | 41000.00 | 410000.00 | 6100.00 | 61000.00 | 15260.00 | 152600.00 | 1800.00 | 18000.00 | 18000.00 | Variant Infratech Private Limited
60.00 | Supply, installation, testing & commissioning of motorised fire & smoke dampers with actuators in supply / return air duct / path of conditioned air in AHU rooms. Fire dampers shall be complete with in-built temperature and smoke sensors and auxiliary switch to trip the AHUs and close the dampers simultaneously. These dampers shall also actuate in response to signal from central smoke alarm system which shall trip the AHU along with closing the damper. Testing of fire dampers shall be as per UL 555 and certified by CBRI. Annular space / Gap around ducting, between ducting & fire damper and around fire damper shall be sealed to make it air tight by Hilti make Fire stop mortar, CP 636 or equivalent other material. SIZE OF FIRE DAMPER - as per duct size | 10.00 | MT² |  | 32000.00 | 320000.00 | 31181.00 | 311810.00 | 16350.00 | 163500.00 | 26500.00 | 265000.00 | 163500.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
61.00 | Supply, installation, testing & commissioning of volume dampers with locking arragment in supply / return air duct / path of conditioned air. SIZE OF DAMPER - as per duct size | 6.00 | MT² |  | 9900.00 | 59400.00 | 5452.00 | 32712.00 | 7030.50 | 42183.00 | 7500.00 | 45000.00 | 32712.00 | AIRON CORPORTION
62.00 | Duct Insulation Work
63.00 | Supply, installation, testing & commissioning of of Duct acoustic insulation with Opencell Insulation from the inside of the duct as per specifications. 13 MM THICK (Minimum) | 90.00 | MT² |  | 1250.00 | 112500.00 | 708.00 | 63720.00 | 721.58 | 64942.20 | 1450.00 | 130500.00 | 63720.00 | AIRON CORPORTION
64.00 | Supply, installation, testing & commissioning of Thermal insulation of Ducts with Close Cell Nitrile on the duct surface area as per specifications. 13 MM THICK (Minimum) | 515.00 | MT² |  | 1150.00 | 592250.00 | 191.00 | 98365.00 | 321.55 | 165598.25 | 1050.00 | 540750.00 | 98365.00 | AIRON CORPORTION
65.00 | Supply and fixing of XLPE Aluminium foil-faced nitrile rubber insulation of following thickness on existing SA (Supply Air), RA (Return Air), and FA (Fresh Air) ducting, including all accessories, adhesives, supports, bends, joints, and labour, etc. complete in all respects as per site requirements and engineer-in-charge's instructions.
66.00 | 25mm | 150.00 | RMT |  | 1500.00 | 225000.00 | 522.00 | 78300.00 | 430.55 | 64582.50 | 1650.00 | 247500.00 | 64582.50 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
67.00 | 19mm | 150.00 | RMT |  | 1380.00 | 207000.00 | 377.00 | 56550.00 | 392.40 | 58860.00 | 1350.00 | 202500.00 | 56550.00 | AIRON CORPORTION
68.00 | 13mm | 150.00 | RMT |  | 1260.00 | 189000.00 | 272.00 | 40800.00 | 327.00 | 49050.00 | 1050.00 | 157500.00 | 40800.00 | AIRON CORPORTION
69.00 | Dismantling and removal of existing installed insulation on SA (Supply Air), RA (Return Air), and FA (Fresh Air) ducting, including aluminium cladding, adhesives, fasteners, supports, and associated accessories, with careful handling to avoid damage to ductwork, stacking of serviceable material as directed, and disposal of unserviceable material outside airport premises, complete in all respects as per site conditions and engineer-in-charge's instructions. | 250.00 | RMT |  | 125.00 | 31250.00 | 200.00 | 50000.00 | 141.70 | 35425.00 | 650.00 | 162500.00 | 31250.00 | Aarham Engineers Pvt. Ltd.
70.00 | Supply and fixing of 24 SWG Aluminium sheet cladding on existing SA (Supply Air), RA (Return Air), and FA (Fresh Air) ducting, including cutting, bending, shaping, jointing, sealing with suitable adhesive/tape, and fixing with appropriate fasteners and supports, complete in all respects as per site conditions and instructions of engineer-in-charge. (Finished surface measurement shall be considered for payment.) | 200.00 | RMT |  | 1480.00 | 296000.00 | 700.00 | 140000.00 | 632.20 | 126440.00 | 1300.00 | 260000.00 | 126440.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
71.00 | Repairing and modification of existing installed aluminium cladding on CHW (Chilled Water) piping of any diameter, wherever required, including removal of damaged portions, reshaping, refixing, sealing of joints with suitable adhesive/tape, and replacement of unserviceable sections with matching suitable size aluminium sheets, complete in all respects as per site conditions and instructions of engineer-in-charge. | 100.00 | RMT |  | 550.00 | 55000.00 | 675.00 | 67500.00 | 632.20 | 63220.00 | 1300.00 | 130000.00 | 55000.00 | Aarham Engineers Pvt. Ltd.
72.00 | ELECTRICAL & CIVIL WORK
73.00 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
74.00 | 600 mm width X 62.5 mm depth X 2.0 mm thickness | 150.00 | Rmt |  | 1800.00 | 270000.00 | 1355.00 | 203250.00 | 1831.20 | 274680.00 | 2500.00 | 375000.00 | 203250.00 | AIRON CORPORTION
75.00 | 300 mm width X 62.5 mm depth X 2.0 mm thickness | 350.00 | Rmt |  | 1100.00 | 385000.00 | 800.00 | 280000.00 | 1153.22 | 403627.00 | 1500.00 | 525000.00 | 280000.00 | AIRON CORPORTION
76.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 500.00 | Rmt |  | 55.00 | 27500.00 | 51.00 | 25500.00 | 43.60 | 21800.00 | 25.00 | 12500.00 | 12500.00 | Variant Infratech Private Limited
77.00 | Providing and fixing 25mm X 5 mm G.I strip on surface or in recess for connections etc. as required. | 180.00 | Rmt |  | 230.00 | 41400.00 | 108.00 | 19440.00 | 218.00 | 39240.00 | 250.00 | 45000.00 | 19440.00 | AIRON CORPORTION
78.00 | Supply, installation, testing & commissioning of M.S. fabrication work, including making of stands, steps and other required supports for crossing the chilled water pipelines, etc., complete as required. | 1500.00 | KG |  | 160.00 | 240000.00 | 160.00 | 240000.00 | 163.50 | 245250.00 | 110.00 | 165000.00 | 165000.00 | Variant Infratech Private Limited
79.00 | Commissioning of system with first charge of refrigerant, including testing, adjustment, balancing and ensuring proper performance of the equipment, complete as required. | 14.00 | Lot |  | 21000.00 | 294000.00 | 7000.00 | 98000.00 | 10900.00 | 152600.00 | 46800.00 | 655200.00 | 98000.00 | AIRON CORPORTION
80.00 | Supply, installation, testing & commissioning of Unit Controller with Remote for one way and two way cassette units. | 8.00 | Set |  | 5000.00 | 40000.00 | 4400.00 | 35200.00 | 2180.00 | 17440.00 | 4250.00 | 34000.00 | 17440.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
81.00 | Supply, installation, testing & commissioning of change over Timer Controller for working unit and stand by units. | 4.00 | Set |  | 15000.00 | 60000.00 | 6000.00 | 24000.00 | 33790.00 | 135160.00 | 6500.00 | 26000.00 | 24000.00 | AIRON CORPORTION
82.00 | Supply of following size XLPE insulated PVC sheathed Aluminium conductor armoured power cable of 1.1 KV grade confirming to IS 7098 (Part-I) with up to date ammendment etc. complete as required.
83.00 | 3.5C x 50 sq. mm. | 504.00 | Mtrs. |  | 800.00 | 403200.00 | 355.00 | 178920.00 | 468.70 | 236224.80 | 247.00 | 124488.00 | 124488.00 | Variant Infratech Private Limited
84.00 | 3.5C x 35 sq. mm. | 288.00 | Mtrs. |  | 700.00 | 201600.00 | 250.00 | 72000.00 | 348.80 | 100454.40 | 190.00 | 54720.00 | 54720.00 | Variant Infratech Private Limited
85.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade Upto 35 sq. mm cable size on wall surfaceas required. | 220.00 | Mtrs. |  | 250.00 | 55000.00 | 110.00 | 24200.00 | 163.50 | 35970.00 | 50.00 | 11000.00 | 11000.00 | Variant Infratech Private Limited
86.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade above 35 sqmm. and Upto 95sqmm. sq. mm cable size on wall surfaceas required. | 180.00 | Mtrs. |  | 260.00 | 46800.00 | 145.00 | 26100.00 | 256.15 | 46107.00 | 50.00 | 9000.00 | 9000.00 | Variant Infratech Private Limited
87.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
88.00 | Upto 35 sq. mm (clamped with 1mm thick saddle) | 150.00 | Mtrs. |  | 260.00 | 39000.00 | 15.00 | 2250.00 | 201.65 | 30247.50 | 50.00 | 7500.00 | 2250.00 | AIRON CORPORTION
89.00 | Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 200.00 | Mtrs. |  | 280.00 | 56000.00 | 20.00 | 4000.00 | 321.55 | 64310.00 | 50.00 | 10000.00 | 4000.00 | AIRON CORPORTION
90.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required.
91.00 | 3.5 x 50 sq. mm. | 18.00 | Each |  | 2500.00 | 45000.00 | 110.00 | 1980.00 | 5286.50 | 95157.00 | 1500.00 | 27000.00 | 1980.00 | AIRON CORPORTION
92.00 | 3.5 x 35 sq. mm. | 16.00 | Each |  | 1600.00 | 25600.00 | 110.00 | 1760.00 | 3542.50 | 56680.00 | 1500.00 | 24000.00 | 1760.00 | AIRON CORPORTION
93.00 | Providing and laying in position cement concrete of specified grade including the cost of all materials, labour, tools and plants required for proper execution of work. The item shall also include centering and shuttering wherever necessary, compacting the concrete to achieve required strength, curing for the prescribed period, and finishing the exposed surface smooth and even as per specifications and directions of the Engineer-in-Charge
94.00 | 1:2:4 (1 cement : 2coarse sand (Zone-III) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources) | 6.00 | Cum |  | 20000.00 | 120000.00 | 4418.00 | 26508.00 | 27250.00 | 163500.00 | 5500.00 | 33000.00 | 26508.00 | AIRON CORPORTION
95.00 | 1:2:4 (1 cement : 2coarse sand (Zone-III) derived from natural sources : 4 graded stone aggregate 40 mm nominal size derived from natural sources) | 8.00 | Cum |  | 20000.00 | 160000.00 | 4212.00 | 33696.00 | 27250.00 | 218000.00 | 6500.00 | 52000.00 | 33696.00 | AIRON CORPORTION
96.00 | 1:3:6 (1Cement : 3 Coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 20 mm nominal size derived from natural sources. | 6.00 | Cum |  | 18000.00 | 108000.00 | 4318.00 | 25908.00 | 32700.00 | 196200.00 | 6500.00 | 39000.00 | 25908.00 | AIRON CORPORTION
97.00 | 1:3:6 (1Cement : 3 Coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 40 mm nominal size derived from natural sources. | 8.00 | Cum |  | 18000.00 | 144000.00 | 3918.00 | 31344.00 | 32700.00 | 261600.00 | 6500.00 | 52000.00 | 31344.00 | AIRON CORPORTION
98.00 | Demolishing R.C.C work manually/ by mechnical means including stacking of steel bars and disposal of unserviceable material within 50 meaters lead as per direction of Engineer - in - charge. | 5.00 | Cum |  | 5000.00 | 25000.00 | 1504.00 | 7520.00 | 5450.00 | 27250.00 | 2600.00 | 13000.00 | 7520.00 | AIRON CORPORTION
99.00 | Demolishing cement concrete manually/ by mechanical means including disposal of material within 50 meters lead as per direction of Engineer-in-charge. Nominal contracte 1:3:6 or richer mix (i/c equivalent desingn mix) | 5.00 | Cum |  | 5000.00 | 25000.00 | 1454.00 | 7270.00 | 5450.00 | 27250.00 | 2000.00 | 10000.00 | 7270.00 | AIRON CORPORTION
100.00 | Demolishing brick work manually/ by mechnical means including stacking of serviceble material and disposal of unserviceble material within 50 metres lead as per direction of Engineer-in-charge. (In cement mortar) | 5.00 | Cum |  | 5000.00 | 25000.00 | 1204.00 | 6020.00 | 5450.00 | 27250.00 | 2000.00 | 10000.00 | 6020.00 | AIRON CORPORTION
101.00 | SH-II Ceiling Mounted Cassette AC
102.00 | Supply, Installation, testing and commissioning of 4 way ceiling mounted Inverter Cassette type Air Conditioning Unit (preferably 5 Star BEE rating or as per OEM availablity) consisting of ceiling mounted indoor unit and condenser (copper) unit with 4TR (or as per OEM) capacity having nominal cooling capacity of minimum 48000 BTU/Hr., minimum 1600 CFM suitable for operation on 3-phase, 415 volts, 50 Hz AC supply (or as per OEM) with scroll type compressor suitable for R-410A/ R-32/ non CFC gas, cordless remote controller, integrated drain pump, auto air swing louvers extremely quiet in operation etc., including mounting indoor unit from the ceiling with suitable brackets/ tie rod as per standard practice in the industry, installation of condensing units with suitable MS angle/ channel/ bracket/ supports on the terrace/ sunshade/ wall/ column as per site requirements, initial filling of the gas to full capacity etc. as required. Net Capacity: - Unit will Deliver Capacity @ 41 Deg.C Ambient Condition with inside Condition of 25 Deg C & 50% RH. | 5.00 | Each |  | 143000.00 | 715000.00 | 125095.00 | 625475.00 | 135575.68 | 677878.40 | 145000.00 | 725000.00 | 625475.00 | AIRON CORPORTION
103.00 | Providing & fixing of suitable size Copper Refrigerant piping suitable for R-410A/ R-32/ non CFC (supply and return) refrigerant with expanded polythene foam insulation tubing with flexible PVC covering pipe for cassette type air conditioners as required. Refrigerant Pipe (Copper pipe) Make: - Mandev, RR, Rajco. | 75.00 | Mtr. |  | 3200.00 | 240000.00 | 1060.00 | 79500.00 | 1199.00 | 89925.00 | 1500.00 | 112500.00 | 79500.00 | AIRON CORPORTION
104.00 | Providing and fixing of 25 mm size PVC drain pipe from the respective units with proper insulation, concealed in wall/clamping on surface, sealing the joints including making of opening and repairing of wall as per site condition. | 75.00 | Mtr. |  | 200.00 | 15000.00 | 155.00 | 11625.00 | 215.82 | 16186.50 | 200.00 | 15000.00 | 11625.00 | AIRON CORPORTION
105.00 | Supply & fixing of 5 core, 4 sq. mm size copper conductor flexible cable for the connections from mains to outdoor units of approved make complete as required at site. | 50.00 | Mtr. |  | 600.00 | 30000.00 | 330.00 | 16500.00 | 686.70 | 34335.00 | 680.00 | 34000.00 | 16500.00 | AIRON CORPORTION
106.00 | Supply & fixing of 3 core, 2.5 sq. mm size copper conductor flexible cable for the interconnections between indoor & outdoor units of approved make complete as required at site. | 75.00 | Mtr. |  | 300.00 | 22500.00 | 175.00 | 13125.00 | 299.75 | 22481.25 | 320.00 | 24000.00 | 13125.00 | AIRON CORPORTION
107.00 | SH-III Wall Mounted Split AC System
108.00 | Supply of 2.0 TR (or as per OEM) capacity having nominal cooling capacity of minimum 24000 BTU/Hr., minimum 800 CFM suitable for operation on single phase, 230 volts, 50 Hz AC supply (or as per OEM) High wall Split type Airconditioners not less than 5 star rating copper coil, inverter type fitted with extra powerful rotory/ reciprocating compressors, including remote, regfrigerant R-32/ non CFC suitable for wall mounting confirming to IS 1391/ Part – 21/92 Amdt. No. 1 (except power consumption norms) with 10 feet copper refrigeration pipes and suitable copper cable and having features like auto air swing(2 way swing), speed setting(3/3), operation control (electronic), auto restart, on timer, evaporator type (2 bend eva) and capable of performing:- (a) Cooling (b) Dehumidifying. (c) Air-circulating (d) Filtering (anti-bacteria). Net Capacity: - Unit will Deliver Capacity @ 41 Deg.C Ambient Condition with inside Condition of 25 Deg C & 50% RH. | 30.00 | Each |  | 50800.00 | 1524000.00 | 44100.00 | 1323000.00 | 44593.01 | 1337790.30 | 82000.00 | 2460000.00 | 1323000.00 | AIRON CORPORTION
109.00 | Supply of 1.5 TR (or as per OEM) capacity having nominal cooling capacity of minimum 18000 BTU/Hr., minimum 400 CFM suitable for operation on single phase, 230 volts, 50 Hz AC supply (or as per OEM) High wall Split type Airconditioners not less than 5 star rating copper coil, inverter type fitted with extra powerful rotory/ reciprocating compressors, including remote, regfrigerant R-32/ non CFC suitable for wall mounting confirming to IS 1391/ Part – 21/92 Amdt. No. 1 (except power consumption norms) with 10 feet copper refrigeration pipes and suitable copper cable and having features like auto air swing(2 way swing), speed setting(3/3), operation control (electronic), auto restart, on timer, evaporator type (2 bend eva) and capable of performing:- (a) Cooling (b) Dehumidifying. (c) Air-circulating (d) Filtering (anti-bacteria). Net Capacity: - Unit will Deliver Capacity @ 41 Deg.C Ambient Condition with inside Condition of 25 Deg C & 50% RH. | 35.00 | Each |  | 50800.00 | 1778000.00 | 41400.00 | 1449000.00 | 37377.76 | 1308221.60 | 65000.00 | 2275000.00 | 1308221.60 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
110.00 | Installation, Testing & commissioning of A/C units as mentioned in item no- 1&2 which includes mounting of indoor & outdoor unit including supply and fixing of MS stand at their respective location along with laying of refrigerant pipeline with insulation & flexible PVC covering pipe up to standard length supplied with the unit , connecting both the units , leak testing of entire system, connecting both indoor and outdoor units with three core 2.5 sq mm PVC insulated flexible copper cable supplied with the unit, top up of refrigerant (if required), minor civil repairing work as per site requirement complete as required. | 65.00 | Job |  | 3600.00 | 234000.00 | 2000.00 | 130000.00 | 1635.00 | 106275.00 | 10000.00 | 650000.00 | 106275.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
111.00 | Providing & fixing of suitable size Copper Refrigerant piping suitable for R-32 (supply and return) refrigerant with expanded polythene foam insulation tubing with flexible PVC covering pipe for split type air conditioners as required. (Measurement of 1 Running mtr. will include both supply & return Cu. Piping with insulation excluding standard length supplied by OEM with AC unit). Refrigerant Pipe (Copper pipe) Make: - Mandev, RR, Rajco. | 300.00 | Mtr. |  | 2400.00 | 720000.00 | 957.00 | 287100.00 | 1090.00 | 327000.00 | 1550.00 | 465000.00 | 287100.00 | AIRON CORPORTION
112.00 | Providing and fixing of 25 mm size PVC drain pipe from the respective units, concealed in wall/clamping on surface, sealing the joints including making of opening and repairing of wall as per site condition. | 200.00 | Mtr. |  | 200.00 | 40000.00 | 155.00 | 31000.00 | 218.00 | 43600.00 | 200.00 | 40000.00 | 31000.00 | AIRON CORPORTION
113.00 | Supply & fixing of 3 core, 2.5 sq mm size copper conductor flexible cable for the interconnections between indoor & outdoor units of approved make complete as required at site. (Measurement excluding standard length supplied by OEM with AC unit). | 200.00 | Mtr. |  | 325.00 | 65000.00 | 180.00 | 36000.00 | 299.75 | 59950.00 | 330.00 | 66000.00 | 36000.00 | AIRON CORPORTION
114.00 | Supply and fixing of single phase, 240V Smart controller/Timer with 4 hr/8 hr duration, 25A capacity, having OV and UV indication/protection suitable for AC power supply 240V, 50 Hz, etc. complete as required. | 6.00 | Each |  | 10000.00 | 60000.00 | 6000.00 | 36000.00 | 35425.00 | 212550.00 | 12000.00 | 72000.00 | 36000.00 | AIRON CORPORTION
115.00 | Dismantling the existing 1.5 TR/ 2.0 TR Split type AC of different capacities completely from different locations of the terminal building and shifting to AAI store i/c. loading / unloading etc. complete as required. | 35.00 | Job |  | 900.00 | 31500.00 | 300.00 | 10500.00 | 1090.00 | 38150.00 | 1250.00 | 43750.00 | 10500.00 | AIRON CORPORTION
116.00 | SH-IV Air Curtains and Hand Dryers
117.00 | Supply, installation, testing and commissioning of Centrifugal Type, Non Recirculating Air curtain having throw at the outlet of the Air Curtain is minimum 21m/s and MOC is of SS-304 grade, having noise level not more than 50db, suitable for door height of 8 feet, operation on single phase, 50Hz, 220V AC (or as per OEM) and provided with velocity control switch and door sensor, etc complete in all respect as required of following dimensions:
118.00 | Length = 900mm (min.), Width = 235mm (min.), Depth = 208mm (min.) | 4.00 | Nos. |  | 21800.00 | 87200.00 | 25215.00 | 100860.00 | 24134.78 | 96539.12 | 40000.00 | 160000.00 | 87200.00 | Aarham Engineers Pvt. Ltd.
119.00 | Length = 1200mm (min.), Width = 235mm (min.), Depth = 208mm (min.) | 8.00 | Nos. |  | 24400.00 | 195200.00 | 29451.00 | 235608.00 | 27731.78 | 221854.24 | 48000.00 | 384000.00 | 195200.00 | Aarham Engineers Pvt. Ltd.
120.00 | Length = 1500mm (min.), Width = 235mm (min.), Depth = 208mm (min.) | 12.00 | Nos. |  | 31400.00 | 376800.00 | 36768.00 | 441216.00 | 33944.78 | 407337.36 | 55000.00 | 660000.00 | 376800.00 | Aarham Engineers Pvt. Ltd.
121.00 | Length = 1800mm (min.), Width = 235mm (min.), Depth = 208mm (min.) | 4.00 | Nos. |  | 45600.00 | 182400.00 | 46219.00 | 184876.00 | 43837.62 | 175350.48 | 72000.00 | 288000.00 | 175350.48 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
122.00 | SITC of touch free Stainless steel-Brushed (304L) airblade (without heating element) having high efficiency particulate air (HEPA) filtered (able to captures more than 99.90% of particles as small as 0.1 microns), throw air speed more than 600 km/h, minimum operating airflow 22 Litre/ second, Motor speed more than 70000 RPM, capable to hand dry in 10 sec (max), noise less than 85 dB, IP24, Maximum upto 950W motor suitable for 160-253V, 50-60 Hz single phase supply and warranty for all parts for 05 years from OEM. (Make - Dyson, Model - Air blade 9kJ HU03 or Equivalent) | 8.00 | Nos. |  | 131000.00 | 1048000.00 | 122264.00 | 978112.00 | 124805.00 | 998440.00 | 95000.00 | 760000.00 | 760000.00 | Variant Infratech Private Limited
123.00 | SITC of touch free polycarbonate 'Nickle' airblade (without heating element) having high efficiency particulate air (HEPA) filtered (able to captures more than 99.90% of particles as small as 0.1 microns), throw air speed more than 600 km/h, minimum operating airflow 22 Litre/ second, Motor speed more than 70000 RPM, capable to hand dry in 12 sec (max), noise less than 85 dB, IP24, Maximum upto 950W motor suitable for 160-253V, 50-60 Hz single phase supply and warranty for all parts for 05 years from OEM. (Make - Dyson, Model -Air blade 9kJ HU02 or Equivalent) | 6.00 | Nos. |  | 81000.00 | 486000.00 | 75022.00 | 450132.00 | 76845.00 | 461070.00 | 110000.00 | 660000.00 | 450132.00 | AIRON CORPORTION
124.00 | Supply, installation, testing and commissioning of Hand Dryer with SS-304 grade MOC suitable for operation on operation on single phase, 50Hz, 220V AC supply having brushless DC motor with auto cutoff within 20 sec, noise level not more than 70 db, along with heater element having drying time less than 15 sec, IPX4 protection, inbuilt HEPA filter, etc. complete as required. (Make- Euronics, Model- TIERRA HAND DRYER or Equivalent) | 18.00 | Nos. |  | 26600.00 | 478800.00 | 20595.00 | 370710.00 | 22608.78 | 406958.04 | 125000.00 | 2250000.00 | 370710.00 | AIRON CORPORTION
125.00 | SH-V Miscellaneous work
126.00 | Supply of spares for CaryAire Make 4‑Way Cassette Type (Chilled Water) Fan Coil Unit, Model MCA‑1000, complete in all respects as per OEM specifications.
127.00 | Grille with filter as per sample | 25.00 | Each |  | 6200.00 | 155000.00 | 3700.00 | 92500.00 | 15043.09 | 376077.25 | 9000.00 | 225000.00 | 92500.00 | AIRON CORPORTION
128.00 | Complete cover with flap, swing motor, grill & filter as per sample | 10.00 | Each |  | 20200.00 | 202000.00 | 13300.00 | 133000.00 | 899.25 | 8992.50 | 7500.00 | 75000.00 | 8992.50 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
129.00 | Supply of spare parts for Toshiba Make VRF Indoor Unit, Model No. MMURP0244, complete in all respects as per OEM specifications.
130.00 | Complete Indoor Unit Assembly (complete housing and integrated coil section), Material code - 2514035 | 4.00 | Each |  | 61775.00 | 247100.00 | 4985.00 | 19940.00 | 43600.00 | 174400.00 | 35000.00 | 140000.00 | 19940.00 | AIRON CORPORTION
131.00 | Fan Blower-assembly (factory‑balanced blower wheel with motor coupling), Material code - 2024956 | 4.00 | Each |  | 8500.00 | 34000.00 | 3705.00 | 14820.00 | 10355.00 | 41420.00 | 22000.00 | 88000.00 | 14820.00 | AIRON CORPORTION
132.00 | All Sensors (temperature, humidity, and safety sensors, etc or as per OEM design), Material code - 2024959,2048774,2024644 | 4.00 | Set |  | 13000.00 | 52000.00 | 3288.00 | 13152.00 | 1635.00 | 6540.00 | 30000.00 | 120000.00 | 6540.00 | M/s. PRANAM HVAC ENGINEERING PVT. LTD.
133.00 | Pump assembly - Drain Pump (built‑in condensate pump with overflow protection switch), Material code - 2047705N | 4.00 | Each |  | 4500.00 | 18000.00 | 3705.00 | 14820.00 | 8175.00 | 32700.00 | 15000.00 | 60000.00 | 14820.00 | AIRON CORPORTION
134.00 | Pan assembly - Drain Tray (condensate collection tray with anti‑corrosion coating), Material code - 2027976 | 4.00 | Each |  | 10400.00 | 41600.00 | 4845.00 | 19380.00 | 9265.00 | 37060.00 | 20000.00 | 80000.00 | 19380.00 | AIRON CORPORTION
135.00 | Grille assembly as per sample | 4.00 | Each |  | 13700.00 | 54800.00 | 7717.00 | 30868.00 | 11445.00 | 45780.00 | 22000.00 | 88000.00 | 30868.00 | AIRON CORPORTION
136.00 | PCB Card (control board with microprocessor and communication interface), Material code - 2024961N | 4.00 | Each |  | 28000.00 | 112000.00 | 12000.00 | 48000.00 | 16350.00 | 65400.00 | 18000.00 | 72000.00 | 48000.00 | AIRON CORPORTION
137.00 | Master Unit Remote (wired/wireless remote controller for system operation), Material code - 2514137 | 4.00 | Each |  | 10000.00 | 40000.00 | 1080.00 | 4320.00 | 6540.01 | 26160.04 | 7500.00 | 30000.00 | 4320.00 | AIRON CORPORTION
| Total in Figures |  |  |  |  | 23241950.00 |  | 15602121.00 |  | 19440000.00 |  | 25903400.00
Lowest Amount Quoted BY: AIRON CORPORTION(15602121.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Air conditioning in new CCR room and ATC substation i/c air conditioning in Aerobridge tunnels and other ancillary work at Vadodara Airport Tender ID: 2026_AAI_262135_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | AIRON CORPORTION (BID ID -966973) | 15602121.00 | L1
| 2 | M/s. PRANAM HVAC ENGINEERING PVT. LTD. (BID ID -967434) | 19440000.00 | L2
| 3 | Aarham Engineers Pvt. Ltd. (BID ID -961283) | 23241950.00 | L3
| 4 | Variant Infratech Private Limited (BID ID -978783) | 25903400.00 | L4