## BoQ1
Government eProcurement System Created By: Semreichui Duidang Created Date/Time: 05-Feb-2026 04:30 PM Tender Title: Improvement or Renovation of Toilets in Terminal Building at Imphal International Airport, Imphal Tender ID: 2026_AAI_262798_1
Tender Inviting Authority: Sr. Manager (Engg-Elect), AAI, Imphal International Airport.
Name of Work: Improvement / Renovation of Toilets in Terminal Building at Imphal International Airport, Imphal.
Contract No: 2026_AAI_262798_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | N.Motilal Singh (GSTN-14AVWPS6147B1Z9) BID ID -970226 |  | ZORAH ENTERPRISE (GSTN-NA) BID ID -965932 |  | M/S Thokchom Okendro Singh (GSTN-NA) BID ID -969535
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying, installation, testing & commissioning of 15W LED recessed/surface Down Lighter round COB type of following body material and construction as per IS : 10322 with driver as per the requirement with driver efficiency > 85%, Operating voltage AC 140-270 Volt, frequency 50/60 Hz, Operating temp range -15 deg to 40 deg centigrade, internal surge protection of 2.5 KV with short & open circuit protection, THD < 10%, P.F. ≥ 0.95, IP 20, CRI > 80, UGR (Unified Glare Rating) < 19, Flicker free (flicker should be below 5%), life time (LED, Driver & Electrical Circuitry), of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends, CCT 3000° K / 4000° K / 5700° K / 6000° K / 6500° K (As per ANSI Bin), SDCM (Standard Deviation Color Matching) < 3, Maximum power consumption should not more than the specified rating and Fixture shall be confirming to relevant BIS standards and trade mark certificate (T.C.). Manufactures Word Mark/ Name Engraved/ Embossing/ Screen printing on housing Complete in all respect with Minimum 5-year OEM warranty. System lumen efficacy ≥ 105 and < 120 lm / Watt output. LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size and CCT shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90° C). Powder coated die cast /Extruded aluminum Body including trim with Aluminum Reflector. | 54.00 | Each |  | 1680.00 | 90720.00 | 1680.00 | 90720.00 | 1102.90 | 59556.60 | 59556.60 | M/S Thokchom Okendro Singh
2.00 | Supplying, Installation, Testing & Commissioning of Panel light 2 x 2 ft. 36 W, of following body material and construction as per IS : 10322 with driver as per the requirement with Driver efficiency > 85%, Operating voltage AC 140-270 Volt, freq 50/60 Hz, Operating temp range -15 deg to 40 deg centigrade, internal surge protection of 2.5 kV with short & Open circuit protection, THD < 10%, P.F. ≥ 0.95, IP20, CRI > 80, UGR (Unified Glare Rating) < 19, Flicker free, (flicker should be below 5%), life time (LED, Driver & Electrical Circuitry), of minimum 50000 Burning Hours with, 70% of initial Lumen maintained till life ends, CCT 3000° K / 4000° K / 5700° K / 6000° K / 6500° K (As per ANSI Bin), SDCM (Standard Deviation Color Matching) < 3, Maximum power consumption should not more than the specified rating and Fixture shall be relevant BIS standard and trade mark certificate (T.C.). Manufactures Word Mark / Name Engraved / Embossing / Screen printing on housing, complete in all respect i/c connections with 1.5 sq. mm FRLS, PVC insulated copper conductor single core cable and earthing etc. as required with Minimum 5-year OEM warranty. System lumen efficacy ≥ 120 < 135 lm / Watt output. LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size and CCT shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminium housing such that LED junction temperature shall not rise above 90°C). Powder coated die cast / Extruded aluminium Body (Thickness > 1.20 mm). | 87.00 | Each |  | 2000.00 | 174000.00 | 2470.00 | 214890.00 | 1353.00 | 117711.00 | 117711.00 | M/S Thokchom Okendro Singh
3.00 | Providing and fixing teak wood frame of H-section or of appropriate design around the bathroom/toilet mirror at airport, including groove for Housing LED strip light, polishing, finishing, and complete in all respects as directed by Engineer-in-Charge. • Material: First class, seasoned teak wood, free from knots and warps. • Section: H-shaped, thickness 25 mm (± 2 mm) and width 50 mm (± 2 mm). • Groove: Continuous machine-cut groove of 12 mm (W) × 12 mm (D) (or as per LED strip size) on inner side of frame to house LED strip light, ensuring proper heat dissipation. • LED String/Strip Light: To be fixed behind and within the groove, with concealed wiring arrangement. • Finish: Smooth machine-planed surface, melamine/polish with moisture-resistant coating suitable for humid bathroom conditions. • Fixing: Brass screws and concealed fasteners, with all mitred joints properly joined and polished. • Measurement: Length to be measured in meters along the perimeter of the mirror (outer edge of frame). | 120.00 | Mtr |  | 1100.00 | 132000.00 | 995.00 | 119400.00 | 733.90 | 88068.00 | 88068.00 | M/S Thokchom Okendro Singh
4.00 | Supplying, fixing, testing, and commissioning of flexible LED strip light of approved make, color temperature 4000 K (neutral white), mounted inside groove of teak wood frame around bathroom mirror, including driver/transformer, wiring, connections, and complete in all respects as per specifications and directions of Engineer-in-Charge. • LED Type: Flexible strip, high brightness SMD LED, min. 12 W per meter, IP65 moisture resistant. • Driver: Branded constant-voltage driver, 230V input, 12/24V DC output, concealed in accessible junction box. • Fixing: With suitable clips/adhesive inside groove, concealed wiring with FRLS copper wire, proper heat dissipation. • Testing: To be tested and commissioned after installation. • Measurement: Length of LED strip installed in meters (m). | 120.00 | Mtr |  | 6280.00 | 753600.00 | 4970.00 | 596400.00 | 2788.00 | 334560.00 | 334560.00 | M/S Thokchom Okendro Singh
5.00 | Supply and drawing for circuit/ submain along with earth wire with the following sizes of FRLS PVC insulated copper conductor cable, single core cable in the existing surface /recessed steel/PVC conduit as required.
5.01 | 2 x 1.5 Sq.mm + 1 x 1.5 Sq.mm earth wire. | 300.00 | Mtr |  | 70.00 | 21000.00 | 87.00 | 26100.00 | 58.22 | 17466.00 | 17466.00 | M/S Thokchom Okendro Singh
5.02 | 2 x 2.5 Sq.mm + 1 x 2.5 Sq.mm earth wire. | 250.00 | Mtr |  | 120.00 | 30000.00 | 147.00 | 36750.00 | 86.92 | 21730.00 | 21730.00 | M/S Thokchom Okendro Singh
6.00 | Supply and drawing for light/ power plug of FRLS PVC insulated, copper conductor cable, single core cable in surface /recessed medium class PVC conduit along with 1 No. 4 sq. mm FRLS PVC insulated copper conductor single core cable for loop earthing as required.
6.01 | 2 x 4 sq.mm. | 200.00 | Mtr |  | 180.00 | 36000.00 | 195.00 | 39000.00 | 123.00 | 24600.00 | 24600.00 | M/S Thokchom Okendro Singh
7.00 | Supplying and fixing of medium class 25 MM PVC Conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. | 600.00 | Mtr |  | 80.00 | 48000.00 | 117.00 | 70200.00 | 69.70 | 41820.00 | 41820.00 | M/S Thokchom Okendro Singh
8.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
8.01 | 5/6 A Switch | 161.00 | Each |  | 70.00 | 11270.00 | 68.00 | 10948.00 | 43.46 | 6997.06 | 6997.06 | M/S Thokchom Okendro Singh
8.02 | 15/16 A switch. | 20.00 | Each |  | 190.00 | 3800.00 | 148.00 | 2960.00 | 102.50 | 2050.00 | 2050.00 | M/S Thokchom Okendro Singh
8.03 | 6 pin 15/16 A socket outlet. | 20.00 | Each |  | 280.00 | 5600.00 | 195.00 | 3900.00 | 151.70 | 3034.00 | 3034.00 | M/S Thokchom Okendro Singh
9.00 | Supplying and fixing following size/ modules, GI box along with modular base & cover plate for modular switches/sockets in recess etc. as required.
9.01 | 3 Module. | 28.00 | Each |  | 350.00 | 9800.00 | 375.00 | 10500.00 | 222.22 | 6222.16 | 6222.16 | M/S Thokchom Okendro Singh
9.02 | 4 Module. | 17.00 | Each |  | 350.00 | 5950.00 | 415.00 | 7055.00 | 246.82 | 4195.94 | 4195.94 | M/S Thokchom Okendro Singh
9.03 | 6 Module. | 13.00 | Each |  | 480.00 | 6240.00 | 557.00 | 7241.00 | 313.24 | 4072.12 | 4072.12 | M/S Thokchom Okendro Singh
10.00 | Supplying and fixing of 6 to 32 A rating, 240/415V, 10kA, C curve MCB suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 14.00 | Each |  | 340.00 | 4760.00 | 217.00 | 3038.00 | 142.68 | 1997.52 | 1997.52 | M/S Thokchom Okendro Singh
11.00 | Supplying and fixing of Double pole, 240V, Isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required.
11.01 | 40 A. | 8.00 | Each |  | 500.00 | 4000.00 | 494.00 | 3952.00 | 280.44 | 2243.52 | 2243.52 | M/S Thokchom Okendro Singh
12.00 | Supply, installation, testing and commissioning of Single inlet CABINET TYPE INLINE DUCT MOUNTED EXHAUST AND SUPPLY OR RETURN FRESH AIR FANS shall be of the centrifugal direct drive type, cabinet inline fan complete with SISW Forward curved centrifugal fan, Standard efficiency motor, fan and motor base frame, drain point with plug in the fan section suitable for installation in any position in vertical or horizontal ducts. The casing shall be double skin internally acoustic lined and constructed of galvanized steel. The housing interior shall be lined with 0.5 inch (13mm) acoustical insulation. The outlet duct collar shall included and shall be adaptable for horizontal or vertical discharge. The fan should fit into the existing duct or opening, providing efficient ventilation.
12.01 | Min. 300 CFM @12-25mm wg static pressure, suitable for operation in 230V ± 10%, 1 Phase 50 Hz AC Supply. | 12.00 | No |  | 37000.00 | 444000.00 | 30500.00 | 366000.00 | 29000.00 | 348000.00 | 348000.00 | M/S Thokchom Okendro Singh
12.02 | Min. 400CFM @15-30mm wg static pressure suitable for operation in 230V ± 10%, 1 Phase 50 Hz AC Supply. | 8.00 | No |  | 39000.00 | 312000.00 | 35900.00 | 287200.00 | 29000.00 | 232000.00 | 232000.00 | M/S Thokchom Okendro Singh
12.03 | Min. 450 CFM @18-30mm wg static pressure suitable for operation in 230V ± 10%, 1 Phase 50 Hz AC Supply. | 1.00 | No |  | 38000.00 | 38000.00 | 37950.00 | 37950.00 | 29000.00 | 29000.00 | 29000.00 | M/S Thokchom Okendro Singh
13.00 | Supply of aluminium flexible ducts as per specifications and approved drawings complete with all fittings such as tees, bends and accessories etc. as per site required, conforming to DIN 18017-3 standards. The ducts shall be five-layered, grooved, and manufactured from high-quality aluminium, ensuring flexibility, durability, and non-combustibility (DIN 4102 Class A1) suitable for HVAC duct connections. The ducts must withstand a maximum operating pressure of 2,500 Pa and an ambient temperature of up to 100°C. | 80.00 | Each |  | 340.00 | 27200.00 | 294.00 | 23520.00 | 183.68 | 14694.40 | 14694.40 | M/S Thokchom Okendro Singh
14.00 | Design, Supply, fabrication, handling and erection of Galvanized sheet metal ducting as per specifications and approved drawings complete with all fittings such as tees, bends and accessories etc. as required including providing suitable suspension and supporting arrangements etc., as required as per IS-655. 24 Gauge. | 200.00 | Sqm |  | 550.00 | 110000.00 | 545.00 | 109000.00 | 950.00 | 190000.00 | 109000.00 | ZORAH ENTERPRISE
15.00 | Supply and fixing the following type machine made, extruded powder coated aluminium grills as per specifications and as per approved drawings and in accordance with site conditions etc., as reqd. Grille without VCD (Size 600 mm x 150 mm). | 7.32 | Sqm |  | 4000.00 | 29280.00 | 3998.00 | 29265.36 | 2345.20 | 17166.86 | 17166.86 | M/S Thokchom Okendro Singh
16.00 | Supply Fabrication and installation of MS Angle Frame for Inline Fan Support/Duct | 200.00 | Kg |  | 100.00 | 20000.00 | 130.00 | 26000.00 | 94.30 | 18860.00 | 18860.00 | M/S Thokchom Okendro Singh
17.00 | Supply, installation, testing and commissioning of Drinking water Free Standing Fountain Type, 106 LPH rated capacity & 60 LPH base rate, pre cooler refrigerated water Hot and Cold of 10ºC to 21ºC ambient temp. made of heavy duty galvanised steel with SS finish with built in 100 micron strainer, green filter, Ultra Blu V, drain and removable drip tray suitable to operate on 220-240 V, 50/60 Hz power supply, 4.7 A full load amps, 820 W complete including inlet , outlet and drain pipe connections etc. complete as required. Similar to OASIS Model No. PLF14FAHY (1100(H) x 432(W) x 356(D) | 3.00 | Each |  | 120000.00 | 360000.00 | 99500.00 | 298500.00 | 230000.00 | 690000.00 | 298500.00 | ZORAH ENTERPRISE
| Total in Figures |  |  |  |  | 2677220.00 |  | 2420489.36 |  | 2276045.18
Lowest Amount Quoted BY: M/S Thokchom Okendro Singh(2276045.18)

## BOQ Summary
BOQ Summary Details Tender Title: Improvement or Renovation of Toilets in Terminal Building at Imphal International Airport, Imphal Tender ID: 2026_AAI_262798_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | M/S Thokchom Okendro Singh (BID ID -969535) | 2276045.18 | L1
| 2 | ZORAH ENTERPRISE (BID ID -965932) | 2420489.36 | L2
| 3 | N.Motilal Singh (BID ID -970226) | 2677220.00 | L3