## BoQ1
Government eProcurement System Created By: Rahul S Mankar Created Date/Time: 06-Mar-2026 04:36 PM Tender Title: Provision of Clean Agent Based Automatic Fire Suppression System for LT Panels at Goa Airport Tender ID: 2026_AAI_263641_1
Tender Inviting Authority: AGM (E-E), Airports Authority of India, Goa International Airport, Goa.
Name of Work : Provision of Clean Agent Based Automatic Fire Suppression System for LT Panels at Goa Airport.
Tender ID - 2026_AAI_263641_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | PYROGUARD ENGINEERS PRIVATE LIMITED (GSTN-07AACCP9466E1Z7) BID ID -979293 |  | CENTRE TAP ENGINEERING (GSTN-24AGPPP8172K1ZP) BID ID -979986 |  | Fire Engineering Technology (GSTN-NA) BID ID -976161 |  | Kalpataru Industries (GSTN-NA) BID ID -979735
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply of UL Listed / FM approved Clean Agent (FK-5-1-12/NOVEC-1230/NAF S-1230) based automatic linear pneumatic tube detection gas suppression system for LT electrical panels of MLCP & STP, design in accordance to NBC 2016 / NFPA 2001 system, comprising following including all components, accessories, connections, fittings and supports etc. complete as per technical specifications as required.
1.10 | 2.0 Kg capacity PESO approved Aluminium seamless alloy cylinder conforming to IS 15660-2017, filled with 2.0 Kg UL Listed / FM approved Clean Agent (FK-5-1-12/NOVEC-1230/NAF S-1230), complete with TPED/CE/PESO/UL/FM approved Direct Low-Pressure (DLP) valve assembly with pressure gauge, ball valve, push-in / push-fit connector for heat detection tube, suitable rupture pressure rated safety burst disc, heavy-duty Stainless Steel / GI mounting brackets including all components, accessories, connections, fittings and supports etc. complete as per technical specifications as required. | 13.00 | Each | 0.00 | 20580.00 | 267540.00 | 20000.00 | 260000.00 | 18000.00 | 234000.00 | 21550.00 | 280150.00 | 234000.00 | Fire Engineering Technology
1.20 | UL Listed Linear Pneumatic Heat Detection Tube (ID: 4- 6 mm & OD: 6-8 mm as per system design requirement) for automatic linear pneumatic tube detection gas suppression system, made of special modified Polyamide (PA), with Red colour, having burst temperature range of 1000C to 1330C, pressurised with dry Nitrogen at 15-20 Bars pressure, end plugs, tee-connectors etc. complete as per technical specifications as required. | 335.00 | Metre | 0.00 | 720.00 | 241200.00 | 1000.00 | 335000.00 | 400.00 | 134000.00 | 650.00 | 217750.00 | 134000.00 | Fire Engineering Technology
1.30 | UL Listed / FM Approved / CE certified / LPCB approved Low Pressure Switch for monitoring pressure loss in fire suppression system complete with electrical contacts (NO/NC), wiring up to fire suppression system monitoring panel, connections, fittings and supports etc. complete as per technical specifications as required. | 13.00 | Each | 0.00 | 2830.00 | 36790.00 | 2000.00 | 26000.00 | 1200.00 | 15600.00 | 2450.00 | 31850.00 | 15600.00 | Fire Engineering Technology
1.40 | End of Line Adaptor with Pressure Gauge suitable for Linear Pneumatic Heat Detection Tube (ID: 4- 6 mm & OD: 6-8 mm as per system design requirement) made of Brass with elastomeric sealings, to be installed at the end of the tube for pressurizing / re-pressurizing, connections, fittings and supports etc. complete as per technical specifications as required. | 13.00 | Each | 0.00 | 3220.00 | 41860.00 | 2000.00 | 26000.00 | 1500.00 | 19500.00 | 1650.00 | 21450.00 | 19500.00 | Fire Engineering Technology
1.50 | Fire Suppression System Monitoring Panel / Master Control Unit with LCD/LED display, hooter cum flasher, 6/12/24 VDC battery backup with in-built charging, minimum 02 Nos. NO/NC potential-free relay contacts, LED indications for Gas Discharge, Battery, System status and AC Power ON etc., suitable for operation on 230 VAC +/- 10%, 50 Hz power supply, extension of power supply from nearest power point along with provision of 5A switch & socket of approved make, related wiring/cabling, connections / interconnections, conduiting etc. (Up to 5 Metres), with provision for integration with FDAS / SCADA / BMS including all components, accessories, connections, fittings and supports etc. complete as per technical specifications as required. | 9.00 | Each | 0.00 | 12920.00 | 116280.00 | 5000.00 | 45000.00 | 5000.00 | 45000.00 | 4250.00 | 38250.00 | 38250.00 | Kalpataru Industries
2.00 | Installation, Testing and Commissioning of UL Listed / FM approved Clean Agent (FK-5-1-12/NOVEC-1230/NAF S-1230) based automatic linear pneumatic tube detection gas suppression system for LT electrical panels of MLCP & STP in accordance to LPS 1666, comprising all components as above, accessories, connections, fittings and supports etc. complete as per technical specifications as required. | 13.00 | Job | 0.00 | 5540.00 | 72020.00 | 5000.00 | 65000.00 | 7500.00 | 97500.00 | 5200.00 | 67600.00 | 65000.00 | CENTRE TAP ENGINEERING
| Total in Figures |  |  |  |  | 775690.00 |  | 757000.00 |  | 545600.00 |  | 657050.00
Lowest Amount Quoted BY: Fire Engineering Technology(545600.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Clean Agent Based Automatic Fire Suppression System for LT Panels at Goa Airport Tender ID: 2026_AAI_263641_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Fire Engineering Technology (BID ID -976161) | 545600.00 | L1
| 2 | Kalpataru Industries (BID ID -979735) | 657050.00 | L2
| 3 | CENTRE TAP ENGINEERING (BID ID -979986) | 757000.00 | L3
| 4 | PYROGUARD ENGINEERS PRIVATE LIMITED (BID ID -979293) | 775690.00 | L4