## BoQ1
Government eProcurement System Created By: VIVEK SHRIVASTAVA Created Date/Time: 13-Mar-2026 06:08 PM Tender Title: Replacement of Indoor LED Lights of NITB at R.B. Airport, Bhopal. SH Internal Electrical Works. Tender ID: 2026_AAI_265242_1
Tender Inviting Authority: AGM(E-E), AAI, R.B. Airport, Bhopal
Name of Work: Replacement of Indoor LED Lights of NITB at R.B. Airport, Bhopal. SH: Internal Electrical Works.
Contract No: AAI/BPL/ENGG(E)/NIT-09/2025-26
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | M R ELECTRICALS (GSTN-27AARPV8927A1Z5) BID ID -984147 |  | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -984153 |  | surbhi association (GSTN-23AGKPD2522N1ZK) BID ID -984253 |  | Taral Electricals (GSTN-24ACMPR0280M1Z9) BID ID -984371 |  | Variant Infratech Private Limited (GSTN-NA) BID ID -984241 |  | O. P. CONSTRUCTIONS (GSTN-NA) BID ID -978664 |  | MANKHA ELECTROTECH PRIVATE LIMITED (GSTN-NA) BID ID -983795 |  | SYNERGY LIGHTING SOLUTIONS (GSTN-NA) BID ID -984108 |  | Shiva Enterprises (GSTN-NA) BID ID -984350 |  | Edge Telecom Pvt Ltd (GSTN-NA) BID ID -983334
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply & Fixing of 10W-12W COB LED Downlight luminaire shall provide range of 900 to 1200 lumens with a approximate cut-out diameter of 110mm and a height of 72mm, suitable for recess mounting. It will feature a white powder-coated extruded aluminium housing with an inbuilt heat sink for enhanced thermal management, ensuring long LED life. The optical compartment will include a high-efficiency reflector and a PC diffuser to produce a precise light beam while minimizing glare. The luminaire will be equipped with LM 80-08 compliant LEDs from reputed manufacturers like Nichia, Cree, Bridgelux, Lumileds, Osram, Seoul, or Citizen, with a minimum L70 life of 50,000 hours at maximum current, supported by a complete LM 80 test report for 10,000 hours. The color temperature will be 3000K, with a minimum Color Rendering Index (CRI) of 80, and the beam angles will be 60°. The driver will have an efficiency greater than 85%, 3 kV internal surge protection, a power factor greater than 0.95, and total harmonic distortion (THD) ≤20%, LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters with 5 years warranty. Relevent Product - Make: Wipro, Code-LD56-141-060-30-XX & Equivalent make as per AAI make list. | 50.00 | Each |  | 2900.00 | 145000.00 | 3200.00 | 160000.00 | 1750.00 | 87500.00 | 1865.00 | 93250.00 | 800.00 | 40000.00 | 4090.00 | 204500.00 | 2661.00 | 133050.00 | 1800.00 | 90000.00 | 1050.00 | 52500.00 | 1210.80 | 60540.00 | 40000.00 | Variant Infratech Private Limited
2.00 | Supply & Fixing of 18W-20W COB LED Downlight luminaire shall provide range of 1800 to 2000 lumens with a approximat cut-out diameter of 110mm and a height of 72mm, suitable for recess mounting. It will feature a white powder-coated extruded aluminium housing with an inbuilt heat sink for enhanced thermal management, ensuring long LED life. The optical compartment will include a high-efficiency reflector and a PC diffuser to produce a precise light beam while minimizing glare. The luminaire will be equipped with LM 80-08 compliant LEDs from reputed manufacturers like Nichia, Cree, Bridgelux, Lumileds, Osram, Seoul, or Citizen, with a minimum L70 life of 50,000 hours at maximum current, supported by a complete LM 80 test report for 10,000 hours. The color temperature will be 3000K, with a minimum Color Rendering Index (CRI) of 80, and the beam angles will be 60°. The driver will have an efficiency greater than 85%, 3 kV internal surge protection, a power factor greater than 0.95, and total harmonic distortion (THD) ≤10%, LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters with 5 years warranty. Relevent Product, Make: Wipro, Code - LD56-251-060-30-XX & Equivalent make as per AAI make list. | 300.00 | Each |  | 3800.00 | 1140000.00 | 3100.00 | 930000.00 | 2000.00 | 600000.00 | 1953.00 | 585900.00 | 1250.00 | 375000.00 | 3990.00 | 1197000.00 | 2634.00 | 790200.00 | 2000.00 | 600000.00 | 1250.00 | 375000.00 | 942.25 | 282675.00 | 282675.00 | Edge Telecom Pvt Ltd
3.00 | Supply and Fixing of LED Highbay light (Round) with Minimum system efficacy of 180 lm/ watt Body should be Pressure die cast aluminium wide beam angle oprating tempreture 0-45 Degree with 100000 burning hour total lumen should not less then 30000 lm with 6 kv surge and PF >0.95 Luminaire Insulation & Serviceability Class 1/ Class B THD <10 % Current Ripple <10% oprating voltage 140 - 270 V EMI / EMC complaince driver High / low cut off complaince with over voltage protection of 440 V, CCT of 5700 K with BIS and NABL cirtified lab Lm-79 reprot with 5 year system generated waranty ciritificate Make - Philips / LT / Wipro / Havells & equivalent make as per AAI Make list. | 50.00 | Each |  | 29000.00 | 1450000.00 | 3100.00 | 155000.00 | 14500.00 | 725000.00 | 11225.00 | 561250.00 | 11300.00 | 565000.00 | 4000.00 | 200000.00 | 10635.00 | 531750.00 | 7500.00 | 375000.00 | 5400.00 | 270000.00 | 8576.10 | 428805.00 | 155000.00 | Manish Electricals
4.00 | Supply & Fixing of 28 to 30 watt Batten with minimum System Efficacy of 145 lm/watt Aluminimum Extruded housing IP20 power Factor >0.9 THD <10% Driver Efficacy >85% Input Voltage Range 140-270V Surge 3.5 kV Desing tempreture 45 Degrees SDCM <5 with BIS, minimum CCT 5700K and LM 79 and 80 reprot of NABL cirtified lab with 5 year system generated waranty ciritificate Make - Philips / LT / Wipro & equivalent make as per AAI Make list. | 200.00 | Each |  | 1400.00 | 280000.00 | 1100.00 | 220000.00 | 1400.00 | 280000.00 | 1117.00 | 223400.00 | 1800.00 | 360000.00 | 1650.00 | 330000.00 | 1770.00 | 354000.00 | 1400.00 | 280000.00 | 830.00 | 166000.00 | 1195.60 | 239120.00 | 166000.00 | Shiva Enterprises
5.00 | Supply & Fixing of Approximate 10mm X 12.5mm of 5 meters length 3000K Flexible strip led light. The luminaire’s shall be made of Polymide double sided PCB. The luminaire shall have Solid state high brightness SMD led chips, IP20,Protection against insects and small items entry into luminaire, 1no of Driver is supplied with 5 mtr roll,The luminaire shall have system wattage of 10 Watt/meter and shall deliver minimum 700 lumens. Fixture shall operating temperature range of 0°C to 45°C. The fixture shall have an integral driver with input voltage for 100-300 VAC, 50Hz, PF≥0.90, THD≤20%, The driver will have an efficiency greater than 85%, The luminaire shall have declared life of 35,000 burning hours. LM 79 and LM80 reports need to be submitted from a NABL/UL accredited lab to verify above parameters, The product will comply with Indian standards IS 10322 Part 5/Section 7:2012, Make: Wipro, Product Code - LS06-10-12-30-50G1 & & equivalent make as per AAI Make list. | 120.00 | Each |  | 1900.00 | 228000.00 | 1500.00 | 180000.00 | 1950.00 | 234000.00 | 1649.00 | 197880.00 | 3000.00 | 360000.00 | 2500.00 | 300000.00 | 3300.00 | 396000.00 | 2000.00 | 240000.00 | 1950.00 | 234000.00 | 1518.10 | 182172.00 | 180000.00 | Manish Electricals
6.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 300.00 | Point |  | 1000.00 | 300000.00 | 1350.00 | 405000.00 | 1350.00 | 405000.00 | 1798.00 | 539400.00 | 1320.00 | 396000.00 | 1246.00 | 373800.00 | 1320.00 | 396000.00 | 800.00 | 240000.00 | 2500.00 | 750000.00 | 2007.20 | 602160.00 | 240000.00 | SYNERGY LIGHTING SOLUTIONS
7.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required.
7.01 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 200.00 | Meter |  | 350.00 | 70000.00 | 225.00 | 45000.00 | 350.00 | 70000.00 | 481.00 | 96200.00 | 660.00 | 132000.00 | 414.00 | 82800.00 | 357.00 | 71400.00 | 300.00 | 60000.00 | 230.00 | 46000.00 | 432.90 | 86580.00 | 45000.00 | Manish Electricals
7.02 | 4 X 2.5 sq. mm + 2 X 2.5 sq. mm earth wire | 650.00 | Meter |  | 500.00 | 325000.00 | 350.00 | 227500.00 | 510.00 | 331500.00 | 592.00 | 384800.00 | 600.00 | 390000.00 | 621.00 | 403650.00 | 492.00 | 319800.00 | 600.00 | 390000.00 | 440.00 | 286000.00 | 491.40 | 319410.00 | 227500.00 | Manish Electricals
7.03 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 50.00 | Meter |  | 400.00 | 20000.00 | 290.00 | 14500.00 | 400.00 | 20000.00 | 517.00 | 25850.00 | 660.00 | 33000.00 | 476.00 | 23800.00 | 438.00 | 21900.00 | 400.00 | 20000.00 | 285.00 | 14250.00 | 468.10 | 23405.00 | 14250.00 | Shiva Enterprises
7.04 | 4 X 4 sq. mm + 2 X 4 sq. mm earth wire | 200.00 | Meter |  | 600.00 | 120000.00 | 450.00 | 90000.00 | 650.00 | 130000.00 | 747.00 | 149400.00 | 660.00 | 132000.00 | 744.00 | 148800.00 | 690.00 | 138000.00 | 800.00 | 160000.00 | 550.00 | 110000.00 | 620.10 | 124020.00 | 90000.00 | Manish Electricals
8.00 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
8.01 | 3 x 2.5 sq. mm | 80.00 | Meter |  | 220.00 | 17600.00 | 225.00 | 18000.00 | 200.00 | 16000.00 | 164.00 | 13120.00 | 250.00 | 20000.00 | 148.00 | 11840.00 | 177.00 | 14160.00 | 120.00 | 9600.00 | 170.00 | 13600.00 | 247.50 | 19800.00 | 9600.00 | SYNERGY LIGHTING SOLUTIONS
8.02 | 6 x 2.5 sq. mm | 200.00 | Meter |  | 440.00 | 88000.00 | 375.00 | 75000.00 | 350.00 | 70000.00 | 318.00 | 63600.00 | 650.00 | 130000.00 | 283.00 | 56600.00 | 330.00 | 66000.00 | 240.00 | 48000.00 | 350.00 | 70000.00 | 404.30 | 80860.00 | 48000.00 | SYNERGY LIGHTING SOLUTIONS
8.03 | 3 x 4 sq. mm | 20.00 | Meter |  | 333.00 | 6660.00 | 270.00 | 5400.00 | 250.00 | 5000.00 | 239.00 | 4780.00 | 360.00 | 7200.00 | 222.00 | 4440.00 | 267.00 | 5340.00 | 200.00 | 4000.00 | 250.00 | 5000.00 | 327.20 | 6544.00 | 4000.00 | SYNERGY LIGHTING SOLUTIONS
8.04 | 6 x 4 sq. mm | 50.00 | Meter |  | 666.00 | 33300.00 | 480.00 | 24000.00 | 450.00 | 22500.00 | 465.00 | 23250.00 | 787.00 | 39350.00 | 424.00 | 21200.00 | 510.00 | 25500.00 | 400.00 | 20000.00 | 420.00 | 21000.00 | 532.35 | 26617.50 | 20000.00 | SYNERGY LIGHTING SOLUTIONS
9.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 8 way (8 + 24), Double door | 2.00 | Each |  | 11500.00 | 23000.00 | 9800.00 | 19600.00 | 10500.00 | 21000.00 | 6326.00 | 12652.00 | 8976.00 | 17952.00 | 6337.00 | 12674.00 | 11400.00 | 22800.00 | 1500.00 | 3000.00 | 13000.00 | 26000.00 | 7250.30 | 14500.60 | 3000.00 | SYNERGY LIGHTING SOLUTIONS
10.00 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Single pole | 48.00 | Each |  | 175.00 | 8400.00 | 210.00 | 10080.00 | 200.00 | 9600.00 | 140.00 | 6720.00 | 198.00 | 9504.00 | 285.00 | 13680.00 | 222.00 | 10656.00 | 120.00 | 5760.00 | 220.00 | 10560.00 | 232.20 | 11145.60 | 5760.00 | SYNERGY LIGHTING SOLUTIONS
11.00 | Supplying and fixing following rating, four pole, 415 volts, isolator in the existing MCB DB complete with connections, testing and commissioning etc. as required. 40 A | 2.00 | Each |  | 1000.00 | 2000.00 | 1600.00 | 3200.00 | 1651.00 | 3302.00 | 1204.00 | 2408.00 | 4620.00 | 9240.00 | 1049.00 | 2098.00 | 1230.00 | 2460.00 | 500.00 | 1000.00 | 890.00 | 1780.00 | 1905.65 | 3811.30 | 1000.00 | SYNERGY LIGHTING SOLUTIONS
12.00 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. 40 A | 2.00 | Each |  | 3500.00 | 7000.00 | 4500.00 | 9000.00 | 5000.00 | 10000.00 | 1742.00 | 3484.00 | 4224.00 | 8448.00 | 3597.00 | 7194.00 | 3300.00 | 6600.00 | 2500.00 | 5000.00 | 2850.00 | 5700.00 | 2737.80 | 5475.60 | 3484.00 | Taral Electricals
13.00 | Supplying and fixing Cable End Boxes (IP 43) suitable for following triple pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, complete with testing and commissioning etc. For 8 way, Double door TPN MCBDB | 2.00 | Each |  | 11000.00 | 22000.00 | 7500.00 | 15000.00 | 3500.00 | 7000.00 | 1169.00 | 2338.00 | 22440.00 | 44880.00 | 1448.00 | 2896.00 | 1707.00 | 3414.00 | 300.00 | 600.00 | 6500.00 | 13000.00 | 2557.90 | 5115.80 | 600.00 | SYNERGY LIGHTING SOLUTIONS
14.00 | Supplying and fixing of following sizes of steel conduit along with accessories in surface / recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit as required. 32 mm | 100.00 | Meter |  | 200.00 | 20000.00 | 210.00 | 21000.00 | 350.00 | 35000.00 | 348.00 | 34800.00 | 462.00 | 46200.00 | 360.00 | 36000.00 | 420.00 | 42000.00 | 150.00 | 15000.00 | 220.00 | 22000.00 | 218.45 | 21845.00 | 15000.00 | SYNERGY LIGHTING SOLUTIONS
15.00 | Supply of 4 X 16 sq.mm PVC insulated and XLPE Sheathed armoured Aluminium conductor cable of 1.1KV grade confirming to IS:7098 with up to date amendments etc. as required. | 500.00 | Meter |  | 200.00 | 100000.00 | 270.00 | 135000.00 | 250.00 | 125000.00 | 219.00 | 109500.00 | 200.00 | 100000.00 | 350.00 | 175000.00 | 150.00 | 75000.00 | 300.00 | 150000.00 | 190.00 | 95000.00 | 218.90 | 109450.00 | 75000.00 | MANKHA ELECTROTECH PRIVATE LIMITED
16.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.Upto 35 sq. mm (clamped with 1mm thick saddle) | 400.00 | Meter |  | 100.00 | 40000.00 | 120.00 | 48000.00 | 50.00 | 20000.00 | 526.00 | 210400.00 | 120.00 | 48000.00 | 400.00 | 160000.00 | 96.00 | 38400.00 | 40.00 | 16000.00 | 85.00 | 34000.00 | 120.20 | 48080.00 | 16000.00 | SYNERGY LIGHTING SOLUTIONS
17.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Upto 35 sq. mm | 100.00 | Meter |  | 100.00 | 10000.00 | 90.00 | 9000.00 | 45.00 | 4500.00 | 47.00 | 4700.00 | 120.00 | 12000.00 | 600.00 | 60000.00 | 96.00 | 9600.00 | 30.00 | 3000.00 | 80.00 | 8000.00 | 120.70 | 12070.00 | 3000.00 | SYNERGY LIGHTING SOLUTIONS
18.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 X 16 sq. mm (28mm) | 8.00 | Set |  | 100.00 | 800.00 | 1000.00 | 8000.00 | 450.00 | 3600.00 | 397.00 | 3176.00 | 660.00 | 5280.00 | 400.00 | 3200.00 | 420.00 | 3360.00 | 250.00 | 2000.00 | 1250.00 | 10000.00 | 2240.40 | 17923.20 | 800.00 | M R ELECTRICALS
| Total in Figures |  |  |  |  | 4456760.00 |  | 2827280.00 |  | 3235502.00 |  | 3352258.00 |  | 3281054.00 |  | 3831172.00 |  | 3477390.00 |  | 2737960.00 |  | 2639390.00 |  | 2732125.60
Lowest Amount Quoted BY: Shiva Enterprises(2639390.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of Indoor LED Lights of NITB at R.B. Airport, Bhopal. SH Internal Electrical Works. Tender ID: 2026_AAI_265242_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Shiva Enterprises (BID ID -984350) | 2639390.00 | L1
| 2 | Edge Telecom Pvt Ltd (BID ID -983334) | 2732125.60 | L2
| 3 | SYNERGY LIGHTING SOLUTIONS (BID ID -984108) | 2737960.00 | L3
| 4 | Manish Electricals (BID ID -984153) | 2827280.00 | L4
| 5 | surbhi association (BID ID -984253) | 3235502.00 | L5
| 6 | Variant Infratech Private Limited (BID ID -984241) | 3281054.00 | L6
| 7 | Taral Electricals (BID ID -984371) | 3352258.00 | L7
| 8 | MANKHA ELECTROTECH PRIVATE LIMITED (BID ID -983795) | 3477390.00 | L8
| 9 | O. P. CONSTRUCTIONS (BID ID -978664) | 3831172.00 | L9
| 10 | M R ELECTRICALS (BID ID -984147) | 4456760.00 | L10