## BoQ1
Government eProcurement System Created By: Tushar Dixit Created Date/Time: 14-May-2026 11:40 AM Tender Title: DSITC of BMS Tender ID: 2026_AAI_266274_1
Tender Inviting Authority: Senior Manager (Engg.-E), AAI, DATS Complex, IGI Airport, New Delhi.
Name of Work: Design, Supply, Installation, Testing and Commissioning of Building Management System (BMS) along with eight (08) years of AICMC (after Two (02) years DLP) at DATS Complex, IGI Airport, New Delhi. SH: Replacement of Existing BMS System
Contract No: AAI/DATS/E-E/BMS-Rep./2025-26/ENIT/06
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | V Automation System (GSTN-NA) BID ID -1005357 |  | Electrotech Overseas Pvt Ltd (GSTN-NA) BID ID -1003817
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH-I SITC Works:-
1.01 | SITC of BMS Server and client Computer System as per tender specifications: i7 Processor (14th or latest generation) or Equivalet PC, Intel(R), Xeon(R) Processor, 3.1GHz, 4MB Cache with 32 GB RAM, & 3 TB SSD for Client system (1 TB SSD for Server system), 10/100 Mbps Ethernet card, USB connection & internal modem, Microsoft(R) Windows(R) 11 OS Professional original, 100/1000 Mbps NIC for Network connection and anti virus having perpetual license software with 32" colour graphics LED monitor as per Tender Specifications. Accessories included Optical Mouse, Key Pad, Laser jet A4 printer having duplexing capacity(only for client system) with the above BMS System configuration. Windows Licensed software compatible with the BMS platform etc. complete as required for both server and Client system. | 1.00 | Nos. |  | 802999.00 | 802999.00 | 778754.00 | 778754.00 | 778754.00 | Electrotech Overseas Pvt Ltd
2.00 | Application Software SITC of the following window based graphical software for IBMS system with Redundant Client for Operator workstation. The following software packages shall have minimum 10000 point license (Both Hardware + Software) features and compliances complete as per tender specifications. (a) 3D & HD vector dynamic, responsive graphics with Autocad import of plan with Zoom In & Zoom Out facility, should have reports, dashbords etc. options completely customijable as per client. (b) Native 64 Bit System , BTL,UL,EN Certified System, BACnet Profile B-AWS/OWS/BC as per the BTL Listing, IoT native connectivity(MQTT) | 1.00 | Nos. |  | 3991088.00 | 3991088.00 | 3860168.00 | 3860168.00 | 3860168.00 | Electrotech Overseas Pvt Ltd
2.01 | (c) Built in C# engine or FBD to build project dynamically, Multi-Monitor Support-(Min 4 Nos), Multi-language support (d) Certified OPC UA Server/Client by OPC Foundation (e) HTML5 based Web-Server software shall permit use of Standard Web-Browsers such as Microsoft Edge, Google Chrome, Mozilla Firefox, etc (f) The Software shall comply to international standards and strive to deliver products that meet security standards such as ISA/IEC 62443, UL2900/TLS 1.3, ISO / IEC 27001, ISO / IEC62443 (g) End-to-end encryption from client to server, End-to-end encryption between servers, Certificate-based data exchange, Encrypted backups (h) Audit Trail, 4-Eye Principle or 21 CFR Part-11 Complaint, Data Point Validation, Verified tempering evidence for report transmission (i) Ability to provide/ receive data to other systems through OPC UA Server/client and Rest web services interface
3.00 | SITC of True IP Based (BTL Certified), UL Listed DDC Standalone 32 Bit Intelligent, peer to peer communication, interoperable DDC, BACnet secure connect communication as per the specification. The compact controller shall have inbuilt 2-port Ethernet switch. The controller shall have 24 inputs / outputs inbuilt and can be expandable upto max 80 points by Input / Output Modules. The DDC shall have minimum 1.2 Ghz processor with minimum 1 GByte RAM and minimum 8 GByte NAND Flash. The controller shall be freely programmable and have System functions (alarming, scheduling, trending, access protection with individually definable user profiles and categories). It should have WLAN interface, Cloud connectivity for remote access and inbuilt port for POT for local interface. Complete as per tender specifications. Note: Comissioning tool should not be dependent on any license / dongle and no extra cost should be charged. The above shall be housed in vandal proof, lockable & secure MS Cabinets to be supplied along with all necessary switchgear protections as required. Number of controllers shall have spare capacity of 15% for future expansion. a) Controller for Chiller Plant Manager as per IO summary b) Controller for AHU's ( Max 1 Ahu's in 1 DDC) as per IO summary c) Controller for CSU's ( Max 1 Csu's in 1 DDC) as per IO summary d) Controller for Basement Ventilation (Fresh Air Fans, Exhaust Fans, Liftwell Pressurization Fans, Staircase Pressurization Fans, Air Smoke Exhaust Fans) as per IO summary e) Controller for Lifts (Max 3 lifts at 1 DDC) as per IO summary f) Controller for Plumbing (4 at 1 DDC) as per IO summary | 1.00 | Lot |  | 38472550.00 | 38472550.00 | 37288313.00 | 37288313.00 | 37288313.00 | Electrotech Overseas Pvt Ltd
4.00 | SITC of True IP Based BTL & UL Listed with BACnet secure connect communication for third party integration. The controller shall have 2-port Ethernet switch and WLAN interface. It should have BTL label/certified (BACnet communications passed the BTL test) and consisting of Dual microprocessor or as per specifications with Storage capacity of 1 GByte RAM. It should support real time clock with backup of upto 7 days using Super capacitor and also should have option for external battery if required. Number of integration data points should be 500 points. Complete as per tender specifications. Note: 3rd party make integartor is not acceptable. a) For Fire Alarm System on BACnet/IP b) For UPS on MODbus RS485 c) For Integration of Pump PLC Soft Data Integration d) Integration of PAHU on Modbus over RS485 e) Integration of Ahu's VFD on Modbus over RS485 f) Integration of UPS on Modbus over RS485 g) Integration of VRF on Bacnet/IP h) Integration of Cooling Towers i) Integration of Chemical dosing plant j) Integration of Fire Dampers | 1.00 | Lot |  | 3419084.00 | 3419084.00 | 3212987.00 | 3212987.00 | 3212987.00 | Electrotech Overseas Pvt Ltd
5.00 | Field instruments Supplying, installing, testing and commissioning of the following sensors / transducers / transmitters. The DDC shall support sensor with DC 0...20 mA or 4...20 mA, DC 0 ... 10 V, LG-Ni 1000, 2x LG-Ni1000, Pt 1000 , NTC 10k, NTC 100k, 1000 Ohm. Complete as per tender specifications.
5.01 | Immersion Temp. Sensor with Thermowell | 40.00 | Nos. |  | 8120.00 | 324800.00 | 7706.00 | 308240.00 | 308240.00 | Electrotech Overseas Pvt Ltd
5.02 | Differential Pressure transmitter /Switch for Water pressure measurement | 43.00 | Mtr. |  | 22100.00 | 950300.00 | 21816.00 | 938088.00 | 938088.00 | Electrotech Overseas Pvt Ltd
5.03 | Duct Temp. Sensor | 72.00 | Nos. |  | 5980.00 | 430560.00 | 5723.00 | 412056.00 | 412056.00 | Electrotech Overseas Pvt Ltd
5.04 | Duct Air Static pressure Sensor | 60.00 | Nos. |  | 16830.00 | 1009800.00 | 15371.00 | 922260.00 | 922260.00 | Electrotech Overseas Pvt Ltd
5.05 | Differential Pressure Switch Air | 84.00 | Nos. |  | 11010.00 | 924840.00 | 10434.00 | 876456.00 | 876456.00 | Electrotech Overseas Pvt Ltd
5.06 | Current Relay | 65.00 | Mtr. |  | 19280.00 | 1253200.00 | 18171.00 | 1181115.00 | 1181115.00 | Electrotech Overseas Pvt Ltd
5.07 | Bi-Level Switch | 5.00 | Nos. |  | 23800.00 | 119000.00 | 21980.00 | 109900.00 | 109900.00 | Electrotech Overseas Pvt Ltd
5.08 | Outside Temp & Humidity sensor | 5.00 | Nos. |  | 16900.00 | 84500.00 | 16362.00 | 81810.00 | 81810.00 | Electrotech Overseas Pvt Ltd
5.09 | Water level switches for water tanks | 7.00 | Nos. |  | 31290.00 | 219030.00 | 30006.00 | 210042.00 | 210042.00 | Electrotech Overseas Pvt Ltd
6.00 | Supply, installation, testing and commissioning of hand held portable operator terminals (POT) minimum 7 inch. TFT display with capacitive touch screen type, shall be able to view graphs , alarms , parameters etc. POT shall have integrated web server. POT With all required connectors etc as per technical specification etc. as per tender specifications. | 1.00 | Nos. |  | 113619.00 | 113619.00 | 113619.00 | 113619.00 | 113619.00 | Electrotech Overseas Pvt Ltd, V Automation System
7.00 | Cabling and Conduiting
7.01 | Supplying, laying, termination, testing and commissioning of 2 Core x 1.0 sq mm PVC insulated, Annealed Tinned Copper, twisted, shielded, unarmoured FRLS cable as per tender specifications.. | 5000.00 | RMT |  | 58.00 | 290000.00 | 46.00 | 230000.00 | 230000.00 | Electrotech Overseas Pvt Ltd
7.02 | Supplying, laying, termination, testing and commissioning of 4 Core x 1.0 sq mm PVC insulated, Annealed Tinned Copper, twisted, shielded, unarmoured FRLS cable. | 3500.00 | RMT |  | 92.00 | 322000.00 | 80.00 | 280000.00 | 280000.00 | Electrotech Overseas Pvt Ltd
7.03 | Supplying, laying, termination, testing & commissioning of CAT 6 unarmoured Cables with required accessories like RJ45 connector etc as per tender specifications. | 915.00 | RMT |  | 54.00 | 49410.00 | 44.00 | 40260.00 | 40260.00 | Electrotech Overseas Pvt Ltd
7.04 | Supplying and laying of 25mm of MS conduit on surface/recess including cutting/filling chases along with conduit accessories etc. complete as required as per tender specifications.. | 2000.00 | RMT |  | 132.00 | 264000.00 | 121.00 | 242000.00 | 242000.00 | Electrotech Overseas Pvt Ltd
7.05 | SITC of GI Flexible conduit for termination in the DDC Panels | 2500.00 | RMT |  | 110.00 | 275000.00 | 105.00 | 262500.00 | 262500.00 | Electrotech Overseas Pvt Ltd
7.06 | Supply, Installation, Testing & Commissioning of 6 core multicore Optical Fibre cable for connectivity between network switches as per tender specifications. | 500.00 | RMT |  | 192.00 | 96000.00 | 180.00 | 90000.00 | 90000.00 | Electrotech Overseas Pvt Ltd
7.07 | SITC of GI perforated Cable Tray of Size 150 mm X 50 mm having a thickness of 1.6 mm (Noiminal) duly protected with Cable Cover Trey of suitable Size as required at site as per tender specifications. | 1000.00 | RMT |  | 611.00 | 611000.00 | 410.00 | 410000.00 | 410000.00 | Electrotech Overseas Pvt Ltd
8.00 | Network Switches
8.01 | Supply, installation, testing and commissioning of Layer 2 switch with 24 ports (RJ-45) including SFP modules, rack mountable, SMPS power supply & other termination accessories (Like Pigtails/LIUs/ Convertors/Splicing equipment ,Patch panel, Patch Cord, Etc) complete as per specifications and as required for BMS DDC Panel Networking. The switch to switch distance shall not exceed beyond 80 meters complete as per tender specifications. | 8.00 | Nos |  | 66544.00 | 532352.00 | 52000.00 | 416000.00 | 416000.00 | Electrotech Overseas Pvt Ltd
8.02 | Supply, installation, testing and commissioning of Layer 2 switch with 16 ports (RJ-45) including SFP modules, rack mountable, SMPS power supply & other termination accessories (Like Pigtails/LIUs/ Convertors/Splicing equipment ,Patch panel, Patch Cord, Etc) complete as per specifications and as required for BMS DDC Panel Networking. The switch to switch distance shall not exceed beyond 80 meters Complete as per tender specifications. | 8.00 | Nos |  | 61900.00 | 495200.00 | 51250.00 | 410000.00 | 410000.00 | Electrotech Overseas Pvt Ltd
9.00 | AICMC COST for 8 Years after defect liability period of 2 years:- All inclusive comprehensive maintenance contract for providing experienced electrical /electronics /software engineer for preventive, breakdown and servicing(minimum 4 quarterly visits in a year) of BMS system installed for operation & monitering of HVAC & other associated systems inclusive of low side, CCUs (PACs), SCU, VFD, Fire fighting system , UPS, VRF and lifts remotely as per above BMS SITC works for BMS DATS Complex including providing operation support in general shift by deploying qualified B.Tech engineer having sufficient experience of the BMS system for operation and supervision of these installations complete all as required and specified. Agency have to supply and replace all the faulty spares including controllers, wires,cables panels etc. as per OEM recommendations complete all as required as per specifications.
9.01 | 1st year after DLP Period of 2 years Rate for 1st year after DLP= (3.5% of SH-I i.e. SITC Cost). | 1.00 | Year |  | 1926761.62 | 1926761.62 | 1843609.88 | 1843609.88 | 1843609.88 | Electrotech Overseas Pvt Ltd
9.02 | 2nd year after DLP Period of 2 years Rate for 2nd year after DLP (6% escalation of SH-II (9.1 ) Cost) | 1.00 | Year |  | 2042367.32 | 2042367.32 | 1954226.47 | 1954226.47 | 1954226.47 | Electrotech Overseas Pvt Ltd
9.03 | 3rd year after DLP Period of 2 years Rate for 3rd year after DLP= (6% escalation of SH-II (9.2 ) Cost) | 1.00 | Year |  | 2164909.36 | 2164909.36 | 2071480.06 | 2071480.06 | 2071480.06 | Electrotech Overseas Pvt Ltd
9.04 | 4th year after DLP Period of 2 years Rate for 4th year after DLP= (6% escalation of SH-II (9.3 ) Cost) | 1.00 | Year |  | 2294803.92 | 2294803.92 | 2195768.86 | 2195768.86 | 2195768.86 | Electrotech Overseas Pvt Ltd
9.05 | 5th year after DLP Period of 2 years Rate for 5th year after DLP= (6% escalation of SH-II (9.4 ) Cost) | 1.00 | Year |  | 2432492.16 | 2432492.16 | 2327514.99 | 2327514.99 | 2327514.99 | Electrotech Overseas Pvt Ltd
9.06 | 6th year after DLP Period of 2 years Rate for 6th year after DLP= (6% escalation of SH-II (9.5 ) Cost) | 1.00 | Year |  | 2578441.69 | 2578441.69 | 2467165.89 | 2467165.89 | 2467165.89 | Electrotech Overseas Pvt Ltd
9.07 | 7th year after DLP Period of 2 years Rate for 7th year after DLP= (6% escalation of SH-II (9.6 ) Cost) | 1.00 | Year |  | 2733148.19 | 2733148.19 | 2615195.84 | 2615195.84 | 2615195.84 | Electrotech Overseas Pvt Ltd
9.08 | 8th year after DLP Period of 2 years Rate for 8th year after DLP= (6% escalation of SH-II (9.7 ) Cost) | 1.00 | Year |  | 2897137.08 | 2897137.08 | 2772107.59 | 2772107.59 | 2772107.59 | Electrotech Overseas Pvt Ltd
| Total in Figures |  |  |  |  | 74120393.34 |  | 70921637.58
Lowest Amount Quoted BY: Electrotech Overseas Pvt Ltd(70921637.58)

## BOQ Summary
BOQ Summary Details Tender Title: DSITC of BMS Tender ID: 2026_AAI_266274_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Electrotech Overseas Pvt Ltd (BID ID -1003817) | 70921637.58 | L1
| 2 | V Automation System (BID ID -1005357) | 74120393.34 | L2