## BoQ1
Government eProcurement System Created By: Parmeet Dahiya Created Date/Time: 15-Apr-2026 03:29 PM Tender Title: SITC of EnM Installations Tender ID: 2026_AAI_269590_1
Tender Inviting Authority: SENIOR MANAGER ENGG(E), RHQ, NR, AAI RHQ-NR, NATS Building, IGI Airport, New Delhi.
Name of Work: Construction of proposed Rooms for New UPS and Battery Banks (COPS system) at INLUS, GAGAN Complex Nangloi, Delhi. (SH- SITC of E&M installations, Internal & External electrification work).
TENDER ID NO.: 2026_AAI_269590_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Shiva Enterprises (GSTN-NA) BID ID -1005384 |  | VENTURE INDIA (GSTN-NA) BID ID -1005777 |  | ASHOKA ELECTRICALS (GSTN-NA) BID ID -1005815
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | LED Panel light 2x2 ft. (System lumen efficacy≥105 <120 lm/Watt) S.I.T.C of 36 Watt Panel light 2x2 ft. of following body material & construction as per IS: 10322 with driver as per the requirement with Driver efficiency >85%, Operating voltage AC 140-270 Volt, freq 50/60 hz, Operating temp range -15 deg to 40°C, internal surge protection of 2.5 KV with Short & Open circuit protection, THD < 10%, P. F.≥0.95, IP20, CRI >80, UGR (Unified Glare Rating) <19, Flicker free, (flicker should be below 5 %), life time (LED, Driver & electrical circuitry) of minimum 50000 Burning Hours with, 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report, CCT 3000°K /4000°K /5700°K /6000°K /6500°K (As per ANSI Bin), SDCM(Standard Deviation Color Matching) <3, Maximum power consumption should not more than the specified rating & Fixture shall be of relevant BIS standard & trade mark certificate ( T.C.). Manufactures Word Mark/ Name Engraved/ Embossing/ Screen printing on housing complete in all respect i/c connections with 1.5 sq mm FRLS, PVC insulated copper conductor single core cable and earthing etc. as required with Minimum 5 year OEM warranty. System lumen efficacy ≥105<120 lm/Watt output. LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size & CCT shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C). Powder coated die cast / Extruded aluminium Body (Thickness ≥ 1.20 mm) | 27.00 | Nos | 2120.34 | 1175.00 | 31725.00 | 1220.00 | 32940.00 | 1300.00 | 35100.00 | 31725.00 | Shiva Enterprises
2.00 | LED Down lighter (SMD Type) (System lumen efficacy ≥ 105 < 120 lm/Watt ) S.I.T.C of 10 Watt LED Recessed/ surface Down lighter (Round/ square/ Rectangular) SMD type of following body material with PMMA & prismatic diffuser & construction as per IS:10322 with driver as per requirement with Driver efficiency >85%, Operating voltage AC 140-270 Volt, Frequency 50/60 hz, Operating temp range -15°C to 40°C, internal surge protection of 2.5 KV with Short & Open circuit protection,THD <10%, P.F.≥0.95, IP20, CRI>80 , UGR (Unified Glare Rating) <19, Flicker free (flicker should be below 5%), life time (LED, Driver & electrical circuitary) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends, CCT 3000°K /4000°K /5700°K /6000°K /6500°K (As per ANSI Bin), SDCM (Standard Deviation Color Matching) <3, Maximum power consumption should not more than the specified rating & Fixture shall be confirming to relevant BIS standards & trade mark certificate (T.C.). Manufactures Word Mark/ Name Engraved/ Embossing/ Screen printing on housing Complete in all respect i/c connections with 1.5 sq mm FRLS, PVC insulated copper conductor single core cable & earthing etc. as required with Minimum 5 year OEM warranty. System lumen efficacy ≥105 & <120 lm/Watt output. LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size & CCT shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C) Powder coated die cast /Extruded aluminum Body including trim | 16.00 | Nos | 494.92 | 470.00 | 7520.00 | 550.00 | 8800.00 | 200.00 | 3200.00 | 3200.00 | ASHOKA ELECTRICALS
3.00 | LED Flood Light, powder coated pressure die cast aluminum (System lumen efficacy ≥120 & <135 lm/Watt) S.I.T.C. of 100 Watt Flood Light, powder coated pressure die cast aluminum body with built in or separate driver as per the requirement with Driver efficiency >85%, Input voltage:Input voltage: 140-270 Volt AC, freq 50/60 hz, Operating temp range -15°C to 50°C, internal surge protection of 5 KV L,N,E as per IEC 61000-4-5, Driver efficiency >85%, THD <10% as per IEC 61000-3-2, P.F.≥0.95, IP-66,IK-10, CRI >80, under voltage & over voltage protection, EMI-EMC as per CISPR-15, lenses for beam angle 30 deg120deg as per the application & the project requirement deg. suitable tiltable fitting, life time (LED, Driver & electrical circuitry) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report, CCT 3000°K /4000°K /5700°K /6000°K/6500°K (As per ANSI Bin), SDCM (Standard Deviation Color Matching) <5, Maximum power consumption should not more than the specified rating & Fixture shall be of relevant BIS standard complete in all respect i/c connections with 1.5 sq mm FRLS, PVC insulated copper conductor single core cable & earthing etc. as required with Minimum 5 year OEM warranty. System lumen efficacy ≥120 & <135 lm/Watt output. LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size & CCT shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C). | 7.00 | Nos. | 2084.75 | 2200.00 | 15400.00 | 3300.00 | 23100.00 | 1800.00 | 12600.00 | 12600.00 | ASHOKA ELECTRICALS
4.00 | Supplying and fixing DP sheet steel enclosure on surface/ recess along with 25/32 A 240 V "C" curve DP MCB complete with connections, testing and commissioning etc. as required. | 14.00 | Job | 963.96 | 1360.00 | 19040.00 | 1050.00 | 14700.00 | 600.00 | 8400.00 | 8400.00 | ASHOKA ELECTRICALS
5.00 | Supplying & fixing following way, horizontal type three pole & neutral, sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, inter-connections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator)
5.01 | 4 way (4 + 12), Double door | 1.00 | Each | 3373.46 | 3260.00 | 3260.00 | 1825.00 | 1825.00 | 3000.00 | 3000.00 | 1825.00 | VENTURE INDIA
5.02 | 6 way (4+18), Double door | 1.00 | Each | 4101.59 | 4350.00 | 4350.00 | 2200.00 | 2200.00 | 4300.00 | 4300.00 | 2200.00 | VENTURE INDIA
6.00 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
6.01 | 5/6 A switch | 26.00 | Each | 84.93 | 130.00 | 3380.00 | 80.00 | 2080.00 | 100.00 | 2600.00 | 2080.00 | VENTURE INDIA
6.02 | 15/16 A switch | 18.00 | Each | 128.64 | 150.00 | 2700.00 | 120.00 | 2160.00 | 110.00 | 1980.00 | 1980.00 | ASHOKA ELECTRICALS
6.03 | 3 pin 5/6 A socket outlet | 14.00 | Each | 100.60 | 180.00 | 2520.00 | 80.00 | 1120.00 | 136.00 | 1904.00 | 1120.00 | VENTURE INDIA
6.04 | 6 pin 15/16 A socket outlet | 18.00 | Each | 162.45 | 240.00 | 4320.00 | 150.00 | 2700.00 | 150.00 | 2700.00 | 2700.00 | VENTURE INDIA, ASHOKA ELECTRICALS
7.00 | Supplying & fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | 25.00 | Each | 32.98 | 30.00 | 750.00 | 28.00 | 700.00 | 130.00 | 3250.00 | 700.00 | VENTURE INDIA
8.00 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc. as required.
8.01 | 2 Module (75 mm X 75 mm) | 8.00 | Each | 245.73 | 350.00 | 2800.00 | 225.00 | 1800.00 | 70.00 | 560.00 | 560.00 | ASHOKA ELECTRICALS
8.02 | 3 Module (100mmX75mm) | 19.00 | Each | 269.65 | 450.00 | 8550.00 | 255.00 | 4845.00 | 90.00 | 1710.00 | 1710.00 | ASHOKA ELECTRICALS
8.03 | 6 Module (200mmX75mm) | 8.00 | Each | 331.49 | 500.00 | 4000.00 | 320.00 | 2560.00 | 140.00 | 1120.00 | 1120.00 | ASHOKA ELECTRICALS
9.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
9.01 | Single pole | 27.00 | Each | 211.10 | 220.00 | 5940.00 | 125.00 | 3375.00 | 200.00 | 5400.00 | 3375.00 | VENTURE INDIA
9.02 | Triple pole and neutral | 2.00 | Each | 1012.62 | 750.00 | 1500.00 | 925.00 | 1850.00 | 660.00 | 1320.00 | 1320.00 | ASHOKA ELECTRICALS
10.00 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required.
10.01 | 63 A | 2.00 | Each | 2368.27 | 2600.00 | 5200.00 | 2050.00 | 4100.00 | 1700.00 | 3400.00 | 3400.00 | ASHOKA ELECTRICALS
11.00 | Providing & Fixing of following rating & breaking capacity Pole MCCB with thermomagnetic release & terminal spreaders in existing cubicle panel board i/c drilling holes in cubicle panel, making connections etc. as required.
11.01 | 400 A, 50KA, FP MCCB | 2.00 | Each | 35181.83 | 30000.00 | 60000.00 | 30000.00 | 60000.00 | 25000.00 | 50000.00 | 50000.00 | ASHOKA ELECTRICALS
12.00 | Supplying & Fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 10.00 | Each | 10.72 | 30.00 | 300.00 | 8.00 | 80.00 | 270.00 | 2700.00 | 80.00 | VENTURE INDIA
13.00 | Supplying & Fixing of following sizes of medium class PVC conduit along with accessories in surface/ recess i/c cutting the wall & making good the same in case of recessed conduit as required.
13.01 | 20 mm | 120.00 | Meter | 105.55 | 100.00 | 12000.00 | 100.00 | 12000.00 | 35.00 | 4200.00 | 4200.00 | ASHOKA ELECTRICALS
13.02 | 25 mm | 120.00 | Meter | 119.57 | 120.00 | 14400.00 | 110.00 | 13200.00 | 38.00 | 4560.00 | 4560.00 | ASHOKA ELECTRICALS
14.00 | Supply of following sizes FRLSH PVC insulated & PVC round sheathed Multi Core Annealed bare Copper stranded Conductor (flexible) industrial Cables for 1100 Volt grade Conforming to IS 694:2010 as & when required as directed by E-I-C:
14.01 | 3 C x 2.5 sqmm | 200.00 | Meter | 111.00 | 220.00 | 44000.00 | 124.00 | 24800.00 | 155.00 | 31000.00 | 24800.00 | VENTURE INDIA
14.02 | 3 C x 4.0 sqmm | 200.00 | Meter | 170.00 | 270.00 | 54000.00 | 193.00 | 38600.00 | 210.00 | 42000.00 | 38600.00 | VENTURE INDIA
15.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required.
15.01 | 2 x 1.5 sq.mm + 1 x 1.5 sq.mm Earth Wire | 350.00 | Meter | 192.13 | 180.00 | 63000.00 | 190.00 | 66500.00 | 110.00 | 38500.00 | 38500.00 | ASHOKA ELECTRICALS
15.02 | 2 x 2.5 sq.mm + 1 x 2.5 sq.mm Earth Wire | 300.00 | Meter | 226.77 | 270.00 | 81000.00 | 210.00 | 63000.00 | 165.00 | 49500.00 | 49500.00 | ASHOKA ELECTRICALS
15.03 | 2 x 4 sq.mm + 1 x 4 sq.mm Earth Wire | 300.00 | Meter | 275.42 | 290.00 | 87000.00 | 270.00 | 81000.00 | 173.00 | 51900.00 | 51900.00 | ASHOKA ELECTRICALS
16.00 | Supply of following sizes XLPE Armoured Cables with ALUMINIUM Conductor 650/1100V. Grade confirming to IS:7098 (Part-1) 1988 with upto date amendments complete as required as directed by E-I-C:
16.01 | 3.5 X 185 sqmm | 500.00 | Meter | 1426.00 | 1100.00 | 550000.00 | 1500.00 | 750000.00 | 1300.00 | 650000.00 | 550000.00 | Shiva Enterprises
16.02 | 3.5 X 50 sqmm | 400.00 | Meter | 439.00 | 350.00 | 140000.00 | 425.00 | 170000.00 | 380.00 | 152000.00 | 140000.00 | Shiva Enterprises
17.00 | Laying of one number PVC insulated & PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required.
17.01 | Above 35 sq.mm & upto Upto 95 sq.mm | 250.00 | Meter | 47.00 | 70.00 | 17500.00 | 50.00 | 12500.00 | 60.00 | 15000.00 | 12500.00 | VENTURE INDIA
17.02 | Above 95 sq.mm & upto 185 sq.mm | 400.00 | Meter | 63.49 | 110.00 | 44000.00 | 60.00 | 24000.00 | 60.00 | 24000.00 | 24000.00 | VENTURE INDIA, ASHOKA ELECTRICALS
18.00 | Laying & fixing of one number PVC insulated & PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required.
18.01 | Above 35 sqmm & Upto 95 sqmm (clamped with 25X3 mm MS flat clamp) | 100.00 | Meter | 107.20 | 95.00 | 9500.00 | 80.00 | 8000.00 | 60.00 | 6000.00 | 6000.00 | ASHOKA ELECTRICALS
18.02 | Above 95 sq. mm and upto 185 sq. mm (clamped with 25/40x3mm MS flat clamp) | 100.00 | Meter | 126.16 | 130.00 | 13000.00 | 80.00 | 8000.00 | 60.00 | 6000.00 | 6000.00 | ASHOKA ELECTRICALS
19.00 | Laying of one number PVC insulated & PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonary open duct as required.
19.01 | Above 35 sq. mm & Upto 95 sq. mm | 50.00 | Meter | 37.11 | 85.00 | 4250.00 | 25.00 | 1250.00 | 60.00 | 3000.00 | 1250.00 | VENTURE INDIA
19.02 | Above 95 sq. mm & upto 185 sq. mm | 100.00 | Meter | 51.95 | 110.00 | 11000.00 | 38.00 | 3800.00 | 60.00 | 6000.00 | 3800.00 | VENTURE INDIA
20.00 | Laying & Fixing of one number PVC insulated & PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required.
20.01 | Above 35 sq.mm and Upto 95 sq.mm (clamped with 25 x 3 mm MS flat clamp) | 100.00 | meter | 75.86 | 95.00 | 9500.00 | 60.00 | 6000.00 | 60.00 | 6000.00 | 6000.00 | VENTURE INDIA, ASHOKA ELECTRICALS
20.02 | Above 95 sq.mm and upto 185 sq.mm (clamped with 25 / 40 x 3mm MS flat clamp) | 50.00 | meter | 94.83 | 110.00 | 5500.00 | 80.00 | 4000.00 | 60.00 | 3000.00 | 3000.00 | ASHOKA ELECTRICALS
21.00 | Supplying & laying of following size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting & cutting, jointing etc.direct in ground (75 cm below ground level) i/c excavation & refilling the trench but excluding sand cushioning & protective covering etc., complete as required.
21.01 | 120 mm dia (OD-120 mm & ID-103 mm nominal) | 300.00 | Meter | 303.46 | 300.00 | 90000.00 | 300.00 | 90000.00 | 170.00 | 51000.00 | 51000.00 | ASHOKA ELECTRICALS
22.00 | Providing, Laying & Fixing of following dia G.I. pipe (medium class) in ground complete with G.I. fittings i/c trenching (75 cm deep)and re-filling etc as required.
22.01 | 100 mm dia | 50.00 | Meter | 1489.24 | 1200.00 | 60000.00 | 1700.00 | 85000.00 | 165.00 | 8250.00 | 8250.00 | ASHOKA ELECTRICALS
23.00 | Earthing with G.I. earth pipe 4.5 mtr. long, 40 mm dia i/c accessories & providing masonary enclosure with cover plate having locking arrangement & watering pipe etc. with charcoal/ coke & salt as required. | 2.00 | Set | 5652.68 | 7000.00 | 14000.00 | 6500.00 | 13000.00 | 35000.00 | 70000.00 | 13000.00 | VENTURE INDIA
24.00 | Supplying & laying 25mm x 5mm G.I strip at 0.50 metre below ground as strip earth electrode i/c connection / terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 20.00 | Meter | 118.74 | 250.00 | 5000.00 | 125.00 | 2500.00 | 150.00 | 3000.00 | 2500.00 | VENTURE INDIA
25.00 | Providing & fixing 25 mm x 5 mm G.I. strip on surface or in recess for connections etc. as required. | 100.00 | Meter | 201.20 | 260.00 | 26000.00 | 190.00 | 19000.00 | 140.00 | 14000.00 | 14000.00 | ASHOKA ELECTRICALS
26.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 100.00 | Meter | 57.72 | 25.00 | 2500.00 | 30.00 | 3000.00 | 30.00 | 3000.00 | 2500.00 | Shiva Enterprises
27.00 | Providing & fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ recessed conduit/submain wiring/ cableas required. | 1500.00 | Meter | 34.63 | 23.00 | 34500.00 | 25.00 | 37500.00 | 36.00 | 54000.00 | 34500.00 | Shiva Enterprises
28.00 | Earthing with copper earth plate 600 mm x 600 mm x 3 mm thick i/c accessories & providing masonary enclosure with cover plate having locking arrangement & watering pipe of 2.7 metre long etc. with charcoal/ coke & salt as required. | 8.00 | Set | 11410.90 | 8500.00 | 68000.00 | 12500.00 | 100000.00 | 17600.00 | 140800.00 | 68000.00 | Shiva Enterprises
29.00 | Supplying & laying 25mm x 5mm copper strip at 0.50 metre below ground as strip earth electrode, i/c connection / terminating with nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping & with 2 sets of brass nut bolt & spring washer spaced at 50mm) | 50.00 | Meter | 801.52 | 650.00 | 32500.00 | 900.00 | 45000.00 | 1680.00 | 84000.00 | 32500.00 | Shiva Enterprises
30.00 | Providing & fixing 25mm x 5mm copper strip in 40mm dia G.I. pipe from earth electrode i/c connection with brass nut, bolt, spring, washer excavation & re-filling etc. as required. | 50.00 | Meter | 1278.96 | 750.00 | 37500.00 | 1300.00 | 65000.00 | 1690.00 | 84500.00 | 37500.00 | Shiva Enterprises
31.00 | Providing & fixing 25mm x 5mm copper strip on surface or inrecess for connections etc. as required. | 150.00 | Meter | 958.19 | 650.00 | 97500.00 | 800.00 | 120000.00 | 1690.00 | 253500.00 | 97500.00 | Shiva Enterprises
32.00 | Supply of 2.0 TR BEE-5 star rating wall mounted Inverter Split type Air Conditioning Units operating on eco-refrigerant (R32 preferrably), copper condenser & copper evaporator coils suitable for operation on 220-240 V single phase 50 Hz supply having all safety features, air filters, cordless remote for operation etc. incl. all accessories such as std. length copper pipe (not less than 3 mtrs), drain pipe, power cable, control cable etc. having compressor warranty of minimum 05 years complete as required. | 12.00 | Each | 54033.00 | 43000.00 | 516000.00 | 48000.00 | 576000.00 | 52000.00 | 624000.00 | 516000.00 | Shiva Enterprises
33.00 | Installation, Testing & Commissioning of 2.0 TR Split AC as per site conditions & connecting the Indoor & Outdoor unit with standard copper pipe of 3 mtrs. approx, brazing, connecting the drain pipe with indoor unit etc. complete as required as directed by E-I-C. | 12.00 | Each | 1180.20 | 1250.00 | 15000.00 | 1500.00 | 18000.00 | 3000.00 | 36000.00 | 15000.00 | Shiva Enterprises
34.00 | Supplying & fixing of copper pipe (1/2", 1/4") for suction / liquid line and connecting the same with existing copper pipe, brazing etc. of indoor / outdoor unit along with insulation, fixing insulation with vinyl tape etc. complete as required as per site requirement and as directed by E-I-C. | 100.00 | Meter | 1033.54 | 1500.00 | 150000.00 | 500.00 | 50000.00 | 1000.00 | 100000.00 | 50000.00 | VENTURE INDIA
35.00 | Supply & Fixing of Drain Pipe with insulation of suitable length to connect with existing drain pipe of AC complete as required | 150.00 | Meter | 88.59 | 200.00 | 30000.00 | 30.00 | 4500.00 | 50.00 | 7500.00 | 4500.00 | VENTURE INDIA
36.00 | Supplying & Fixing of outdoor wall brackets so as to mount the outdoor units of Split AC on wall / floor complte as required with nut, bolts etc. as directed by E-I-C. | 12.00 | Job | 935.11 | 850.00 | 10200.00 | 400.00 | 4800.00 | 1500.00 | 18000.00 | 4800.00 | VENTURE INDIA
37.00 | Supplying & applying of preventive coating on Copper pipes (condenser / evaporator) to prevent refrigerant leakage from 2 TR Split Acs complete as required as directed by E-I-C. | 12.00 | Job | 987.00 | 250.00 | 3000.00 | 400.00 | 4800.00 | 600.00 | 7200.00 | 3000.00 | Shiva Enterprises
38.00 | LT PANEL S.I.T.C. of cubicle type LT panel (TTA) indoor type, IP54 protection, 50 KA suitable for 415V, 3 Phase, 4 wire 50 Hz AC supply system fabricated in compart-mentalized design from CRCA sheet steel of 2mm thick for frame work & covers, 3mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade having 4P Aluminium alloy bus bars of high conductivity, SMC bus bar supports with short circuit withstand capacity of 50 KA for 1 sec, bottom base channel of MS section not less than 100 mm x 50 mm x 5 mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25 mm x 5 mm at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Al. Bus bars & control wiring with suitable size of PVC insulated copper conductor, cable alleys, cable gland plates in two half i/c providing following:
38.01 | (A) INCOMER i) 02 Nos. MCCB, 300A, 35 kA, Four Pole with micro-processor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu) for both incomers. ii) 01 No. MCCB, 300A, 35 kA, Four Pole with micro-processor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu) for bus coupler. Each MCCB above shall be provided with: i) 16 Parameter Multifunction digital meter to read A, V, KVA, KW, KVAR, KVAH, Hz, P. F & THD etc. The MFM to be duly equipped with RS-485 Port on both the incomer MCCBs. ii) OFF/ON/Trip indicating LED lights with 2A SP MCB iii) 1 Set Extended Rotary operating mechanism & terminal extension spreaders for all MCCBs. iv) 1-Set of LED Phase Indicating Lights R,Y,B with 2A SP MCB for protection. (B) BUS BARS 4 Nos 400 A Electrolytic Aluminium Bus- Bars of equal cross-section. (C) Accessories for Electrical Inter-Locking i) Electrical interlocking arrangement as per drawing approved by E-I-C & technical specifications among 2 nos. Incomers from Main LT Panel & 1 nos. Bus coupler i/c inter-connections etc. as required.
38.02 | (D) OUTGOINGS i) 08 Nos. MCCB, 200A, 35 kA, Four Pole with micro--processor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). Each Outgoing MCCB above shall be provided with: i) 16 Parameter Multifunction digital meter to read A, V, KVA, KW, KVAR, KVAH, Hz, P.F & THD etc. The MFM to be duly equipped with RS-485 Port. ii) OFF/ON/Trip indicating LED lights with 2A SP MCB iii) 1 Set Extended Rotary operating mechanism & terminal extension spreaders for all MCCBs. iv) 1-Set of LED Phase Indicating Lights R, Y, B with 2A SP MCB for protection. | 1.00 | Job | 961874.00 | 798000.00 | 798000.00 | 800000.00 | 800000.00 | 826343.00 | 826343.00 | 798000.00 | Shiva Enterprises
39.00 | Execution of items of work as per requirement of site from the CPWD Schedule of Rates (DSR E&M-2022) as per CPWD Specification complete as required (total amount of Rs.3,00,000/- (excl. GST) is kept for DSR Items 2022). Note:- Bidder may refer Clause 32 of e-NOTICE INVITING TENDER before quoting against this item. | 1.00 | Job | 300000.00 | 150000.00 | 150000.00 | 260000.00 | 260000.00 | 175000.00 | 175000.00 | 150000.00 | Shiva Enterprises
| Total in Figures |  |  |  |  | 3482605.00 |  | 3755685.00 |  | 3797997.00
Lowest Amount Quoted BY: Shiva Enterprises(3482605.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of EnM Installations Tender ID: 2026_AAI_269590_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Shiva Enterprises (BID ID -1005384) | 3482605.00 | L1
| 2 | VENTURE INDIA (BID ID -1005777) | 3755685.00 | L2
| 3 | ASHOKA ELECTRICALS (BID ID -1005815) | 3797997.00 | L3