## BoQ1
Government eProcurement System Created By: VIVEKANAND PRASAD MORIL Created Date/Time: 24-Apr-2026 05:58 PM Tender Title: Miscellaneous Work Repair work of existing Kerfs filling for Secondary cable and other works in Operational Area at SGRDJ International Airport Amritsar. Tender ID: 2026_AAI_273334_1
Tender Inviting Authority: <DGM (Engg-Elect), Airports Authority of India, Sri Guru Ram Dass Jee, International Airport, Amritsar - 143101>
Name of Work: <Miscellaneous Work : Repair work of existing Kerfs filling for Secondary cable and other works in Operational Area at SGRDJ International Airport Amritsar.>
Tender ID: <2026_AAI_ 273334 _1>
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | REWINDER TECHNO ELECTRICALS (GSTN-18AAFFR7457K1ZL) BID ID -1011368 |  | Vardhman Airport Solutions Limited (GSTN-NA) BID ID -1010805
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, filling and compaction (by tamping rammer) of cold bitumen in around on existing Kerf (of size approx 30 mm width and depth upto 35 mm) (after applying bituminous emulsion) of runway/taxiway at discrete locations including removing & relaying of secondary lead, removing of old existing bitumen & cleaning the area by compressor or other suitable means as required as per direction of Engineer-in-charge. | 1000.00 | Mtr |  | 150.00 | 150000.00 | 200.00 | 200000.00 | 150000.00 | REWINDER TECHNO ELECTRICALS
2.00 | Filling the existing Kerf having secondary cables (of approx size up to 40mm deep and 30mm wide) in PQC area with Polysulphide joint sealing compound of approved make conforming to BS-5212-1990 or IS: 11433-1995 including making good the damaged corners of concrete slab where reqd., supplying & inserting the back-up rod of appropriate dia, applying 2 coats of primer compatible with polysulphide, use of masking tape etc. and tooled to give a neat finish to the applied sealant, including removal of old sealing compound, baker rod, cleaning the dust by compressor or other suitable means etc & disposal of scrap material as per direction of Engineer-in-charge. | 13000.00 | Mtr |  | 300.00 | 3900000.00 | 350.00 | 4550000.00 | 3900000.00 | REWINDER TECHNO ELECTRICALS
3.00 | Refinishing with concrete of 1:2:4 (1 cement, 2 sand, 4 coarse aggregate) projected surface of existing housing box/ Feeder pillar near approach/runway / taxiway shoulder/apron in soft soil/ Hard surface and needs cements finish on the top of approx size 900mm x 900mm etc., after removing of existing damaged plaster & disposal of debries at a lead of atleast 50 mtrs as reqd as per direction of Enginner-in charge . | 100.00 | Nos |  | 1000.00 | 100000.00 | 960.00 | 96000.00 | 96000.00 | Vardhman Airport Solutions Limited
4.00 | Refinishing with concrete of 1:2:4 (1 cement, 2 sand, 4 coarse aggregate) projected surface of existing housing box near approach/runway / taxiway shoulder/apron in soft soil/ Hard surface and needs cements finish on the top of approx size 600mm x 600mm etc., after removing of existing damaged plaster & disposal of debries at a lead of atleast 50 mtrs as reqd as per direction of Enginner-in charge . | 350.00 | Nos |  | 750.00 | 262500.00 | 960.00 | 336000.00 | 262500.00 | REWINDER TECHNO ELECTRICALS
5.00 | Supply of cubicle MS transformer housing box/Collar of different sizes made of 6mm thick all around except the top surface which is 10mm thick having suitable nos holes on different side surfaces suitable for 32/40/50mm dia HDPE/DWC pipe (As per site requirement and drawing approved by E.I.C.) etc. | 12000.00 | KG |  | 118.00 | 1416000.00 | 150.00 | 1800000.00 | 1416000.00 | REWINDER TECHNO ELECTRICALS
6.00 | SITC of LED Guidance Sign Board of various sizes as per ICAO Annex.14 Vol.I (legends as approved by Engineer-in-Charge) made out of anodized 2mm thick Aluminium frame with suitable angle support with 1.5MM thick Al. backcover, 4 MM thick polycarbonate sheet with glare free face, the letter & symbol should be screen printed on inside of sign face made of self adhesive film of 3M applied on the inside face with required colouring, suitable arrangement shall be made for water tightness & locking arrangement, signboard shall be uniformly internally illuminated with LED lights with 24 V DC converter to achieve illumination level operated on input source 2.5A to 6.6A constant current without flickering including suitable rating isolating transformer, secondary leads, supporting frangible legs & frame, installation on 10 mm thick 1:2:4 CC all around 1 mtr of leg etc. complete as required and as specified. | 32.00 | Sqmt |  | 45000.00 | 1440000.00 | 55000.00 | 1760000.00 | 1440000.00 | REWINDER TECHNO ELECTRICALS
7.00 | SITC of LED Guidance Sign Board of various sizes as per ICAO Annex.14 Vol.I (legends as approved by Engineer-in-Charge) made out of anodized 2mm thick Aluminium frame with suitable angle support with 1.5MM thick Al. backcover, 4 MM thick polycarbonate sheet with glare free face, the letter & symbol should be screen printed on inside of sign face made of self adhesive film of 3M applied on the inside face with required colouring, suitable arrangement shall be made for water tightness & locking arrangement, signboard shall be uniformly internally illuminated with LED lights with 24 V DC converter to achieve illumination level operated on input source 2.5A to 6.6A constant current without flickering including, secondary leads, supporting frangible legs & frame, etc. complete as required and as specified. | 18.00 | Sqmt |  | 36000.00 | 648000.00 | 55000.00 | 990000.00 | 648000.00 | REWINDER TECHNO ELECTRICALS
8.00 | Installation of transformer housing box near approach/runway / taxiway shoulder/apron in soft soil & disposal of debries at a lead of atleast 50 mtrs i/c making 150mm thick cement concrete (1:2:4) all around the box and bottom i/c. providing 10" long 1/2" dia B-class GI pipe at the bottom of the housing box for drainage of water i/c. excavation, alignment, levelling, finishing with cement plaster of projected surface of housing box and needs cements finish on the top etc. as per drawing and as per direction of Enginner-in charge . | 250.00 | Nos |  | 1800.00 | 450000.00 | 1500.00 | 375000.00 | 375000.00 | Vardhman Airport Solutions Limited
9.00 | Earthing with G.I. earth pipe 4.5 meter long, 40 mm dia including accessories, and providing enclosure of size 350mm x 350 mm (H) made out 6 mm thick MS sheet and top cover 10 mm thick MS sheet (counter shunk fitting, M-10 nuts and bolts.) having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 50.00 | Nos |  | 6000.00 | 300000.00 | 8500.00 | 425000.00 | 300000.00 | REWINDER TECHNO ELECTRICALS
10.00 | Supply of cubical Feeder Pillar box of size 0.6 Mtr Width x 0.3 Mtr Depth x 0.45 Mtr Height of MS Sheet 2mm thick Welded structure. i/c 2 Nos. legs of approx 1.0 mtr length made out of 40 mm dia GI/Al. pipe alongwith breakable coupling to make the feeder pillar frangible . Feeder Pillar shall be including 2 Nos. earthing studs on outer side. | 30.00 | Nos |  | 9200.00 | 276000.00 | 14500.00 | 435000.00 | 276000.00 | REWINDER TECHNO ELECTRICALS
11.00 | ITC of cubical Feeder Pillar box of size 0.6 Mtr Width x 0.3 Mtr Depth x 0.45 Mtr as per site requirement. | 30.00 | Nos |  | 500.00 | 15000.00 | 600.00 | 18000.00 | 15000.00 | REWINDER TECHNO ELECTRICALS
12.00 | Supply and pouring of VG-30 Bitumen conforming to IS: 73-2013 after suitable heating. It will be poured on Kerf of Runway/Taxiway for finishing rough surface, reducing water damage etc. | 500.00 | Mtr. |  | 120.00 | 60000.00 | 65.00 | 32500.00 | 32500.00 | Vardhman Airport Solutions Limited
13.00 | Cutting kerf of suitable size i/c chipping, hammering, cleaning & drying etc. & refilling the kerf with sealant material etc, as reqd. & laying upto 02 Nos of secondary leads. | 2000.00 | Mtr. |  | 400.00 | 800000.00 | 325.00 | 650000.00 | 650000.00 | Vardhman Airport Solutions Limited
14.00 | Cutting kerf of suitable size i/c chipping, hammering, cleaning & drying etc. & refilling the kerf with sealant material etc, as reqd. & laying 3 - 4 Nos of secondary leads. | 500.00 | Mtr. |  | 450.00 | 225000.00 | 420.00 | 210000.00 | 210000.00 | Vardhman Airport Solutions Limited
15.00 | Making holes in existing Housing boxes on site for entry of 40/50 mm dia HDPE/GI pipe as per direction & satisfaction of Engineer –in-charge. | 500.00 | Nos. |  | 200.00 | 100000.00 | 180.00 | 90000.00 | 90000.00 | Vardhman Airport Solutions Limited
16.00 | Supply of elevated type Omni-directional Blue, medium intensity LED type Taxiway Edge Light fittings suitable for Taxiway, for operation at 6.6 Amps, series circuit supply, complete with Omni-directional, Lens clamping mechanism, breakable coupling, gasket, two pin secondary leads, base plate with 06 Nos, M-10 stainless steel bolts and other accessories including White/blue LED with an integrated encapsulated electronic module complete as required conforming to latest ICAO Annex-14 requirement and as specified in Aerodrome Design Manual, Part 4 (Visual Aids) latest Edition. (AMA Make and equivalent) | 30.00 | Nos |  | 6000.00 | 180000.00 | 4500.00 | 135000.00 | 135000.00 | Vardhman Airport Solutions Limited
17.00 | Supply of Bi-directional elevated type high intensity Runway Edge Light Fitting suitable for use with 150 watt 6.6A halogen lamp complete with all accessories including lamp, lenses & clear-clear (20 nos) /Amber-clear (10 Nos) filters, two pin secondary lead plug suitable for connection with isolating transformer, breakable coupling, gasket and Base Plate with 06 nos of ss bolts, spring & plain washers & other accessories etc. as per site requirement complete as required & as specified. (AMA Make and equivalent) | 30.00 | Nos |  | 7500.00 | 225000.00 | 9000.00 | 270000.00 | 225000.00 | REWINDER TECHNO ELECTRICALS
18.00 | Calibration of Clinometer (for measurement of PAPI alignment) by Govt Approved Lab | 2.00 | Nos |  | 5000.00 | 10000.00 | 8500.00 | 17000.00 | 10000.00 | REWINDER TECHNO ELECTRICALS
19.00 | Calibration of Alignment tool (for measurement of Approach Light alignment) by Govt Approved Lab | 1.00 | Nos |  | 2000.00 | 2000.00 | 8500.00 | 8500.00 | 2000.00 | REWINDER TECHNO ELECTRICALS
20.00 | Calibration of Lux Meter by Govt Approved Lab | 2.00 | Nos. |  | 1000.00 | 2000.00 | 8500.00 | 17000.00 | 2000.00 | REWINDER TECHNO ELECTRICALS
21.00 | SITC of frangible Pole (60 mm dia, 03 mtr. Height) of suitable material with suitable coupler to fix simple approach light. | 13.00 | Nos. |  | 8000.00 | 104000.00 | 8500.00 | 110500.00 | 104000.00 | REWINDER TECHNO ELECTRICALS
22.00 | Providing 02 Nos of Engineers/Supervisor having minimum qualification Diploma Engineering with minimum two year experience or B Tech in relevent feild to assist and supervision of operation area project works as per direction and satisfaction of EIC. | 8.00 | Month |  | 60000.00 | 480000.00 | 70000.00 | 560000.00 | 480000.00 | REWINDER TECHNO ELECTRICALS
23.00 | Repair and maintenance work for the above BOQ Items by providing minimum No of manpower comprising one (01) Skilled, one (01) Semi-Skilled, and one (01) Unskilled Manpower. | 8.00 | Month |  | 66000.00 | 528000.00 | 75000.00 | 600000.00 | 528000.00 | REWINDER TECHNO ELECTRICALS
24.00 | Note: 1. Rate quoted shall be inclusive of any taxes, duties, Cess, fee, royalty charges etc. levied under any statute but exclusive of GST. Goods & Services Tax (GST) shall be paid to the contractor for any taxable supply/ services/works against a valid tax invoice as per terms and conditions of the contract.
| Total in Figures |  |  |  |  | 11673500.00 |  | 13685500.00
Lowest Amount Quoted BY: REWINDER TECHNO ELECTRICALS(11673500.00)

## BOQ Summary
BOQ Summary Details Tender Title: Miscellaneous Work Repair work of existing Kerfs filling for Secondary cable and other works in Operational Area at SGRDJ International Airport Amritsar. Tender ID: 2026_AAI_273334_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | REWINDER TECHNO ELECTRICALS (BID ID -1011368) | 11673500.00 | L1
| 2 | Vardhman Airport Solutions Limited (BID ID -1010805) | 13685500.00 | L2