## BoQ1
Government eProcurement System Created By: Abhijeet Sinha Created Date/Time: 13-May-2026 05:53 PM Tender Title: Augmentation of Air conditioning system in CTX room by provision of Ductable split unit at MBB airport, Agartala. Tender ID: 2026_AAI_274084_1
Tender Inviting Authority: Sr. Manager (Engg. - Elect.), Airports Authority of India, M.B.B. Airport, Agartala.
Name of Work: Augmentation of Air conditioning system in CTX room by provision of Ductable split unit at MBB airport, Agartala.
Contract No: 2026_AAI_274084_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Voltas Limited (GSTN-19AAACV2809D1ZJ) BID ID -1013757 |  | R.S. COOLING AND ELECTRICAL SERVICE (GSTN-NA) BID ID -1016019
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC Work
2.00 | Supply, Installation, Testing & Commissioning of cubicle type panel made out of 2 mm thick CRCA sheet, totally enclosed, IP 42 (minimum), modular type, floor mounted with channel base frame, dust and vermin proof, indoor, compartmentalized and suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system with extendable busbars on both sides, including control wiring with 2.5 sq mm size FRLS wires/cable, interconnection, protections duly powder coated painting etc. having following switchgears, metering instruments and accessories as per specifications and provision for Top or Bottom Entry as approved by Engineer-in-Charge. INCOMER: 4 (Four) pole Moulded Case Circuit Breaker (50 kA), 315 Amp with built in microprocessor based release unit with adjustable setting for O/L, S/C and inbuilt E/F protection complete with spreader, extended rotary handle as required - 1 Set. Digital dual source Class 1 multifunction meter with RS 485 Port i/c suitable CTs & PTs for 3 phase, 4 wire operation complete as required - 1 Set. Indicating lamps for ON/OFF/TRIP complete as required - 3 Nos. Indicating lamps for R/Y/B indication complete as required - 3 Nos. Aux Contacts, Controls, MCBs (SP/DP), protection relays etc. complete as required - 1 Lot. BUSBARS: High conductivity electrolytic quality aluminium alloy Bus Bars. OUTGOING: 4 (Four) pole Moulded Case Circuit Breaker 100 Amp (25 kA), with adjustable setting for O/L, S/C fault complete with spreader, extended rotary handle as required - 2 Set. 4 (Four) pole Moulded Case Circuit Breaker 63 Amp (25 kA), with adjustable setting for O/L, S/C fault complete with spreader, extended rotary handle as required - 4 Set. Class 1.0 Digital Ammeter with Selector switch - 6 Sets Class 1.0 Digital Voltmeter (range 0 - 500V) with Selector switch - 6 Sets Indicating lamps for ON/OFF/TRIP complete as required - 18 Nos. Aux Contacts, Controls, MCBs (SP/DP), CTs & PTs, protection relays etc. complete as required - 1 Lot. Others: Empty compartment as spare for future load addition in the Panel - 2 Nos. Side Cable alley to be considered for Entry of Cables. Note: 1. All breaking capacities shall be ICU=ICS. 2. Any other component not specifically mentioned but are required for the safe & reliable operation of panel shall be deemed to be inclusive in the item. Nothing extra on any account shall be paid in this item. 3. Control wiring should be with minimum 2.5 sq mm size FRLS wires/cable. | 1.00 | Each | 1.00 | 412437.00 | 412437.00 | 435000.00 | 435000.00 | 412437.00 | Voltas Limited
3.00 | Supply, Installation, testing and commissioning of ceiling suspended air cooled inverter type Ductable split unit of capacity 8.5 TR suitable for operation on R 32/R-410A /R-407 Green refrigerant with micro-processor based control, high efficiency Scroll type compressor hermetically sealed complete with automatic capacity, safety switches, lubrication system, air cooled condenser with axial type condenser fan suitable to work on 400V +/- 10%, 3 Phase, 50Hz AC power supply and BMS compatible complete hanging supports, base channel, vibration pad etc. complete as required as per the attached SCC & as per the direction of Engineer-in-Charge. | 3.00 | Nos | 1.00 | 193513.00 | 580539.00 | 168000.00 | 504000.00 | 504000.00 | R.S. COOLING AND ELECTRICAL SERVICE
4.00 | Supply & filling of Green Refrigerant (R 32/R-410A /R-407 or equivalent) for AC units complete as required as per the Direction of Engineer-in-Charge. | 30.00 | Kg | 1.00 | 1251.00 | 37530.00 | 1200.00 | 36000.00 | 36000.00 | R.S. COOLING AND ELECTRICAL SERVICE
5.00 | Supply, Installation, testing and commissioning including vaccumiazation and Nitrogen testing of following nominal sizes of soft/hard drawn copper refrigerant piping complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XLPE Class-O tubular insulation/with Class-O closed cell elastometric nitrile rubber tubular sleeves sections of 19 mm thick insulation as given below for Suction and Liquid lines, all accessories as per specifications etc. as required : 15.86 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm | 45.00 | Meter | 1.00 | 1491.00 | 67095.00 | 900.00 | 40500.00 | 40500.00 | R.S. COOLING AND ELECTRICAL SERVICE
6.00 | Supply, Installation, testing and commissioning including vaccumiazation and Nitrogen testing of following nominal sizes of soft/hard drawn copper refrigerant piping complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XLPE Class-O tubular insulation/with Class-O closed cell elastometric nitrile rubber tubular sleeves sections of 19 mm thick insulation as given below for Suction and Liquid lines, all accessories as per specifications etc. as required : 28.58 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm | 45.00 | Meter | 1.00 | 2498.00 | 112410.00 | 1800.00 | 81000.00 | 81000.00 | R.S. COOLING AND ELECTRICAL SERVICE
7.00 | Supply and laying of 25 mm dia PVC condensate pipe for drain water piping with 9 mm thick (Class "O") closed cell Elastomeric Nitrile Rubber Insulation i/c providing necessary joints and supports complete as required as per the Direction of Engineer-in-Charge. | 50.00 | Meter | 2.00 | 267.00 | 13350.00 | 220.00 | 11000.00 | 11000.00 | R.S. COOLING AND ELECTRICAL SERVICE
8.00 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required as per the Direction of Engineer-in-Charge. 0.80 mm | 10.00 | Sqm | 1.00 | 1328.00 | 13280.00 | 2100.00 | 21000.00 | 13280.00 | Voltas Limited
9.00 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required as per the Direction of Engineer-in-Charge. 0.63 mm | 150.00 | Sqm | 1.00 | 1111.00 | 166650.00 | 1800.00 | 270000.00 | 166650.00 | Voltas Limited
10.00 | Providing and fixing fire retardant nonporous double layer flexible canvas connection for ductable split ACs as per site complete etc. as per direction and complete satisfaction of EIC. | 6.00 | Jobs | 1.00 | 3335.00 | 20010.00 | 1500.00 | 9000.00 | 9000.00 | R.S. COOLING AND ELECTRICAL SERVICE
11.00 | Supply and fixing of Galvanised iron backdraft/gravity damper complete as required as per the direction of Engineer-in-Charge. | 1.00 | Sqm | 1.00 | 19172.00 | 19172.00 | 10800.00 | 10800.00 | 10800.00 | R.S. COOLING AND ELECTRICAL SERVICE
12.00 | Supplying, fixing testing commissioning of supply air diffusers of powder coated aluminium with aluminium volume control dampers with anti smudge ring & removable core as per the Direction of Engineer-in-Charge. | 3.00 | Sqm | 1.00 | 32925.00 | 98775.00 | 19500.00 | 58500.00 | 58500.00 | R.S. COOLING AND ELECTRICAL SERVICE
13.00 | Supplying, fixing, testing commissioning of Return air diffusers of powder coated aluminium without volume control dampers with anti smudge ring & removable core as per the Direction of Engineer-in-Charge.. | 3.00 | Sqm | 1.00 | 21673.00 | 65019.00 | 17500.00 | 52500.00 | 52500.00 | R.S. COOLING AND ELECTRICAL SERVICE
14.00 | Supply and fixing of 10 mm thick open cell nitrile rubber for acoustic insulation complete as required as per the direction of Engineer-in-Charge. | 15.00 | Sqm | 1.00 | 1191.00 | 17865.00 | 825.00 | 12375.00 | 12375.00 | R.S. COOLING AND ELECTRICAL SERVICE
15.00 | Supplying and fixing of 13 mm thick closed cell Nitrile rubber (Class “O”) for thermal insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required. | 150.00 | Sqm | 1.00 | 646.00 | 96900.00 | 569.00 | 85350.00 | 85350.00 | R.S. COOLING AND ELECTRICAL SERVICE
16.00 | Supply of XLPE Insulated, Cores Laid Up, PVC Inner sheathed, Strip Armoured, Extruded PVC Type ST2 Outer Sheathed, 1100V Grade Aluminium Conductor cable of size 3.5 core X 150 Sq mm as per IS 7098 (Part 1) 1988 with upto date Amendments complete etc. as required. | 100.00 | Meter | 1.00 | 1269.00 | 126900.00 | 1020.00 | 102000.00 | 102000.00 | R.S. COOLING AND ELECTRICAL SERVICE
17.00 | Supply of XLPE Insulated, Cores Laid Up, PVC Inner sheathed, Strip Armoured, Extruded PVC Type ST2 Outer Sheathed, 1100V Grade Copper Conductor cable of size 4 core X 16 Sq mm as per IS 7098 (Part 1) 1988 with upto date Amendments complete etc. as required. | 300.00 | Meter | 1.00 | 1388.00 | 416400.00 | 1165.00 | 349500.00 | 349500.00 | R.S. COOLING AND ELECTRICAL SERVICE
18.00 | Supply of XLPE Insulated, Cores Laid Up, PVC Inner sheathed, Unarmoured, Extruded PVC Type ST2 Outer Sheathed, 1100V Grade Copper Conductor cable of size 3 core X 1.5 Sq mm as per IS 7098 (Part 1) 1988 with upto date amendments complete etc. as required. | 300.00 | Meter | 1.00 | 144.00 | 43200.00 | 220.00 | 66000.00 | 43200.00 | Voltas Limited
19.00 | Supply of control cum transmission wiring with FRLS PVC insulated Copper conductor of 6 core x 2.5 sq. mm including making termination for interconnection of indoor and outdoor units as per direction and complete satisfaction of EIC. | 50.00 | Meter | 1.00 | 397.00 | 19850.00 | 420.00 | 21000.00 | 19850.00 | Voltas Limited
20.00 | Supplying and installing perforated painted with powder coating M.S. cable trays of size 300 mm width X 50 mm depth X 1.6 mm thickness with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. | 100.00 | Meter | 1.00 | 1176.00 | 117600.00 | 850.00 | 85000.00 | 85000.00 | R.S. COOLING AND ELECTRICAL SERVICE
21.00 | Supplying and installing perforated painted with powder coating M.S. cable trays of size 150 mm width X 50 mm depth X 1.6 mm thickness with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. | 50.00 | Meter | 1.00 | 867.00 | 43350.00 | 550.00 | 27500.00 | 27500.00 | R.S. COOLING AND ELECTRICAL SERVICE
22.00 | Supplying and installing perforated painted with powder coating M.S. cable trays of size 100 mm width X 50 mm depth X 1.6 mm thickness with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. | 30.00 | Meter | 1.00 | 726.00 | 21780.00 | 370.00 | 11100.00 | 11100.00 | R.S. COOLING AND ELECTRICAL SERVICE
23.00 | Supplying and installing perforated painted with powder coating M.S. cable trays bends of size 300 mm width X 50 mm depth X 1.6 mm thickness with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. | 10.00 | Each | 1.00 | 4935.00 | 49350.00 | 1050.00 | 10500.00 | 10500.00 | R.S. COOLING AND ELECTRICAL SERVICE
24.00 | Supplying and installing perforated painted with powder coating M.S. cable trays bends of size 150 mm width X 50 mm depth X 1.6 mm thickness with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. | 2.00 | Each | 1.00 | 4118.00 | 8236.00 | 850.00 | 1700.00 | 1700.00 | R.S. COOLING AND ELECTRICAL SERVICE
25.00 | Supplying and installing perforated painted with powder coating M.S. cable trays Tees of size 300 mm width X 50 mm depth X 1.6 mm thickness with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. | 10.00 | Each | 1.00 | 5785.00 | 57850.00 | 1250.00 | 12500.00 | 12500.00 | R.S. COOLING AND ELECTRICAL SERVICE
26.00 | Supplying and installing perforated painted with powder coating M.S. cable trays Tee of size 150 mm width X 50 mm depth X 1.6 mm thickness with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. | 1.00 | Each | 1.00 | 4963.00 | 4963.00 | 850.00 | 850.00 | 850.00 | R.S. COOLING AND ELECTRICAL SERVICE
27.00 | Supplying and installing perforated painted with powder coating M.S. cable trays Reducer of size 300 mm width X 50 mm depth X 1.6 mm thickness with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. | 1.00 | Each | 1.00 | 7336.00 | 7336.00 | 1550.00 | 1550.00 | 1550.00 | R.S. COOLING AND ELECTRICAL SERVICE
28.00 | Supplying and installing perforated painted with powder coating M.S. cable trays Reducer of size 150 mm width X 50 mm depth X 1.6 mm thickness with perforation not more than 17.5%, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required. | 2.00 | Each | 1.00 | 6335.00 | 12670.00 | 1250.00 | 2500.00 | 2500.00 | R.S. COOLING AND ELECTRICAL SERVICE
29.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size Upto 35 Sq. mm on wall surface (clamped with 1 mm thick saddle) as required. | 50.00 | Meter | 1.00 | 84.00 | 4200.00 | 90.00 | 4500.00 | 4200.00 | Voltas Limited
30.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size Upto 35 Sq. mm on cable tray (clamped with 1mm thick saddle) as required. | 400.00 | Meter | 1.00 | 84.00 | 33600.00 | 120.00 | 48000.00 | 33600.00 | Voltas Limited
31.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size Above 95 sq. mm and upto 185 sq. mm on wall surface (clamped with 25/40x3mm MS flat clamp) as required. | 40.00 | Meter | 1.00 | 117.00 | 4680.00 | 150.00 | 6000.00 | 4680.00 | Voltas Limited
32.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of size Above 95 sq. mm and upto 185 sq. mm on cable tray (clamped with 25/40x3mm MS flat clamp) as required. | 60.00 | Meter | 1.00 | 117.00 | 7020.00 | 180.00 | 10800.00 | 7020.00 | Voltas Limited
33.00 | Supplying and making end termination with brass compression gland and aluminium lugs for size 3.5 X 150 Sq. mm of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV as required. | 2.00 | set | 1.00 | 1519.00 | 3038.00 | 2950.00 | 5900.00 | 3038.00 | Voltas Limited
34.00 | Supplying and making end termination with brass compression gland and Copper Lugs for size 4 X 16 sq. mm of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 6.00 | set | 1.00 | 1334.00 | 8004.00 | 1050.00 | 6300.00 | 6300.00 | R.S. COOLING AND ELECTRICAL SERVICE
35.00 | Supply and laying of 6 SWG earthing wire on surface/recessed conduit/submain wiring/cable/pipes etc. i/c termination as required as per the direction of engineer-in-charge. | 80.00 | Meter | 1.00 | 59.00 | 4720.00 | 90.00 | 7200.00 | 4720.00 | Voltas Limited
36.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface/recess etc. i/c termination as required as per the direction of engineer-in-charge. | 200.00 | Meter | 1.00 | 217.00 | 43400.00 | 300.00 | 60000.00 | 43400.00 | Voltas Limited
37.00 | Supply & fixing of of 63 Amp, 415 V, 10 kA, "C" curve, Four Pole (FP) Miniature Circuit Breaker (MCB) alongwith metal enclosure complete with fixing on surface, making connections, testing & commissioning as required. | 5.00 | Nos | 1.00 | 4743.00 | 23715.00 | 6500.00 | 32500.00 | 23715.00 | Voltas Limited
38.00 | AICMC Work
39.00 | All Inclusive Comprehensive Maintenance Contract for above 03 nos. Ductable units provided at MBB Airport, Agartala comprising of periodical, preventive, break down maintenance as per the OEM recommendations & AAI requirements and attending emergency services as and when required on 24 hrs. basis and including all necessary spares and consumables to keep the equipments in perfect working condition complete as required and as specified. 1st Year Post DLP | 12.00 | Months | 1.00 | 4250.00 | 51000.00 | 4335.00 | 52020.00 | 51000.00 | Voltas Limited
40.00 | All Inclusive Comprehensive Maintenance Contract for above 03 nos. Ductable units provided at MBB Airport, Agartala comprising of periodical, preventive, break down maintenance as per the OEM recommendations & AAI requirements and attending emergency services as and when required on 24 hrs. basis and including all necessary spares and consumables to keep the equipments in perfect working condition complete as required and as specified. 2nd Year Post DLP | 12.00 | Months | 1.00 | 4463.00 | 53556.00 | 5202.00 | 62424.00 | 53556.00 | Voltas Limited
| Total in Figures |  |  |  |  | 2887450.00 |  | 2614369.00
Lowest Amount Quoted BY: R.S. COOLING AND ELECTRICAL SERVICE(2614369.00)

## BOQ Summary
BOQ Summary Details Tender Title: Augmentation of Air conditioning system in CTX room by provision of Ductable split unit at MBB airport, Agartala. Tender ID: 2026_AAI_274084_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | R.S. COOLING AND ELECTRICAL SERVICE (BID ID -1016019) | 2614369.00 | L1
| 2 | Voltas Limited (BID ID -1013757) | 2887450.00 | L2