## BoQ1
Government eProcurement System Created By: SURAJ E Created Date/Time: 06-May-2026 10:30 AM Tender Title: SITC of CCRs at Trichy International Airport Tender ID: 2026_AAI_274126_1
Tender Inviting Authority: Senior Manager (Engg-E). Airports Authority of India, Trichy Airport, Trichy- 620 007
Name of Work: SITC of CCRs at Trichy International Airport
Contract No: 2026_AAI_274126_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | NASU SYSTEMS (GSTN-27ABAPS2566G1ZK) BID ID -1008999 |  | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -1015972
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of 7.5 kW CCR with 4KW tapping capacity Indoor Type Air Cooled Constant Current Regulator (CCR) of Micro Processor Controlled, Thyristor Type suitable for operation on single phase 230V / 2-phase 400V AC + PE ± 10%, 50 Hz input AC supply with 5 steps variation of current output (2.8, 3.4, 4.0, 5.2 and 6.6 Amp) and able to communicate with PC or PLC controlled system with digital output ammeter (0-10 Amps), over current, over voltage, open circuit and earth fault protection and earth leakage meter, two stage earth leakage detector, positive back indication equipments, hours run counter, LCD display, local and remote control complete as required and confirm to specifications enclosed and integration with existing Airfield Lighting Control and Monitoring System (ALCMS) along with providing PLC I/O module, relay modules, connectors, modifications of graphics interface etc, as required. (Make: As per AAI list of approved makes) | 4.00 | Each |  | 339300.00 | 1357200.00 | 355000.00 | 1420000.00 | 1357200.00 | NASU SYSTEMS
| Total in Figures |  |  |  |  | 1357200.00 |  | 1420000.00
Lowest Amount Quoted BY: NASU SYSTEMS(1357200.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of CCRs at Trichy International Airport Tender ID: 2026_AAI_274126_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | NASU SYSTEMS (BID ID -1008999) | 1357200.00 | L1
| 2 | Manish Electricals (BID ID -1015972) | 1420000.00 | L2