## BoQ1
Government eProcurement System Created By: KASI R Created Date/Time: 02-Jun-2026 05:29 PM Tender Title: SITC of 350TR Cooling tower in place of old and worn out cooling towers of HVAC plant at Madurai Airport. SH Replacement of 02 nos. cooling towers, pumps, starters, VFD etc. Phase II. Tender ID: 2026_AAI_274982_1
Tender Inviting Authority: AIRPORTS AUTHORITY OF INDIA
Name of Work: SITC of 350TR cooling tower in place of old and worn out cooling towers of HVAC plant at Madurai Airport. SH: Replacement of 02 nos. cooling towers, pumps, starters, VFD etc. - Phase II.
Contract No: AAI/MDU/E-E/MDU-479/NIT-01/2026-27 Tender ID No.2026_AAI_274982_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Bluestar Limited (GSTN-NA) BID ID -1018379 |  | Shinryo Suvidha Engineers India Pvt Ltd (GSTN-NA) BID ID -1016547
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Cooling Tower SITC of FRP INDUCED DRAFT COOLING TOWERS for air conditioning system. Each tower shall be complete with basin, casing, distribution system, filling, louvers,HDG supporters, SS nut bolts, GI / aluminium ladder, fan and motor including modification of PCC / RCC foundation as required. Efficiency of Motor (class IE3) as per IS 12615. Motor shall be suitable for 415±10% volts, 50 cycles, 3 phase power supply, Isolator panel with MCCB and emergency poweroff push button (EPO) at cooling tower and earthing, shall also be included. Tower for airconditioning system shall be selected on the basis of ambient wet bulb 25.56 deg C. The cooling tower shall be CTI certified. The cooling tower shall be IP 55 and VFD / VSD controled. Cooling tower suitable for minimum 330 TR Screw chillers having flow rate of 865.43 USGPM, inlet temperature of 35 deg C and outlet temperature of 30 deg C having heat rejection capacity minimum 20 % extra against 330 TR chiller. (Colour of cooling tower shall be as per AAI approval.) Note: Range shall be 4.2 deg C and wet bulb approach shall be 2.77 deg C Existing concrete basement size - 4.75 mtr X 4.70 mtr, cooling tower sizes to be matched with the same. | 2.00 | Job |  | 887735.00 | 1775470.00 | 1188983.00 | 2377966.00 | 1775470.00 | Bluestar Limited
2.00 | Condenser Pump variable Speed Supply, installation, testing and commissioning of CENTRIFUGAL END-SUCTION PUMP water pump sets factory mounted on a common base with anti-vibration pads, with electric motor for recirculation of water for the central air-conditioning system. All pumps shall be aligned. The pump motor TEFC (IE3) or better shall be suitable for 415±10% V, 50 cycles, 3 phase power supply and Class F insulation. Minimum pump efficiency shall be 90%. The qouted rates for Condenser pumps shall be inclusive of PCC / RCC foundation wherever is required. Pump performance characteristics shall be as follows as per specifications. Condenser water Pumps - Variable speed Water flow rate : 1078.70 USGPM Head : 25 Mtr | 4.00 | Job |  | 442005.00 | 1768020.00 | 481060.00 | 1924240.00 | 1768020.00 | Bluestar Limited
3.00 | Supply, Installation, Testing & Commissioning of condenser water pipes of following sizes of MS 'C' class along with necessary clamps, vibration isolators and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted etc. as per specification and as required complete in all respect. a) 400mm dia Note:-The Pipes size 150mm & below shall be M.S. 'C' class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above. | 125.00 | Mtr |  | 11945.00 | 1493125.00 | 9978.00 | 1247250.00 | 1247250.00 | Shinryo Suvidha Engineers India Pvt Ltd
4.00 | Supply, Installation, Testing & Commissioning of condenser water pipes of following sizes of MS 'C' class along with necessary clamps, vibration isolators and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted etc. as per specification and as required complete in all respect. c)250mm dia Note:-The Pipes size 150mm & below shall be M.S. 'C' class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above. | 120.00 | Mtr |  | 6575.00 | 789000.00 | 6349.00 | 761880.00 | 761880.00 | Shinryo Suvidha Engineers India Pvt Ltd
5.00 | Supply, Installation, Testing & Commissioning of condenser water pipes of following sizes of MS 'C' class along with necessary clamps, vibration isolators and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted etc. as per specification and as required complete in all respect. d) 200mm dia Note:-The Pipes size 150mm & below shall be M.S. 'C' class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above. | 30.00 | Mtr |  | 5290.00 | 158700.00 | 5149.00 | 154470.00 | 154470.00 | Shinryo Suvidha Engineers India Pvt Ltd
6.00 | Supply, Installation, Testing & Commissioning of condenser water pipes of following sizes of MS 'C' class along with necessary clamps, vibration isolators and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted etc. as per specification and as required complete in all respect. e) 150mm dia Note:-The Pipes size 150mm & below shall be M.S. 'C' class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above. | 24.00 | Mtr |  | 3565.00 | 85560.00 | 3166.00 | 75984.00 | 75984.00 | Shinryo Suvidha Engineers India Pvt Ltd
7.00 | Supply, Installation, Testing & Commissioning of condenser water pipes of following sizes of MS 'C' class along with necessary clamps, vibration isolators and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted etc. as per specification and as required complete in all respect. f) 100mm dia Note:-The Pipes size 150mm & below shall be M.S. 'C' class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above. | 24.00 | Mtr |  | 2385.00 | 57240.00 | 1850.00 | 44400.00 | 44400.00 | Shinryo Suvidha Engineers India Pvt Ltd
8.00 | Supply, Installation, Testing & Commissioning of condenser water pipes of following sizes of MS 'C' class along with necessary clamps, vibration isolators and fittings such as bends, tees etc. but excluding valves, strainers, gauges etc. adequately supported on rigid supports duly painted etc. as per specification and as required complete in all respect. g)50mm dia Note:-The Pipes size 150mm & below shall be M.S. 'C' class as per IS : 1239 and pipes size above 150mm shall be welded black steel pipe heavy class as per IS: 3589, from minimum 6.35mm thick M.S. Sheet for pipes upto 350 mm dia. And from minimum 7mm thick MS sheet for pipes of 400 mm dia and above. | 30.00 | Mtr |  | 1080.00 | 32400.00 | 840.00 | 25200.00 | 25200.00 | Shinryo Suvidha Engineers India Pvt Ltd
9.00 | Supply, Installiing, Testing & Commissioning of M.S. Pot strainer with SS Strainer 400 mm (PN 16) complete with all necessary accessories etc. as required. | 1.00 | Job |  | 136985.00 | 136985.00 | 304898.00 | 304898.00 | 136985.00 | Bluestar Limited
10.00 | Supply, Installiing, Testing & Commissioning of Y-Strainer with SS Strainer 250 mm (PN 16) complete with all necessary accessories etc. as required as per specification. | 4.00 | Job |  | 38285.00 | 153140.00 | 73712.00 | 294848.00 | 153140.00 | Bluestar Limited
11.00 | Providing and fixing in position the following CI Butterfly valves for cooling tower water line cut to required lengths and installed with all welded joints with flanges & support etc. as required complete as per technical specifications. a) 400 mm dia Gear Type valve. (PN 16) | 4.00 | Job |  | 48625.00 | 194500.00 | 56899.00 | 227596.00 | 194500.00 | Bluestar Limited
12.00 | Providing and fixing in position the following CI Butterfly valves for cooling tower water line cut to required lengths and installed with all welded joints with flanges & support etc. as required complete as per technical specifications. b) 250 mm dia valve (PN 16) | 12.00 | Job |  | 20025.00 | 240300.00 | 24675.00 | 296100.00 | 240300.00 | Bluestar Limited
13.00 | Providing and fixing in position the following CI Butterfly valves for cooling tower water line cut to required lengths and installed with all welded joints with flanges & support etc. as required complete as per technical specifications. c) 200 mm dia valve (PN 16) | 2.00 | Job |  | 14655.00 | 29310.00 | 17731.00 | 35462.00 | 29310.00 | Bluestar Limited
14.00 | Providing and fixing in position the following CI Butterfly valves for cooling tower water line cut to required lengths and installed with all welded joints with flanges & support etc. as required complete as per technical specifications. d) 150 mm dia valve (PN 16) | 2.00 | Job |  | 9770.00 | 19540.00 | 10009.00 | 20018.00 | 19540.00 | Bluestar Limited
15.00 | Providing and fixing in position the following CI Butterfly valves for cooling tower water line cut to required lengths and installed with all welded joints with flanges & support etc. as required complete as per technical specifications. e) 100 mm dia valve (PN 16) | 2.00 | Job |  | 5365.00 | 10730.00 | 6925.00 | 13850.00 | 10730.00 | Bluestar Limited
16.00 | Providing and fixing in position the following CI Non-Return valve for cooling tower water line cut to required lengths and installed with all welded joints with flanges & support etc. as required complete as per technical specifications. 250 mm dia valve (PN 16) | 4.00 | Job |  | 22745.00 | 90980.00 | 26952.00 | 107808.00 | 90980.00 | Bluestar Limited
17.00 | Supply, Installation, Testing and Commissioning of Variable Frequency Drive (VFD), capacity of 30kW/40HP, Three Phase, voltage range 380-480V, IP20 for the existing secondary pump installed at site, VFD shall be compatiable with existing BMS panel etc. complete as required as per technical specification & site requirement. | 4.00 | Job |  | 91150.00 | 364600.00 | 118846.00 | 475384.00 | 364600.00 | Bluestar Limited
18.00 | Supply, Installation, Testing and Commissioning of Variable Frequency Drive (VFD), capacity of 18.5kW/25HP, Three Phase, voltage range 380-480V, IP20 for the existing and proposed cooling towers, VFD shall be compatiable with existing BMS panel etc. complete as required as per technical specification & site requirement. | 4.00 | Job |  | 61200.00 | 244800.00 | 101816.00 | 407264.00 | 244800.00 | Bluestar Limited
19.00 | Supply, Installation, Testing and Commissioing of EC fan control panel having CRCA sheet IP 54 rating, 1no. of 4P, 63A, 36kA thermal magentic release type MCCB, 4 nos. of 4Pole 16A, 10kA MCB, minimum 4 nos. of 16A contactor/as per site requirement, minimum 3 nos. of 10A, 440V AC, 50Hz 4 position selector switch/as per site requirement, LED indication lamp for START and STOP position, suitable connectors, accessoires etc. suitable control wiring etc. complete as required as per site requirement. The panel should be easily integrated with existing BMS panel installed at Madurai Airport. | 14.00 | Job |  | 35910.00 | 502740.00 | 27664.00 | 387296.00 | 387296.00 | Shinryo Suvidha Engineers India Pvt Ltd
20.00 | Providing and fixing in position the industrial type pressure gauges (0-150 PSI) with gun metal / brass valves complete as required. | 8.00 | Job |  | 2635.00 | 21080.00 | 2201.00 | 17608.00 | 17608.00 | Shinryo Suvidha Engineers India Pvt Ltd
21.00 | Providing and fixing in position the industrial type pressure gauges (0-220 PSI) with gun metal / brass valves complete as required. | 8.00 | Job |  | 2635.00 | 21080.00 | 2201.00 | 17608.00 | 17608.00 | Shinryo Suvidha Engineers India Pvt Ltd
22.00 | Providing & fixing in position the mercury in glass industrial type thermometers. | 16.00 | Job |  | 2415.00 | 38640.00 | 2708.00 | 43328.00 | 38640.00 | Bluestar Limited
23.00 | Supply, installation testing and commissioning of Magnetic flow meter suitable for 2800M³/hr flow with preamplifier and microprocessor including necessary cabling, conduit, etc. complete as required as per site requirement. | 1.00 | Job |  | 397145.00 | 397145.00 | 355518.00 | 355518.00 | 355518.00 | Shinryo Suvidha Engineers India Pvt Ltd
24.00 | Providing & Laying of makeup tank pipeline with UPVC pipes of following size with all fittings and threaded adaptors, couplings, tests, bends, reducers, end caps, elbows etc. complete as required as per site requirement. 90mm Dia | 150.00 | Mtr |  | 600.00 | 90000.00 | 1641.00 | 246150.00 | 90000.00 | Bluestar Limited
25.00 | Supply of 3.5C X 35 Sq.mm XLPE insulated PVC sheathed, armoured Aluminium conductor power cable of 1.1 KV grade as per IS 7098 part I 1988 with upto date amendments etc complete as required. | 300.00 | Mtr |  | 400.00 | 120000.00 | 530.00 | 159000.00 | 120000.00 | Bluestar Limited
26.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on cable tray as required. Up to 35sq. mm (clamped with 1mm thick saddle) | 150.00 | Mtr |  | 160.00 | 24000.00 | 118.00 | 17700.00 | 17700.00 | Shinryo Suvidha Engineers India Pvt Ltd
27.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Up to 35sq. mm (clamped with 1mm thick saddle) | 20.00 | Mtr |  | 170.00 | 3400.00 | 118.00 | 2360.00 | 2360.00 | Shinryo Suvidha Engineers India Pvt Ltd
28.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Up to 35sq.mm | 100.00 | Mtr |  | 170.00 | 17000.00 | 118.00 | 11800.00 | 11800.00 | Shinryo Suvidha Engineers India Pvt Ltd
29.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5C X 35 Sq.mm | 8.00 | Set |  | 1130.00 | 9040.00 | 883.00 | 7064.00 | 7064.00 | Shinryo Suvidha Engineers India Pvt Ltd
30.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess or in cable tray for loop earthing as required. | 300.00 | Mtr |  | 95.00 | 28500.00 | 118.00 | 35400.00 | 28500.00 | Bluestar Limited
31.00 | Supply, Installation, Testing and commissioning of Twin lobe positive displacement type, rotary air blowers with V-belt drive, belt guard, base plate, inlet filter-silencer, flexible connectors, control valves, pressure gauge and piping for a capacity of 200CUM/Hr @ 6000MMWG at required pressure with 10 HP motor with pulley, suitable electrical control panel with under/over voltage protection, over current protection, phase failure protection, modification of existing pipe line along with suitable accessoires, providing suitable basement foundation to mount the blower etc. to supply sufficient air for the salt mixing process (saltwater desalination) at softner plant installed at Madurai Airport etc. complete as required as per site requirement and site conditions. | 2.00 | Job |  | 223905.00 | 447810.00 | 226613.00 | 453226.00 | 447810.00 | Bluestar Limited
32.00 | Providing and fixing in position the following CI Non-Return valve for cooling tower water line cut to required lengths and installed with all welded joints with flanges & support etc. as required complete as per technical specifications. 80 mm dia valve (PN 16) | 2.00 | Job |  | 4700.00 | 9400.00 | 4524.00 | 9048.00 | 9048.00 | Shinryo Suvidha Engineers India Pvt Ltd
33.00 | Providing corrugated G.S. sheet roofing including vertical / curved surface fixed with polymer coated J or L hooks, bolts and nuts 8 mm diameter with bitumen and G.I. limpet washers or with G.I. limpet washers filled with white lead, including a coat of approved steel primer and two coats of approved paint on overlapping of sheets complete (up to any pitch in horizontal/vertical or curved surfaces), excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required. 1.00 mm thick with zinc coating not less than 275 gm/m² | 16.00 | Sqm |  | 1585.00 | 25360.00 | 2119.00 | 33904.00 | 25360.00 | Bluestar Limited
34.00 | Supply, installation, balancing and commissioning of factory fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of 1.25 mm sheet thickness complete as required. | 50.00 | Sqm |  | 1955.00 | 97750.00 | 1722.00 | 86100.00 | 86100.00 | Shinryo Suvidha Engineers India Pvt Ltd
35.00 | Welding by gas or electric plant including transportation of plant at site etc. complete as required. | 500.00 | Cm |  | 175.00 | 87500.00 | 200.00 | 100000.00 | 87500.00 | Bluestar Limited
36.00 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge. In cement mortar | 20.00 | Cum |  | 1980.00 | 39600.00 | 10595.00 | 211900.00 | 39600.00 | Bluestar Limited
| Total in Figures |  |  |  |  | 9624445.00 |  | 10989628.00
Lowest Amount Quoted BY: Bluestar Limited(9624445.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of 350TR Cooling tower in place of old and worn out cooling towers of HVAC plant at Madurai Airport. SH Replacement of 02 nos. cooling towers, pumps, starters, VFD etc. Phase II. Tender ID: 2026_AAI_274982_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Bluestar Limited (BID ID -1018379) | 9624445.00 | L1
| 2 | Shinryo Suvidha Engineers India Pvt Ltd (BID ID -1016547) | 10989628.00 | L2