## BoQ1
Government eProcurement System Created By: UMESH CHAURASIA Created Date/Time: 01-Jun-2026 05:00 PM Tender Title: Development of Solapur Airport. SH Provision of power supply to watch tower and provision of Additional standby feeder for PAPI units Tender ID: 2026_AAI_274999_1
Tender Inviting Authority: Asst. Gen. Manager (Engg-Elect), AAI RHQ, WR, Mumbai
Name of Work: Development of Solapur airport SH: Provision of power supply to watch tower and provision of Additional standby feeder for PAPI units
Contract No:
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -1019988 |  | Shiva Enterprises (GSTN-NA) BID ID -1019979 |  | Variant Infratech Private Limited (GSTN-NA) BID ID -1019973
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, manufacture and Supply of indoor compartmentalized type LT panel 36 kA short circuit breaking capacity panel of suitable size bus bars with SMC/DMC supports made of 2mm CRCA sheet totally enclosed,IP-42,free standing floor/ wall mounting,powder coated painting suitable to operation on 3 phase and neutral,415V,50Hz AC system with bus bars G.I flat Earth strip on both sides, Removeable gland plates at bottom with suitable size of predrilled holes for cabels,cable interconnections,wiring earthing,rotary handles & spreader links to all MCCBs,powder coated painting etc,with following items and installation on suitable channels / elevated concrete foundation as per site requirement/directions of E-I-C. INCOMER (a) 200 A, 4P MCCB, Microprocessor based release (lcs = Icu = 36kA) with inbuilt O/L , S/C & E/F protection, shunt trip, auxiliary contacts - 2 Nos (b) R, Y, B phase indicating LED lamps with 2 amp back up MCB - 2 Set (c) Digital Mulit functional meter suitable range for 3 phase 4 wire with LED display and selector switch along with MCB of suitable ratings - 02 sets for 3 phase 4 wire with LED display and selector switch and cast resin CT ratio progragmmable and auto ranging along with 3 numbers of class 1.0,15VA suitable range CTs-02 Sets. (d) ON, OFF, TRIP Indicating LED Lamps With 2 Amp MCB - 2 Set MANUAL CHANGE OVER SWITCH One set of four pole 200 Amps, 36 KA capacity BUSBAR One set of 400 Amps TPN Aluminium Busbar of 36 KA capacity OUTGOING a) 63 A, 4P MCCB with built in Microprocessor based release with adjustable thermal setting (lcs = Icu =36 KA) - 01 Nos. (b) 100 A, 4P MCCB with built in Microprocessor based release with adjustable thermal setting (lcs = Icu =36 KA) - 03 Nos. | 1.00 | job | 1.25 | 375000.00 | 375000.00 | 300000.00 | 300000.00 | 316250.00 | 316250.00 | 300000.00 | Shiva Enterprises
2.00 | Design, manufacture and supplyof outdoor compartmentalized type feeder pillar 36 kA short circuit breaking capacity panel of suitable size bus bars with SMC/DMC supports made of 2mm CRCA sheet totally enclosed,IP-65,free standing floor/ wall mounting,powder coated painting suitable to the existing space,operation on 3 phase and neutral,415V,50Hz AC system with bus bars G.I flat Earth strip on both sides, Removeable gland plates at bottom with suitable size of predrilled holes for cabels,cable interconnections,wiring earthing,rotary handles & spreader links to all MCCBs,powder coated painting etc,with following items and installation on suitable channels / elevated concrete foundation as per site requirement/directions of E-I-C. INCOMER (a) 100 A, 4P MCCB, Microprocessor based release (lcs = Icu = 36kA) with inbuilt O/L , S/C & E/F protection, shunt trip, auxiliary contacts - 2 Nos (b) R, Y, B phase indicating LED lamps with 2 amp back up MCB - 2 Set (c) Digital Mulit functional meter suitable range for 3 phase 4 wire with LED display and selector switch along with MCB of suitable ratings - 01 sets for 3 phase 4 wire with LED display and selector switch and cast resin CT ratio progragmmable and auto ranging along with 3 numbers of class 1.0,15VA suitable range CTs-02 Sets. (d) ON, OFF, TRIP Indicating LED Lamps With 2 Amp MCB - 2 Set BUSBAR One set of 200 Amps TPN Aluminium Busbar of 36 KA capacity OUTGOING . (a) 32Amps, 4P power contractor with 230 volts 50 HZ contrctor coil connected through 24 hour timer for perimeter lighting - 01 set. b) 01 no. 6 way horizontal TPN DB consisist of 03 no.10 Amps TPN MCB, 01 no. 6 Amps SPN MCB, | 7.00 | job | 0.00 | 220000.00 | 1540000.00 | 107000.00 | 749000.00 | 74750.00 | 523250.00 | 523250.00 | Variant Infratech Private Limited
3.00 | Installation Testing and commissioning of Indoor type LT panel on existing cable trench by provinfing suitable MS channels/Angles including cutting, welding, grinding and painting as per site requirement / directions of E-I-C. | 1.00 | job | 100.00 | 5000.00 | 5000.00 | 8500.00 | 8500.00 | 5750.00 | 5750.00 | 5000.00 | Awasthi Electric Works
4.00 | installation,testing and commisioning of outdoor type feederpillar by provinfing suitable MS channels/Angles including cutting, welding, grinding and painting / elevated concrete foundation as per site requirement/directions of E-I-C. | 7.00 | job | 53.00 | 3000.00 | 21000.00 | 6500.00 | 45500.00 | 5750.00 | 40250.00 | 21000.00 | Awasthi Electric Works
5.00 | Supply of following size of XLPE insulated & PVC sheathed, armoured, aluminium conductor under ground cable of 1.1KV grade as per IS 7098:1988 Part-I with upto date amendments complete as required. 2C x 6 Sq.mm | 150.00 | Meter | 10.00 | 99.00 | 14850.00 | 80.00 | 12000.00 | 405.00 | 60750.00 | 12000.00 | Shiva Enterprises
6.00 | Supply of following size of XLPE insulated & PVC sheathed, armoured, aluminium conductor under ground cable of 1.1KV grade as per IS 7098:1988 Part-I with upto date amendments complete as required. 3.5C x 95 Sq.mm | 7000.00 | Meter | 11.00 | 645.00 | 4515000.00 | 570.00 | 3990000.00 | 598.00 | 4186000.00 | 3990000.00 | Shiva Enterprises
7.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC-HDPE pipe as required Above 35 sq. mm and upto 95 sq. mm | 1600.00 | meter | 11.00 | 30.00 | 48000.00 | 70.00 | 112000.00 | 58.00 | 92800.00 | 48000.00 | Awasthi Electric Works
8.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 35 sq. mm and upto 95 sq. mm | 40.00 | Meter | 11.00 | 30.00 | 1200.00 | 70.00 | 2800.00 | 58.00 | 2320.00 | 1200.00 | Awasthi Electric Works
9.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required Upto 35 sq. mm (clamped with 1mm thick saddle) | 150.00 | Meter | 11.00 | 50.00 | 7500.00 | 70.00 | 10500.00 | 58.00 | 8700.00 | 7500.00 | Awasthi Electric Works
10.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required Above 35 sq. mm and upto 95 sq. mm (clamped with 25x3mm MS flat clamp) | 5400.00 | Meter | 11.00 | 80.00 | 432000.00 | 70.00 | 378000.00 | 40.00 | 216000.00 | 216000.00 | Variant Infratech Private Limited
11.00 | Laying of 120mm dia DWC HDPE pipe along with all accessories like socket, bend, couplers etc. complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc complete as required. | 1600.00 | Meter | 11.00 | 150.00 | 240000.00 | 110.00 | 176000.00 | 1300.00 | 2080000.00 | 176000.00 | Shiva Enterprises
12.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 2C x 6 Sq.mm (19 mm) | 14.00 | set | 11.00 | 250.00 | 3500.00 | 400.00 | 5600.00 | 1150.00 | 16100.00 | 3500.00 | Awasthi Electric Works
13.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3.5C x 90 sq.mm (45 mm) | 16.00 | set | 11.00 | 600.00 | 9600.00 | 700.00 | 11200.00 | 1495.00 | 23920.00 | 9600.00 | Awasthi Electric Works
14.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 16.00 | set | 11.00 | 11500.00 | 184000.00 | 8000.00 | 128000.00 | 7820.00 | 125120.00 | 125120.00 | Variant Infratech Private Limited
15.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required | 50.00 | Meter | 11.00 | 200.00 | 10000.00 | 240.00 | 12000.00 | 288.00 | 14400.00 | 10000.00 | Awasthi Electric Works
16.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 6500.00 | Meter | 11.00 | 20.00 | 130000.00 | 18.00 | 117000.00 | 12.00 | 78000.00 | 78000.00 | Variant Infratech Private Limited
17.00 | Laying of following size. "B" class GI pipe across the nallah / drainage & road crossing / in pavement at a depth of approx. 0.5 mtr including making trench by cutting the road / pavement, excavation and refilling the trench, consolidation and making good the surface excluding PCC work complete etc. as required. Upto 150 mm dia. GI pipe. | 50.00 | Meter | 11.00 | 300.00 | 15000.00 | 1750.00 | 87500.00 | 1725.00 | 86250.00 | 15000.00 | Awasthi Electric Works
18.00 | Supplying, Installation, Testing and Commissioning of making cable route marker with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size ) of size 60 cm X 60 cm at the bottom and 50 cm X 50 cm at the top with a thickness of 1°Cm including inscription duly engraved as required. | 30.00 | Each | 11.00 | 800.00 | 24000.00 | 600.00 | 18000.00 | 5175.00 | 155250.00 | 18000.00 | Shiva Enterprises
19.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 metres in width, and lift upto 1.5 metres, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 metres. | 10.00 | cum | 11.00 | 2000.00 | 20000.00 | 750.00 | 7500.00 | 5175.00 | 51750.00 | 7500.00 | Shiva Enterprises
20.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed medium class PVC conduit, with piano type switch, phenolic laminated sheet, suitable size M.S. box and earthing the point with 1.5 sq.mm. FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 21.00 | point | 11.00 | 1500.00 | 31500.00 | 1950.00 | 40950.00 | 8625.00 | 181125.00 | 31500.00 | Awasthi Electric Works
21.00 | Installation, testing and commissioning of wall mounted fan, including wiring with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable etc. as required. | 7.00 | Each | 11.00 | 150.00 | 1050.00 | 200.00 | 1400.00 | 1150.00 | 8050.00 | 1050.00 | Awasthi Electric Works
22.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required. 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 100.00 | Meter | 11.00 | 270.00 | 27000.00 | 200.00 | 20000.00 | 405.00 | 40500.00 | 20000.00 | Shiva Enterprises
23.00 | Supply of 4 feet, 20 W, 6500K, extruded polycarbonate LED batten suitable to operate on single phase 240V supply | 7.00 | Each | 11.00 | 250.00 | 1750.00 | 450.00 | 3150.00 | 748.00 | 5236.00 | 1750.00 | Awasthi Electric Works
24.00 | Installation, testing and commissioning of pre-wired, fluorescent fitting / compact fluorescent fitting / Street light fitting of all types, complete with all accessories and tube/lamp etc. directly on ceiling/ wall, including connections with 1.5 sq. mm FRLS PVC insulated, copper conductor, single core cable and earthing etc. as required. | 7.00 | Each | 11.00 | 50.00 | 350.00 | 200.00 | 1400.00 | 748.00 | 5236.00 | 350.00 | Awasthi Electric Works
25.00 | Supply of wall mounted fan of 400mm sweep, 1350RPM with control ON-OFF , variable speed modes, oscillation control, height adjustable balanced 3 leaf suitable for operation on 230 volts 50hz AC power supply etc as required.(Make: Havels, Model:Swing or similar from list of approved makes) | 7.00 | Each | 11.00 | 2300.00 | 16100.00 | 2500.00 | 17500.00 | 2875.00 | 20125.00 | 16100.00 | Awasthi Electric Works
26.00 | Supply of floor mounted bubble top water dispenser having cold and hot water storage capacity of minimum 3.2ltr and 0.9Ltr with use of non CFC refrigrent,cooling capacity minimum 2.5Ltr/hr , heating capacity minimum 5Ltr/hr, LED indicator and 3 Faucets (Normal/Hot/Cold) mode function with 02 nos 20Ltr water can etc complete as required. | 8.00 | Each | 11.00 | 18000.00 | 144000.00 | 9500.00 | 76000.00 | 13800.00 | 110400.00 | 76000.00 | Shiva Enterprises
27.00 | Supplying and fixing suitable size PVC box with modular plate and cover in front on surface or in recess, including providing and fixing 2 no 6 pin 5/6 & 15/16 A modular socket outlet and 02 no 15/16 A modular switch, connections etc. as required. | 14.00 | Each | 11.00 | 700.00 | 9800.00 | 650.00 | 9100.00 | 4025.00 | 56350.00 | 9100.00 | Shiva Enterprises
28.00 | Supply of 2 Core 6 sqmm. XLPE insulated & PE Sheathed unshielded (unscreened) Stranded copper conductor single core airfield lighting cable of 5KV grade confirming to IS 7098 Part-II with upto date amendement s as required and conforming to technical specifications enclosed(conforming to IS: 7098-Part II (latest edition) | 3200.00 | Meter | 10.00 | 255.00 | 816000.00 | 275.00 | 880000.00 | 448.50 | 1435200.00 | 816000.00 | Awasthi Electric Works
29.00 | Supply of following size DWC HDPE pipe, lSI marked along with all accessories like socket, bend couplers etc. complete as required. Rodent treated, Non-flame propogated, Termite proof features to be includeded in the pipe. 50 mm dia (OD-50 mm & ID-38 mm nominal) | 3200.00 | Meter | 22.00 | 70.00 | 224000.00 | 75.00 | 240000.00 | 63.00 | 201600.00 | 201600.00 | Variant Infratech Private Limited
30.00 | Laying of 50mm dia DWC HDPE pipe along with all accessories like socket, bend, couplers etc. complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc complete as required. | 3200.00 | Meter | 0.00 | 145.00 | 464000.00 | 70.00 | 224000.00 | 1300.00 | 4160000.00 | 224000.00 | Shiva Enterprises
31.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of grade exceeding 1.1 KV but not exceeding 11 KV of size upto 35 Sq.mm in the existing RCC/HUME/METAL/HDPE pipe as required. | 3200.00 | Meter | 1.00 | 25.00 | 80000.00 | 50.00 | 160000.00 | 58.00 | 185600.00 | 80000.00 | Awasthi Electric Works
32.00 | Supply of 5KV grade plug and receptacle of type I class "B" connector suitable for field attachment with 5KV grade PVC insulated sheathed single core 6 Sq.mm copper conductor cable as per ICAO/CAR compliance and complete as required. | 15.00 | set | 1.00 | 600.00 | 9000.00 | 1650.00 | 24750.00 | 1208.00 | 18120.00 | 9000.00 | Awasthi Electric Works
33.00 | Making field connections by crimping 6 Sq.mm plug and receptacle with the existing 6 Sq.mm Single core copper conductor, PVC insulated, PVC sheathed cable including filling with gap with water sealant material, applying PVC insulation tape over HT tape insulation etc. as required. | 15.00 | set | 1.00 | 500.00 | 7500.00 | 850.00 | 12750.00 | 1725.00 | 25875.00 | 7500.00 | Awasthi Electric Works
34.00 | Installation of transformer housing box with a base concrete of 1:3:6 of size 630 x 630 x 100mm thick all round concrete of 1:2:4 150mm thick. The top sloped with 1:2:4 cement concrete including providing and fixing 10" long 1/2" dia "B" class GI pipe with checknuts for drainage of water including excavation of side shoulder and re-filling (wherever the transformer are in a line the same has to be aligned in such a way that the centers fall in a straight line) etc. complete as required. | 10.00 | Each | 1.00 | 5000.00 | 50000.00 | 6000.00 | 60000.00 | 11500.00 | 115000.00 | 50000.00 | Awasthi Electric Works
35.00 | Providing and Fixing of top cover plate made with 5mm thick MS Sheet suitable for existing 330mm dia CI transformer housing box with 6 Nos. Stainless steel M-10 bolts, spring and plain washers including providing and fixing of rubber gasket, painting etc. complete as required. | 15.00 | Each | 1.00 | 3500.00 | 52500.00 | 4000.00 | 60000.00 | 2875.00 | 43125.00 | 43125.00 | Variant Infratech Private Limited
36.00 | Supply of 200 watts 6.6 Amps 2 pin Halogen lamp suitable for the HIRL fitting./ Suitable for Existing AMA make elevated type HIRL fitting. | 24.00 | Each | 1.00 | 2500.00 | 60000.00 | 3200.00 | 76800.00 | 1325.00 | 31800.00 | 31800.00 | Variant Infratech Private Limited
37.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 3200.00 | Meter | 1.00 | 20.00 | 64000.00 | 18.00 | 57600.00 | 12.00 | 38400.00 | 38400.00 | Variant Infratech Private Limited
| Total in Figures |  |  |  |  | 9654200.00 |  | 8136500.00 |  | 14764602.00
Lowest Amount Quoted BY: Shiva Enterprises(8136500.00)

## BOQ Summary
BOQ Summary Details Tender Title: Development of Solapur Airport. SH Provision of power supply to watch tower and provision of Additional standby feeder for PAPI units Tender ID: 2026_AAI_274999_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Shiva Enterprises (BID ID -1019979) | 8136500.00 | L1
| 2 | Awasthi Electric Works (BID ID -1019988) | 9654200.00 | L2
| 3 | Variant Infratech Private Limited (BID ID -1019973) | 14764602.00 | L3