## BoQ1
Government eProcurement System Created By: Amit Singh Created Date/Time: 22-Jun-2026 03:55 PM Tender Title: Replacement of outdoor feeder pillar at different location at Silchar Airport Tender ID: 2026_AAI_275893_1
Tender Inviting Authority: Asst. General Manager (Engg-Electrical), AAI, Silchar Airport.
Name of Work: Replacement of outdoor feeder pillar at different location at Silchar Airport.
Tender Id: 2026_AAI_275893_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | D.D.METAL CORPORATION (GSTN-18ACGPD4624F2ZW) BID ID -1021638 |  | BR Power Control and Automation Services (GSTN-06AREPS4024K1ZP) BID ID -1022074 |  | ECS ENGINEERING PVT LTD (GSTN-09AABCE5944P1Z1) BID ID -1022187 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -1022238
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Manufacturing, Supply, Installation, Testing & Commissioning of PTTA double door outdoor feeder pillar, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP 65, free standing, floor mounting, dust and vermin proof with canopy type cover, compartmentalized, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system with busbar including internal wiring with suitable size wires/cable, interconnection, duly powder coated painting etc. including supply & installation of following switchgears, metering instruments and accessories in the Panel and as per specifications shall be equipped with surge protection device type-2. i) INCOMER: 320 A, Four pole, Thermal Magnetic release variable range Moulded Case Circuit Breaker with extended rotary handle and all accessories (Icu=Ics, 36 KA). = 2 No.with mechanical/electrical interlocking. ii) BUSBARS: 400 Amp TPN busbars of high conductivity electrolytic quality aluminium alloy. = 1 Set. iii) OUTGOING: (a) 250 A, Four pole, Thermal Magnetic release variable range Moulded Case Circuit Breaker with Operating handle (36 kA) = 2 Nos. (b) 160 A, Four pole, Thermal Magnetic release variable range Moulded Case Circuit Breaker with Operating handle (36 kA) = 2 Nos. (c) 100 A, Four pole, Thermal Magnetic release variable range Moulded Case Circuit Breaker with Operating handle (36 kA) = 3 Nos. (d) 63 A, Four pole, Thermal Magnetic release variable range Moulded Case Circuit Breaker with Operating handle (36 kA) = 2 Nos. (e) 40 A, Two Pole, DP Isolator = 3 Nos. iv) INSTRUMENTS: 1 sets digital voltmeter for 3 phase, 4 wire operation with inbuilt selector switches along with 3 No. control MCB's., 1 sets digital ammeter of suitable range (measure 0 to 300 Amp) for 3 phase, 4 wire operation with inbuilt selector switches and 3 No. suitable range CT's., 1 Set of phase indicating lamps, LED type, RYB for Incomer and ON-OFF indicator for Incomer. (LOCATION: Engg. Civil Office & AAI Residential Main Feeder Pillar) | 1.00 | Job | 0.00 | 440000.00 | 440000.00 | 486829.00 | 486829.00 | 500000.00 | 500000.00 | 592000.00 | 592000.00 | 440000.00 | D.D.METAL CORPORATION
2.00 | Design, Manufacturing, Supply, Installation, Testing & Commissioning of PTTA double door outdoor feeder pillar, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP 65, free standing, floor mounting, dust and vermin proof with canopy type cover, compartmentalized, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system with busbar including internal wiring with suitable size wires/cable, interconnection, duly powder coated painting etc. including supply & installation of following switchgears, metering instruments and accessories in the Panel and as per specifications shall be equipped with surge protection device type-2. i) INCOMER: 250 A, Four pole, Thermal Magnetic release variable range Moulded Case Circuit Breaker with extended rotary handle and all accessories (Icu=Ics, 36 KA). = 1 No. ii) BUSBARS: 300 Amp TPN busbars of high conductivity electrolytic quality aluminium alloy. = 1 Set. iii) OUTGOING: (a) 100 A, Four pole, Thermal Magnetic release variable range Moulded Case Circuit Breaker with Operating handle (36 kA) = 2 Nos. (b) 63 A, Four pole, Thermal Magnetic release variable range Moulded Case Circuit Breaker with Operating handle (36 kA) = 2 Nos. (c) 40 A, Two Pole, DP Isolator = 6 Nos. iv) INSTRUMENTS: 1 sets digital voltmeter for 3 phase, 4 wire operation with inbuilt selector switches along with 3 No. control MCB's., 1 sets digital ammeter of suitable range (measure 0 to 300 Amp) for 3 phase, 4 wire operation with inbuilt selector switches and 3 No. suitable range CT's., 1 Set of phase indicating lamps, LED type, RYB for Incomer and ON-OFF indicator for Incomer. (LOCATION: AAI Residential Colony Sub Main-I Feeder Pillar) | 2.00 | Job | 0.00 | 180000.00 | 360000.00 | 224408.00 | 448816.00 | 240000.00 | 480000.00 | 245000.00 | 490000.00 | 360000.00 | D.D.METAL CORPORATION
3.00 | Design, Manufacturing, Supply, Installation, Testing & Commissioning of PTTA double door outdoor feeder pillar, cubicle type, made out of 2mm thick CRCA sheet, totally enclosed, IP 65, free standing, floor mounting, dust and vermin proof with canopy type cover, compartmentalized, suitable for operation on 3 phase and neutral, 415 V, 50Hz AC system with busbar including internal wiring with suitable size wires/cable, interconnection, duly powder coated painting etc. including supply & installation of following switchgears, metering instruments and accessories in the Panel and as per specifications shall be equipped with surge protection device type-2. i) INCOMER: 160 A, Four pole, Thermal Magnetic release variable range Moulded Case Circuit Breaker with extended rotary handle and all accessories (Icu=Ics, 36 KA). = 1 No. ii) BUSBARS: 200 Amp TPN busbars of high conductivity electrolytic quality aluminium alloy. = 1 Set. iii) OUTGOING: (a) 100 A, Four pole, Thermal Magnetic release variable range Moulded Case Circuit Breaker with Operating handle (36 kA) = 2 Nos. (b) 63 A, Four pole, Thermal Magnetic release variable range Moulded Case Circuit Breaker with Operating handle (36 kA) = 2 Nos. (c) 40 A, Two Pole, DP Isolator = 6 Nos. iv) INSTRUMENTS: 1 sets digital voltmeter for 3 phase, 4 wire operation with inbuilt selector switches along with 3 No. control MCB's., 1 sets digital ammeter of suitable range (measure 0 to 300 Amp) for 3 phase, 4 wire operation with inbuilt selector switches and 3 No. suitable range CT's., 1 Set of phase indicating lamps, LED type, RYB for Incomer and ON-OFF indicator for Incomer. (LOCATION: CISF Barrack & CISF Family Qtr, AAI Residential APD Quarter Block & AAI Residential Colony Sub Main-II Feeder Pillar) | 3.00 | Job | 0.00 | 170000.00 | 510000.00 | 214210.00 | 642630.00 | 195000.00 | 585000.00 | 227000.00 | 681000.00 | 510000.00 | D.D.METAL CORPORATION
4.00 | Supply of 1250 A ACB, 4 Pole, 50KA, Model SR18G Protection LSIGN C-POWER S1 Draw-Out ACBs will have inbuilt 6NO+6NC Aux contact for EDO breakers, Safety shutter assembly, Racking handle, Door sealing frame, Push-button cover & Rating error preventor. Electrical version includes 240V AC Shunt trip coil, Closing coil and Motor for electrical charging complete as required. (MAKE: L&T or Equivalent) | 1.00 | Each | 0.00 | 271000.00 | 271000.00 | 234720.00 | 234720.00 | 143400.00 | 143400.00 | 195000.00 | 195000.00 | 143400.00 | ECS ENGINEERING PVT LTD
5.00 | Supply of Shunt Release (SR) Type EA1 : 415V AC for 800 A, 3 Pole ACB complete as required. (MAKE: L&T or Equivalent) | 2.00 | Each | 0.00 | 3000.00 | 6000.00 | 3487.00 | 6974.00 | 1900.00 | 3800.00 | 2500.00 | 5000.00 | 3800.00 | ECS ENGINEERING PVT LTD
6.00 | Supply of Under Voltage Release (UVR) Type MV : 415V AC for 800 A, 3 Pole ACB complete as required. (MAKE: L&T or Equivalent) | 2.00 | Each | 0.00 | 4700.00 | 9400.00 | 4900.00 | 9800.00 | 3200.00 | 6400.00 | 4000.00 | 8000.00 | 6400.00 | ECS ENGINEERING PVT LTD
7.00 | Supply of Microswitch for Common Indication of O/L & S/C (3) each for 800 A, 3 Pole ACB complete as required. (MAKE: L&T or Equivalent) | 2.00 | Each | 0.00 | 4700.00 | 9400.00 | 4793.00 | 9586.00 | 1800.00 | 3600.00 | 35000.00 | 70000.00 | 3600.00 | ECS ENGINEERING PVT LTD
8.00 | Supply of Spring charging Motor 240V AC for 800 A, 3 Pole ACB complete as required. (MAKE: L&T or Equivalent) | 2.00 | Each | 0.00 | 48000.00 | 96000.00 | 15000.00 | 30000.00 | 24000.00 | 48000.00 | 3500.00 | 7000.00 | 7000.00 | Awasthi Electric Works
9.00 | Supply of Motor Limit Switch for 800 A, 3 Pole ACB complete as required. (MAKE: L&T or Equivalent) | 2.00 | Each | 0.00 | 2000.00 | 4000.00 | 6124.00 | 12248.00 | 1900.00 | 3800.00 | 3500.00 | 7000.00 | 3800.00 | ECS ENGINEERING PVT LTD
10.00 | Supply of Hardware kit for Motor for 800 A, 3 Pole ACB complete as required. (MAKE: L&T or Equivalent) | 2.00 | Each | 0.00 | 2600.00 | 5200.00 | 20864.00 | 41728.00 | 2000.00 | 4000.00 | 35000.00 | 70000.00 | 4000.00 | ECS ENGINEERING PVT LTD
11.00 | Supplying of 3.5 core, 70 sqmm size of 1.1kv grade multistand aluminium conductor XLPE insulated PVC sheathed armoured Heavy duty power cable (as per IS: 7098:1988 with upto date amendments) complete as required as per specifications. | 200.00 | Mtr | 0.00 | 750.00 | 150000.00 | 627.00 | 125400.00 | 550.00 | 110000.00 | 525.00 | 105000.00 | 105000.00 | Awasthi Electric Works
12.00 | Supplying of 3.5 core, 185 sqmm size of 1.1kv grade multistand aluminium conductor XLPE insulated PVC sheathed armoured Heavy duty power cable (as per IS: 7098:1988 with upto date amendments) complete as required as per specifications. | 600.00 | Mtr | 0.00 | 1640.00 | 984000.00 | 1429.00 | 857400.00 | 1285.00 | 771000.00 | 1245.00 | 747000.00 | 747000.00 | Awasthi Electric Works
13.00 | Supply of 250A changeover switch with weather proof enclosure complete as required. | 1.00 | Each | 0.00 | 30000.00 | 30000.00 | 42216.00 | 42216.00 | 26000.00 | 26000.00 | 25500.00 | 25500.00 | 25500.00 | Awasthi Electric Works
14.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 4 X 16 sq. mm (28mm) | 10.00 | Each | 0.00 | 600.00 | 6000.00 | 610.00 | 6100.00 | 250.00 | 2500.00 | 350.00 | 3500.00 | 2500.00 | ECS ENGINEERING PVT LTD
15.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 25 sq. mm (28mm) | 6.00 | Each | 0.00 | 600.00 | 3600.00 | 680.00 | 4080.00 | 260.00 | 1560.00 | 350.00 | 2100.00 | 1560.00 | ECS ENGINEERING PVT LTD
16.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 35 sq. mm (32mm) | 6.00 | Each | 0.00 | 700.00 | 4200.00 | 750.00 | 4500.00 | 270.00 | 1620.00 | 400.00 | 2400.00 | 1620.00 | ECS ENGINEERING PVT LTD
17.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 50 sq. mm (35mm) | 6.00 | Each | 0.00 | 1000.00 | 6000.00 | 809.00 | 4854.00 | 300.00 | 1800.00 | 450.00 | 2700.00 | 1800.00 | ECS ENGINEERING PVT LTD
18.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 70 sq. mm (38mm) | 6.00 | Each | 0.00 | 1700.00 | 10200.00 | 892.00 | 5352.00 | 350.00 | 2100.00 | 550.00 | 3300.00 | 2100.00 | ECS ENGINEERING PVT LTD
19.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 185 sq. mm (57mm) | 6.00 | Each | 0.00 | 2500.00 | 15000.00 | 1500.00 | 9000.00 | 1600.00 | 9600.00 | 1000.00 | 6000.00 | 6000.00 | Awasthi Electric Works
20.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 3½ X 240 sq. mm (62mm) | 3.00 | Each | 0.00 | 3000.00 | 9000.00 | 1800.00 | 5400.00 | 1900.00 | 5700.00 | 1200.00 | 3600.00 | 3600.00 | Awasthi Electric Works
21.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. Above 35 sq. mm and upto 95 sq. mm | 100.00 | Mtr | 0.00 | 550.00 | 55000.00 | 465.00 | 46500.00 | 470.00 | 47000.00 | 450.00 | 45000.00 | 45000.00 | Awasthi Electric Works
22.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required. Above 95 sq. mm and upto 185 sq. mm | 200.00 | Mtr | 0.00 | 550.00 | 110000.00 | 580.00 | 116000.00 | 600.00 | 120000.00 | 450.00 | 90000.00 | 90000.00 | Awasthi Electric Works
23.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Above 35 sq. mm and upto 95 sq. mm | 25.00 | Mtr | 0.00 | 75.00 | 1875.00 | 93.00 | 2325.00 | 50.00 | 1250.00 | 65.00 | 1625.00 | 1250.00 | ECS ENGINEERING PVT LTD
24.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Above 95 sq. mm and upto 185 sq. mm | 35.00 | Mtr | 0.00 | 125.00 | 4375.00 | 134.00 | 4690.00 | 75.00 | 2625.00 | 85.00 | 2975.00 | 2625.00 | ECS ENGINEERING PVT LTD
25.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 35 sq. mm and upto 95 sq. mm | 25.00 | Mtr | 0.00 | 75.00 | 1875.00 | 104.00 | 2600.00 | 50.00 | 1250.00 | 50.00 | 1250.00 | 1250.00 | ECS ENGINEERING PVT LTD, Awasthi Electric Works
26.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 95 sq. mm and upto 185 sq. mm | 35.00 | Mtr | 0.00 | 125.00 | 4375.00 | 135.00 | 4725.00 | 75.00 | 2625.00 | 70.00 | 2450.00 | 2450.00 | Awasthi Electric Works
27.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Above 35 sq. mm and upto 95 sq. mm | 50.00 | Mtr | 0.00 | 100.00 | 5000.00 | 104.00 | 5200.00 | 100.00 | 5000.00 | 140.00 | 7000.00 | 5000.00 | D.D.METAL CORPORATION, ECS ENGINEERING PVT LTD
28.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Above 95 sq. mm and upto 185 sq. mm | 180.00 | Mtr | 0.00 | 100.00 | 18000.00 | 120.00 | 21600.00 | 120.00 | 21600.00 | 175.00 | 31500.00 | 18000.00 | D.D.METAL CORPORATION
29.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 12.00 | Set | 0.00 | 9000.00 | 108000.00 | 10000.00 | 120000.00 | 8000.00 | 96000.00 | 11500.00 | 138000.00 | 96000.00 | ECS ENGINEERING PVT LTD
30.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 75.00 | Mtr | 0.00 | 25.00 | 1875.00 | 433.00 | 32475.00 | 270.00 | 20250.00 | 300.00 | 22500.00 | 1875.00 | D.D.METAL CORPORATION
31.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 1300.00 | Mtr | 0.00 | 40.00 | 52000.00 | 65.00 | 84500.00 | 45.00 | 58500.00 | 45.00 | 58500.00 | 52000.00 | D.D.METAL CORPORATION
| Total in Figures |  |  |  |  | 3291375.00 |  | 3428248.00 |  | 3085980.00 |  | 3426900.00
Lowest Amount Quoted BY: ECS ENGINEERING PVT LTD(3085980.00)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of outdoor feeder pillar at different location at Silchar Airport Tender ID: 2026_AAI_275893_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ECS ENGINEERING PVT LTD (BID ID -1022187) | 3085980.00 | L1
| 2 | D.D.METAL CORPORATION (BID ID -1021638) | 3291375.00 | L2
| 3 | Awasthi Electric Works (BID ID -1022238) | 3426900.00 | L3
| 4 | BR Power Control and Automation Services (BID ID -1022074) | 3428248.00 | L4