## BoQ1
Government eProcurement System Created By: BHAITHI DEVARAJU Created Date/Time: 24-Jun-2026 12:26 PM Tender Title: Provision of Power Supply to DVOR at Vijayawada Airport Tender ID: 2026_AAI_275940_1
Tender Inviting Authority: Asst. General Manager (Engg-E), Airports Authority of India, Vijayawada International Airport.
Name of Work: Provision of Power Supply to DVOR at Vijayawada Airport.
Contract No: 2026_AAI_275940_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Balaji Engineering (GSTN-33ADGPV2628A1ZV) BID ID -1031053 |  | Manish Electricals (GSTN-23ABLPM9012E1ZW) BID ID -1031118 |  | DY Infra & Projects Private Limited (GSTN-NA) BID ID -1031187
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply, installation, testing and commissioning of prime rated 30 KVA DG Set along with acoustic enclosure including providing foundation platform as per OEM Design and minor civil works if required, meeting CPCB Pollution Norms of CPCB IV+ as applicable on the Day of submission of Tender and comprising of following: (A) 01 No. Alternator suitable for generating 24 KW/30 KVA at 415 V, 3 Phase, 50 Hz, 0.8 PF, 1500 RPM, Self ventilated, Self regulated and Self excited with brushless type with Class H Insulation etc., conforming to IS 15999 as specified and as required. (B) 01 No. Multi cylinder, 4 Stroke, Turbo charged Diesel Engine developing suitable BHP at 1500 RPM suitable for above mentioned alternator and complete with all accessories such as base frame, AVM Pads, Battery of 12V 180AH, All types of filters (Including Air filter of heavy duty), Coupling, starter, Automatic electronic speed governing mechanism, Compact radiator etc., and conforming to relevant IS with up to date amendments as specified and as required. (C) Integrated microprocessor based generator set control system providing digital voltage regulation, Engine protection, Alternator protection, Isochronous governing switch for AMF Function, Battery monitoring, Operator interface, Communication interface etc., as specified and as required. (D) 1 No. Integral control / Isolator panel made of 2mm thick CRCA Sheet, comprising of DG Controller (as mentioned above), Copper bus bars of capacity not less than 160 Amps with incoming / outgolng terminals, Indicating lamps for 'Load ON' and 'Set running', Instrument fuses duly wired and ferruled, 4P MCCB of 160 Amps 36 KA rating with Overload, Short circuit and Earth fault protections of microprocessor based as required. (E) 1 No. inbuilt Fuel tank of capacity as per OEM Design complete with connecting pipes, valves, fuel level indicators etc., as specified and as required. (F) Customised Compact Modular Type Tested Acoustic Enclosure suitable for the above DG Set to limit the Noise Level to 75 dB (A) at a distance of 1 Mtr., from the Enclosure, made out of CRCA sheet of 1.6 mm thickness for the Outside Cover and Doors and for Inside Cover with 0.8 mm thick perforated GI Sheet, Louvers of thickness 1.6 mm CRCA Sheet for Fresh Air and Hot Air, Powder coated after Seven Tank Process, Neoprene Rubber Gasket and heavy duty SS locks with SS Hinges, Acoustic made up of high quality rock wool/glass wool/ mineral wool as per OEM design, Base Frame of suitable Size Channel, provision to accommodate Batteries, and Support for Silencers, provided with 4 Nos. LED Tube light Fittings of 2 feet and Switches as required.
1.01 | (G) Exhaust gas piping for above DG of suitable dia.welded black MS, B class pipe confirming to IS:3589 cut to required lengths and installed with necessary bends, supports and clamps, bellows, residential silenser, insulation of exhaust system with mineral wool/Rockwool 50 mm thick, wire mesh & aluminium cladding of minimum thickness of 0.6 mm etc., as required meeting CPWD/PCB/AAI Specifications. All Above 1(A) - 1 (G) | 2.00 | Job | 100.00 | 900000.00 | 1800000.00 | 985000.00 | 1970000.00 | 676000.00 | 1352000.00 | 1352000.00 | DY Infra & Projects Private Limited
2.00 | Fabrication, SITC of MV Switch Board [AMF] Panel made of 14 SWG CRCA Sheet Steel, dust tight, vermin proof, Totally enclosed, cubicle type, Confirming to IP 42, floor mounting, free standing, extensible on both sides, suitable for indoor operation at 433 V, 3 Phase, 4 Wire, 50 Hz, A.C.System complete with all accessories, interconnection, connection, earthing, painting, cable entry provision, provided with bottom base channel and locking arrangements including grouting etc., as required and comprising of the following: (A) One No. 160 A, 36KA, 4P, MCCBs with Thermal Magnetic Releases for OC/SC/EF Protection with microprocessor based releases for EB Supply with CT operated 3 Phase digital protective relay, CT Operated Digital Meter, ON/OFF/TRIP Indication and Phase Indication Lamps. (B) One No. 160 A, 36KA, 4P, MCCBs with Thermal Magnetic Releases for OC/SC/EF Protection with microprocessor based releases for DG Supply with CT operated 3 Phase digital protective relay, CT Operated Digital Meter, ON/OFF/TRIP Indication and Phase Indication Lamps. (C) Two Nos. On Load Change Over Switches of each rating 125A, 4P, 415 V (One for EB and DG Set Bye-Pass Arrangement) including providing and fixing Al Busbars of 200 A Capacity (Neutral At Par) as required. (D) Two Nos. of 4 Module Surge Protection Device (SPD) Type I + II, having 50KA, 10/350 micro seconds neutral to earth at Incomer Side as required. (E) 12 V Battery Charger consisting of transformer, rectifier, DC/AC Ammeter, DC/AC Volt Meter and charge rate selector switch with position OFF/Trickle/OFF/Boost for charging capacity of 12 Volts lead acid battery (1 No 12 volts, 25 plates 180 AH in two steps i.e. trickle/boost charging), Rheostat etc., as required. (F) One Set of Selector Swiches for Auto/Manual/Test/Off Operation and One Set of Push Button for Start/Stop/Reset etc. (G) One Set of 5 mm, 3 LED Display for indicating Performance of DG Set and One Hooter to alarm the abnormality of DG Set. (H) One Set of 200 Amps Al. Bus Bar with at par neutral bus (I) PLC System for Operation and Monitoring of 2 Nos. of DG Set including interlinking with DG Controller, Programming, Operation of II Set in case of I Set fails to start and vice versa etc., as required. (One Common PLC will be installed for both AMF Panel) (J) All accessories such as fuses, auxillary contactors, auxillary switches, timers, MultiCore Control Cabling from DG Set To AMF Panel etc., as required. [Power Cabling Not Included] ALL AS ABOVE 2 (A) TO 2 (J) | 2.00 | Job | 100.00 | 350000.00 | 700000.00 | 290000.00 | 580000.00 | 305000.00 | 610000.00 | 580000.00 | Manish Electricals
3.00 | Fabrication, SITC of MV Switch Board Non-Essential cum APFC Panel made of 14 SWG CRCA Sheet Steel, dust tight, vermin proof, Totally enclosed, cubicle type, Confirming to IP 42, floor mounting, free standing, extensible on both sides, suitable for indoor operation at 433 V, 3 Phase, 4 Wire, 50 Hz, A.C.System complete with all accessories, interconnection, connection, earthing, painting, cable entry provision, provided with bottom base channel and locking arrangements including grouting etc., as required and comprising of the following: (A) Two Nos. of 250A, 50 KA, 4P MCCBs with Thermal Magnetic Releases for OC/SC/EF Protection as INCOMERS with ON/OFF/TRIP Indication Lamps and Phase Indication Lamps, Multifunction Meter i/c. CTs, Interlocking Facility with Incomers and Buscouplers as required. (B) One No. 250A, 50 KA, 4P MCCB as Bus Coupler with ON/OFF Indication Lamps as required. (C) Two Nos. of 4 Module Surge Protection Device (SPD) Type I + II, having 50KA, 10/350 micro seconds neutral to earth at Incomer Side as required. (D) Two Nos. of 15 KVAR Capacitor bank, including suitable capacity 3 Ph., Delta Connected Super Heavy Duty, MPP Capacitor with Al. Round Enclosure of Voltage Rating 440 V (Minimum) with Copper Wound 7% Detuned Reactors, Capacitor Duty Contactors, 63 A, 3P, 15 KA, MCBs, 10 sqmm Interconnecting PVC Insulated FR Copper Flexi-Wires, Push Button, ON/OFF Indication Lamps. (E) Two No. of 14 Steps APFC Relay with VA Sensors of (250/5) Amps Resin Cast CT at appropriate Transformer's Secondary Circuit i/c supplying, laying/fixing of 7C X 2.5 Sq.mm. PVC insulated PVC sheatherd armourned, copper conductor Control Cabling from Transformer Secondary to APFC Panel (suitable length), providing Auto/Manual Facility as required. (F) Two No. 125 A, 36 KA, 4P MCCBs (D Sine Series of L&T/Equivalent) with Thermal Magnetic Releases for OC/SC/EF Protection with microprocessor based releases as Incomer (For capacitor bank) with CT operated 3 Phase digital protective relay, CT Operated Digital Meter, ON/OFF/TRIP Indication, ON OFF Push Buttons, Phase Indication Lamps etc., as required. (G) Two Nos. 200 A, 36 KA, 4P MCCB (D Sine Series of L&T/Equivalent) as Outgoing with inbuilt O/C and E/F Protection with Microprocessor Based Releases and provided with Resin Cast CTs with Digital Meter and ON/OFF/TRIP Indication Lamps etc., as required. (H) Two Nos. 125 A, 36 KA, 4P MCCB (D Sine Series of L&T/Equivalent) as Outgoing with inbuilt O/C and E/F Protection with Microprocessor Based Releases and provided with Resin Cast CTs with Digital Meter and ON/OFF/TRIP Indication Lamps etc., as required.
3.10 | (I) Two Nos. 100 A, 36 KA, 4P MCCB (D Sine Series of L&T/Equivalent) as Outgoing with inbuilt O/C and E/F Protection with Microprocessor Based Releases and provided with Resin Cast CTs with Digital Meter and ON/OFF/TRIP Indication Lamps etc., as required. (J) One Set of 300 Amps Al. Bus Bars with at Par Neutral BUS BARS as required. (K) All accessories such as fuses, auxillary contactors, auxillary switches, etc. as required. All Above 3(A) to 3(K) - 1 Job | 1.00 | Job | 100.00 | 350000.00 | 350000.00 | 70000.00 | 70000.00 | 9500.00 | 9500.00 | 9500.00 | DY Infra & Projects Private Limited
4.00 | Fabrication and S.I.T.C of 250A Rating, 4 Pole on load Changeover switch in Sheet Steel Enclosure complete with Phase barrier, Handle Assembly having Door Interlock and Padlocking arrangement, Indoor MV Feeder Pillar Panel with door arrangement made out of 3mm thick outer, CRCA sheet steel, dust tight, vermin proof, totally enclosed, cubicle type with top canopy for safety protection Confirming to IP54 stand mounting, free standing, suitable for operation at 433 V, 3 phase, 4 wire, 50 Hz, A.C. Power supply system complete with all accessories, interconnection, connection, earthing, painting, grouting, providing pedastal upto the height of 300MM, Cable Entry provision etc. as required. | 1.00 | Job | 100.00 | 50000.00 | 50000.00 | 90000.00 | 90000.00 | 52000.00 | 52000.00 | 50000.00 | Balaji Engineering
5.00 | Supply of 4C x 185 Sq.mm, XLPE insulated and PVC sheathed armoured aluminium conductor power cable of 1.1 KV grade conforming to IS 7098 (Part-1) with upto date ammendments etc., complete as required. (Note: If the manufacturer does not have NABL accredited Laboratory samples from site shall be collected jointly by AAI and the agency and it will be sent to NABL accredited Laboratories / Govt Laboratories / IIT / IISc / IISER / College /University for acceptance Testing as per IS. The contractor will do all Liasoning, Transportation etc. and pay the testing charges. Nothing extra will be paid by AAI. if it is found that the cable supplied is not as per the requirement of IS, The supply will be rejected or recovery shall be made from the bill or any due pending with AAI from any airports) | 1200.00 | Mtr | 10.00 | 1500.00 | 1800000.00 | 1500.00 | 1800000.00 | 2150.00 | 2580000.00 | 1800000.00 | Balaji Engineering, Manish Electricals
6.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 4C x 185 Sq.mm of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 14.00 | Set | 10.00 | 1000.00 | 14000.00 | 1200.00 | 16800.00 | 4550.00 | 63700.00 | 14000.00 | Balaji Engineering
7.00 | Supplying and making end termination with brass compression gland and aluminium lugs for 4C x 16-25 Sq.mm of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 2.00 | Set | 10.00 | 500.00 | 1000.00 | 1000.00 | 2000.00 | 350.00 | 700.00 | 700.00 | DY Infra & Projects Private Limited
8.00 | Supplying and making straight through joint with heat shrinkable kit including ferrules and other jointing materials for 3.5C X 185 sq. mm of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. | 2.00 | Each | 10.00 | 1000.00 | 2000.00 | 4500.00 | 9000.00 | 5820.00 | 11640.00 | 2000.00 | Balaji Engineering
9.00 | Supplying and laying of OD 110 mm dia., HDPE, PE63, PN-6 Pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 4984, complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. | 1100.00 | Mtr | 10.00 | 350.00 | 385000.00 | 550.00 | 605000.00 | 506.00 | 556600.00 | 385000.00 | Balaji Engineering
10.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/DWC/HDPE pipe as required. Above 95 sq. mm and upto 185 sq. mm | 1170.00 | Mtr | 10.00 | 50.00 | 58500.00 | 50.00 | 58500.00 | 110.00 | 128700.00 | 58500.00 | Balaji Engineering, Manish Electricals
11.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 95 sq. mm and upto 185 sq. mm | 20.00 | Mtr | 10.00 | 50.00 | 1000.00 | 100.00 | 2000.00 | 100.00 | 2000.00 | 1000.00 | Balaji Engineering
12.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. 3.5 Core x 185 sq. mm (Clamped with 1.25mm thick saddle) | 10.00 | Mtr | 10.00 | 50.00 | 500.00 | 250.00 | 2500.00 | 350.00 | 3500.00 | 500.00 | Balaji Engineering
13.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 10.00 | Each | 10.00 | 8000.00 | 80000.00 | 8500.00 | 85000.00 | 5450.00 | 54500.00 | 54500.00 | DY Infra & Projects Private Limited
14.00 | Earthing with copper earth plate 600 mm X 600 mm X 5 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 5.00 | Each | 10.00 | 25000.00 | 125000.00 | 22000.00 | 110000.00 | 14500.00 | 72500.00 | 72500.00 | DY Infra & Projects Private Limited
15.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe including GI Bends and laying 0.50 meter below the ground from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 100.00 | Mtr | 10.00 | 600.00 | 60000.00 | 750.00 | 75000.00 | 1150.00 | 115000.00 | 60000.00 | Balaji Engineering
16.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe including GI Bends and laying 0.50 meter below the ground from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 50.00 | Mtr | 10.00 | 1500.00 | 75000.00 | 1400.00 | 70000.00 | 3210.00 | 160500.00 | 70000.00 | Manish Electricals
17.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 25.00 | Mtr | 10.00 | 500.00 | 12500.00 | 550.00 | 13750.00 | 280.00 | 7000.00 | 7000.00 | DY Infra & Projects Private Limited
18.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 15.00 | Mtr | 10.00 | 1300.00 | 19500.00 | 1200.00 | 18000.00 | 2950.00 | 44250.00 | 18000.00 | Manish Electricals
19.00 | Providing and fixing of conventional type lighting protection system with copper lightning conductor finial, made of 25 mm dia. 300 mm long, copper rod, having multi prong at top, with 85 mm dia. 6 mm thick copper base plate and bimetallic plate including holes etc., including providing and installation of 65mm dia., G.I Pole mast up to 6 metre height, one end GI Pole fabricated with 10mm thick GI base plate (250X250X10mm) with 4 No of holes for pole fixing pole including PCC Foundation suitable for installation pole lightning arrester etc., complete as required. | 1.00 | Job | 10.00 | 15000.00 | 15000.00 | 22500.00 | 22500.00 | 12500.00 | 12500.00 | 12500.00 | DY Infra & Projects Private Limited
20.00 | Providing and laying in position cement concrete 1:2:4 (1cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) in foundation / road crossing / flooring etc., including fram work etc as required. | 2.00 | Cum | 10.00 | 6000.00 | 12000.00 | 9500.00 | 19000.00 | 5850.00 | 11700.00 | 11700.00 | DY Infra & Projects Private Limited
21.00 | Supplying and fixing of 6 way (8 + 18), Double door surface / recess mounting, horizontal type, three pole and neutral, sheet steel, MCB distribution board with IP43, IK09 Protection, 415 V, on surface / recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) | 1.00 | Each | 10.00 | 7500.00 | 7500.00 | 7500.00 | 7500.00 | 4950.00 | 4950.00 | 4950.00 | DY Infra & Projects Private Limited
22.00 | Supplying and fixing of 40A, 10kA, Four pole (Three phase & neutral), 415V, residuel current circuit breaker (RCCB) having a sensitivity current 100mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 1.00 | Each | 10.00 | 1000.00 | 1000.00 | 3100.00 | 3100.00 | 2050.00 | 2050.00 | 1000.00 | Balaji Engineering
23.00 | Supplying and fixing of 40A, 10kA, Four pole, C-Curve, 415 V, miniature circuit breaker in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 1.00 | Each | 10.00 | 250.00 | 250.00 | 1600.00 | 1600.00 | 2010.00 | 2010.00 | 250.00 | Balaji Engineering
24.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of single poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 16.00 | Each | 10.00 | 300.00 | 4800.00 | 210.00 | 3360.00 | 380.00 | 6080.00 | 3360.00 | Manish Electricals
25.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLSH PVC insulated copper conductor single core cable in surface / recessed medium class, FRLSH, PVC conduit, with modular switch, modular plate, suitable PVC box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required. Group C | 12.00 | Points | 10.00 | 1500.00 | 18000.00 | 1200.00 | 14400.00 | 1550.00 | 18600.00 | 14400.00 | Manish Electricals
26.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLSH PVC insulated copper conductor, single core cable in surface/ recessed medium class FRLSH PVC conduit as required. 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 30.00 | Mtr | 10.00 | 250.00 | 7500.00 | 300.00 | 9000.00 | 215.00 | 6450.00 | 6450.00 | DY Infra & Projects Private Limited
27.00 | Wiring for light/ power plug with 2X4 sq. mm FRLSH PVC insulated copper conductor single core cable in surface/ recessed medium class FRLSH PVC conduit alongwith 1 No. 4 sq. mm FRLSH PVC insulated copper conductor single core cable for loop earthing as required. | 70.00 | Mtr | 10.00 | 250.00 | 17500.00 | 250.00 | 17500.00 | 290.00 | 20300.00 | 17500.00 | Balaji Engineering, Manish Electricals
28.00 | Supplying and fixing of 6 Module GI box alongwith modular base & cover plate for modular switches in recess etc. as required. | 7.00 | Each | 10.00 | 500.00 | 3500.00 | 250.00 | 1750.00 | 285.00 | 1995.00 | 1750.00 | Manish Electricals
29.00 | Supplying and fixing of 4 Module GI box alongwith modular base & cover plate for modular switches in recess etc. as required | 2.00 | Each | 10.00 | 500.00 | 1000.00 | 200.00 | 400.00 | 235.00 | 470.00 | 400.00 | Manish Electricals
30.00 | Supplying and fixing 10A Modular switch on the existing modular plate & switch box including connections but excluding modular plate etc. as required. | 4.00 | Each | 10.00 | 500.00 | 2000.00 | 1000.00 | 4000.00 | 220.00 | 880.00 | 880.00 | DY Infra & Projects Private Limited
31.00 | Supplying and fixing 20A Modular switch on the existing modular plate & switch box including connections but excluding modular plate etc. as required. | 14.00 | Each | 10.00 | 500.00 | 7000.00 | 150.00 | 2100.00 | 220.00 | 3080.00 | 2100.00 | Manish Electricals
32.00 | Supplying and fixing 6A Modular twin socket outlet on the existing modular plate & switch box including connections but excluding modular plate etc. as required. | 4.00 | Each | 10.00 | 200.00 | 800.00 | 100.00 | 400.00 | 250.00 | 1000.00 | 400.00 | Manish Electricals
33.00 | Supplying and fixing 16A Modular twin socket outlet on the existing modular plate & switch box including connections but excluding modular plate etc. as required. | 14.00 | Each | 10.00 | 500.00 | 7000.00 | 200.00 | 2800.00 | 380.00 | 5320.00 | 2800.00 | Manish Electricals
34.00 | Repairing, servicing, testing and commissioning of 50KVA, On-load, 3-Phase, Air cooled type, micro processed voltage stabilizer. Job includes repairing with all respect without any noise / humming, re-programming, voltage setting etc., complete etc., put in to service condition as required. (Make: Consul, Model: HVS33A0050100086) | 1.00 | Job | 10.00 | 5000.00 | 5000.00 | 35000.00 | 35000.00 | 65000.00 | 65000.00 | 5000.00 | Balaji Engineering
| Total in Figures |  |  |  |  | 5643850.00 |  | 5721960.00 |  | 5986475.00
Lowest Amount Quoted BY: Balaji Engineering(5643850.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Power Supply to DVOR at Vijayawada Airport Tender ID: 2026_AAI_275940_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Balaji Engineering (BID ID -1031053) | 5643850.00 | L1
| 2 | Manish Electricals (BID ID -1031118) | 5721960.00 | L2
| 3 | DY Infra & Projects Private Limited (BID ID -1031187) | 5986475.00 | L3