## BoQ1
Government eProcurement System Created By: TANSUKH TANSUKH Created Date/Time: 10-Jul-2026 03:33 PM Tender Title: Provision of ILS at Kishangarh Airport, Ajmer. SH Electrical works related to Aerosol based Fire Extinguishing System and Addressable Fire Alarm and Detection system. Tender ID: 2026_AAI_276343_2
Tender Inviting Authority:-Asstt. Gen. Manager (Engg-E), Kishangarh Airport, Ajmer-305801
Name of Work:-Provision of ILS at Kishangarh Airport, Ajmer. SH:-Electrical works related to Aerosol based Fire Extinguishing System and Addressable Fire Alarm & Detection system.
Contract No:-2026_AAI_276343_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Nexus Fire And Security Systems (GSTN-07AAKFN7125K1ZY) BID ID -1031855 |  | CENTRE TAP ENGINEERING (GSTN-24AGPPP8172K1ZP) BID ID -1035690 |  | Nexpo Power Solutions Private Limited (GSTN-NA) BID ID -1036341
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Manufacturing and Supply of Fixed Aerosol based Fire Extinguishing system for Equipment Room of (4040(L) x5000(W)x3500(H) mm) having No false ceiling and No False flooring including following major system equipment UL/EN/GOST R53284 listed and in compliance to NFPA 2010/ISO, with upto date amendments and with required fittings and accessories as per technical specification. (A) Suitable nos Electrically operated/actuated Condensed Aerosol generator of suitable capacity of aerosol generating solid compound based on UL/EN/GOST R53284/ISO15779 approved design concentration, Powder-coated MS Body,Stainless Steel Mounting Brackets for Extinguishing generators, applicable for A, B & C class of Fire with Volumetric Design Consideration, Zero Ozone Depletion potential & Zero Global Warming Potential, Negligible Atmospheric LifeTime. (B) Sequential Activator suitable for operate aerosol generators with LED fault indicator. (C) Simulation lamps for testing the signals to the generators. (D) Conventional Agent Release Panel, 4-Zone, LCD display listed to UL/EN and complies with NFPA-72 including battery backup,provision of testing and reseting, gas release indication alarms and system wiring meeting all system requirements etc. complete as required. (E) Conventional type multi criteria (Smoke+heat) detectors UL/EN listed. (F) Manual gas release and gas abort station having manual break glass push button UL/EN listed. (G) Outdoor Flameproof Hooter cum strobe UL/EN listed. (H) Alarm LED signages (DO NOT ENTER & EVACUATE IMMEDIATELY) and Instruction chart. (I) Any other equipments required as per site requirement complete as required. ( Except supply and laying of fire survival cable) (J) Design of complete Fixed Aerosol Fire Extinguishing system shall be duly vetted by the OEM or his authorized dealer. (K) Installation Testing and Commissioning of complete system as per site requirement. | 2.00 | Job | 100.00 | 423066.00 | 846132.00 | 418500.00 | 837000.00 | 513579.00 | 1027158.00 | 837000.00 | CENTRE TAP ENGINEERING
2.00 | Design, manufacturing and SITC of Fixed Aerosol based Fire Extinguishing system for Battery Room(3720(L) x 5000(W) x 3500(H) mm) having No false ceiling and No False flooring including following major system equipment UL/EN/GOST R53284 listed and in compliance to NFPA 2010/ISO, with upto date amendments and with required fittings and accessories as per technical specification. (A) Suitable nos Electrically operated/actuated Condensed Aerosol generator of suitable capacity of aerosol generating solid compound based on UL/EN/GOST R53284/ISO15779 approved design concentration, Powder-coated MS Body,Stainless Steel Mounting Brackets for Extinguishing generators, applicable for A, B & C class of Fire with Volumetric Design Consideration, Zero Ozone Depletion potential & Zero Global Warming Potential, Negligible Atmospheric LifeTime. (B) Sequential Activator suitable for upto 3 generators with LED fault indicator. (C) Simulation lamps for testing the signals to the generators. (D) Conventional Agent Release Panel, 4-Zone, LCD display listed to UL/EN and complies with NFPA-72 including battery backup,provision of testing and reseting, gas release indication alarms and system wiring meeting all system requirements etc. complete as required. (E) Conventional type multi criteria (Smoke+heat) detectors UL/EN listed. (F) Manual gas release and gas abort station having manual break glass push button UL/EN listed. (G) Outdoor Flameproof Hooter cum strobe UL/EN listed. (H) Alarm LED signages (DO NOT ENTER & EVACUATE IMMEDIATELY) and Instruction chart. (I) Any other equipments required as per site requirement complete as required. ( Except supply and laying of fire survival cable) (J) Design of complete Fixed Aerosol Fire Extinguishing system shall be duly vetted by the OEM or his authorized dealer. (K) Installation Testing and Commissioning of complete system as per site requirement. | 2.00 | Job | 100.00 | 400490.00 | 800980.00 | 418500.00 | 837000.00 | 460325.00 | 920650.00 | 800980.00 | Nexus Fire And Security Systems
3.00 | Supply, installation, Testing & commissioning of IP based Addressable type Fire Alarm control panel of minimum 2 loops (each Loop card having capacity to accommodate minimum 20 detectors and 20 modules) with the following facilities like 80 character display unit, power supply unit, built in battery charger, including 24 Volts sealed maintenance free lead acid batteries for 02 hours backup, suitable for Auto dialer facility, web server PCB for IP connectivity etc. complete as required. | 2.00 | Job | 100.00 | 267277.00 | 534554.00 | 124000.00 | 248000.00 | 70385.00 | 140770.00 | 140770.00 | Nexpo Power Solutions Private Limited
4.00 | SITC of 02 channel wireless auto dialer (GSM based), (Voice and SMS) having facitlity of storing voice message & min. 10 contact numbers, work with all types of GSM network, 1 levels of password protected with all necessary accessories including SIM ( as per site requirement) with 1 year recharge, connections beween fire alarm panel etc, complete as required. | 2.00 | Job | 100.00 | 13935.00 | 27870.00 | 12400.00 | 24800.00 | 15402.00 | 30804.00 | 24800.00 | CENTRE TAP ENGINEERING
5.00 | Supply, Installation, Testing & commissioning of UL / EN listed (latest version) intelligent addressable multi criteria detector (Smoke + heat) ( Base Included) with inbuilt fault isolator isolator base and with unique optical sensing chamber, visible LED, fully coated circuit board, superior RF / Transient protection suitable for 2 wires loop connection, complete with plug into common separate base & housing constructed of LEXAN (or polycarbonate) complete with connections etc. as required and to be installed on ceiling etc. complete as required. | 16.00 | Each | 100.00 | 2227.00 | 35632.00 | 2325.00 | 37200.00 | 2200.00 | 35200.00 | 35200.00 | Nexpo Power Solutions Private Limited
6.00 | Supply, installation, Testing & commissioning of Analoge addressable sounder cum strobe complete with base and mounting box with all mounting accessories (U.L/EN Listed). | 2.00 | Each | 100.00 | 3712.00 | 7424.00 | 4650.00 | 9300.00 | 5163.00 | 10326.00 | 7424.00 | Nexus Fire And Security Systems
7.00 | Supply, Installation, Testing & commissioning of UL/EN listed (latest version) intelligent addressable Manual call station (Resetable pull / push type) suitable for semi flush mounting, IP 54 for indoor use & IP 65 for outdoor use with inbuilt fault isolator / isolator module with double gang outlet box, equipment for key operated test-reset lock, electronic or rotary switches for address setting including cover with connections etc. complete as required. | 4.00 | Each | 100.00 | 3902.00 | 15608.00 | 4650.00 | 18600.00 | 7728.00 | 30912.00 | 15608.00 | Nexus Fire And Security Systems
8.00 | Supplying, installation, testing & commissioning of UL / EN listed Response Indicator i/c Mounting Boxes installed on surface/ recessed having two LED complete with all connections and with termination/ connection etc complete as required. | 4.00 | Each | 100.00 | 160.00 | 640.00 | 155.00 | 620.00 | 130.00 | 520.00 | 520.00 | Nexpo Power Solutions Private Limited
9.00 | Supplying & laying of 2 x 1.5 sqmm fire survival armoured cable, 600 / 1000V rated with annealed copper conductor having glass mica fire barrier tape covered by extruded layer of Cross Linkable Ethylene Propylene Rubber (EPR) insulation and LSZH inner bedding, steel wire armouring & LSZH outer sheath, on existing wall / in pipe / surface etc. complete as required. | 228.00 | Mtr | 100.00 | 201.00 | 45828.00 | 328.60 | 74920.80 | 202.00 | 46056.00 | 45828.00 | Nexus Fire And Security Systems
10.00 | Providing, Fixing,Testing and Commissioning ISI marked portable type fire extinguishers of 6 Kg capacity ABC Dry Powder type as per IS standards, finished externally with red enamel paint, complete in all respects including initial fill and provision of wall suspension and other accessories etc complete as required. | 4.00 | Each | 100.00 | 2607.00 | 10428.00 | 3100.00 | 12400.00 | 24668.00 | 98672.00 | 10428.00 | Nexus Fire And Security Systems
11.00 | Providing, Fixing,Testing and Commissioning ISI marked portable type fire Extinguisher, capacity of 4.5 Kg, Carbon-dioxide type flat base including valve, discharge hose of not less than 10 mm dia. min. 600 mm long & complete in all respects including initial fill with C02 gas confirming to IS:307-1966 filled to a filling ratio of not more than 0.667and wall suspension bracket etc complete as required. | 4.00 | Each | 100.00 | 4623.00 | 18492.00 | 7750.00 | 31000.00 | 24668.00 | 98672.00 | 18492.00 | Nexus Fire And Security Systems
12.00 | Supply & installation of 4 Nos. mild steel sand buckets of 9 litre capacity painted "Red Color" with nomenclature "FIRE" white in english and black in hindi filled with sand complete with stand & canopy duly painted "Red Color" of suitable height to hang 4 Buckets etc complete as required. | 2.00 | Job | 100.00 | 4735.00 | 9470.00 | 7750.00 | 15500.00 | 9717.00 | 19434.00 | 9470.00 | Nexus Fire And Security Systems
| Total in Figures |  |  |  |  | 2353058.00 |  | 2146340.80 |  | 2459174.00
Lowest Amount Quoted BY: CENTRE TAP ENGINEERING(2146340.80)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of ILS at Kishangarh Airport, Ajmer. SH Electrical works related to Aerosol based Fire Extinguishing System and Addressable Fire Alarm and Detection system. Tender ID: 2026_AAI_276343_2
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | CENTRE TAP ENGINEERING (BID ID -1035690) | 2146340.80 | L1
| 2 | Nexus Fire And Security Systems (BID ID -1031855) | 2353058.00 | L2
| 3 | Nexpo Power Solutions Private Limited (BID ID -1036341) | 2459174.00 | L3