## BoQ1
Government eProcurement System Created By: Parmeet Dahiya Created Date/Time: 25-Jun-2026 12:20 PM Tender Title: Renovation Modification Works at MT Workshop at RHQ, NR. SH-Electrical Works Tender ID: 2026_AAI_276901_1
TENDER INVITING AUTHORITY: SENIOR MANAGER ENGG(E), AAI, RHQ, NR, NATS COMPLEX, TR-2 ROAD, IGI AIRPORT, NEW DELHI - 110037.
NAME OF WORK: RENOVATION / MODIFICATION WORKS AT MT WORKSHOP, RHQ-NR, RANGPURI, NEW DELHI. (SH: ELECTRICAL WORKS)
TENDER ID NO.: 2026_AAI_276901_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | NATIONAL SAFETY ENGINEERS (GSTN-07ADCPT3599E3Z6) BID ID -1029621 |  | ECS ENGINEERING PVT LTD (GSTN-09AABCE5944P1Z1) BID ID -1029426 |  | DY Infra & Projects Private Limited (GSTN-NA) BID ID -1029368 |  | SYNERGY LIGHTING SOLUTIONS (GSTN-NA) BID ID -1029578
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of Electrical Spares / Light Fixtures
1.01 | LED Panel light 2x2 ft. (System lumen efficacy ≥105 <120 lm/Watt) Supplying, Installation, Testing & Commissioning of 36 Watt Panel light 2x2 ft. of following body material and construction as per IS:10322 with driver as per the requirement with Driver efficiency >85%, Operating voltage AC 140-270 Volt, freq 50/ 60 hz, Operating temp range -15 deg to 40 deg centigrade, internal surge protection of 2.5 KV with Short & Open circuit protection, THD<10%, PF.≥0.95, IP20, CRI >80, UGR (Unified Glare Rating)<19, Flicker free, (flicker should be below 5%), life time (LED, Driver & Electrical Circuitry) of minimum 50000 Burning Hours with, 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report, CCT 3000°K / 4000°K / 5700°K /6000°K / 6500°K (As per ANSI Bin), SDCM (Standard Deviation Color Matching) <3, Maximum power consumption should not more than the specified rating and fixture shall be of relevant BIS standard & trade mark certificate (TC). Manufactures Word Mark/ Name Engraved/ Embossing/ Screen printing on housing. complete in all respect i/c connections with suitable size FRLS, PVC insulated copper conductor single core cable & earthing etc. as required with minimum 5 year OEM warranty. System lumen efficacy ≥105 <120 lm/Watt output, LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size & CCT shall be as approved by Engineer-in-Charge as per requirement.(Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C). CRCA Sheet body (Thickness>0.50 mm) | 92.00 | NOS. |  | 1630.00 | 149960.00 | 1500.00 | 138000.00 | 3550.00 | 326600.00 | 2000.00 | 184000.00 | 138000.00 | ECS ENGINEERING PVT LTD
1.02 | LED Down lighter (SMD Type) (System lumen efficacy ≥ 105 < 120 lm/Watt) Supplying, Installation, Testing & Commissioning of 18 Watt LED Recessed/Surface Down lighter (Round/ square/ Rectangular) SMD type of following body material with PMMA & prismatic diffuser and construction as per IS: 10322 with driver as per the requirement with Driver efficiency >85%, Operating Voltage AC 140-270 Volt, frequency 50/60 hz, Operating temp. range -15 deg to 40 deg. centigrade, internal surge protection of 2.5 KV with Short & Open circuit protection, THD <10%, P.F.≥0.95, IP20, CRI >80, UGR (Unified Glare Rating) < 19, Flicker free (flicker should be below 5%), life time (LED, Driver & Electrical Circuitary), of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends, CCT 3000°K / 4000°K / 5700°K / 6000°K / 6500°K (As per ANSI Bin), SDCM (Standard Deviation Color Matching) <3, Maximum power consumption should not more than the specified rating & fixture shall be confirming to relevant BIS standard & trade mark certificate (TC). Manufactures Word Mark / Name Engraved/ Embossing/ Screen printing on housing complete in all respect i/c connections with suitable size FRLS, PVC insulated copper conductor single core cable & earthing etc. as required with Minimum 5 year OEM warranty. System lumen efficacy ≥105 & <120 lm/Watt output. LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size & CCT shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C). Powder coated die cast /Extruded aluminium Body i/c trim with Aluminium Reflector | 34.00 | NOS. |  | 1000.00 | 34000.00 | 816.00 | 27744.00 | 1670.00 | 56780.00 | 1000.00 | 34000.00 | 27744.00 | ECS ENGINEERING PVT LTD
1.03 | LED Flood Light, powder coated pressure die cast aluminium (System lumen efficacy ≥120 & <135 lm/Watt) Supplying, Installation, Testing & Commissioning of 70 Watt Flood Light, powder coated pressure die cast aluminum body with built in or separate driver as per the requirement with Driver efficiency >85%, Input voltage: 140-270 Volt AC, freq 50/60 hz, Operating temp range -15°C to 50°C, internal surge protection of 5 KV L, N, E as per IEC 61000-4-5, Driver efficiency >85%, THD <10% as per IEC 61000-3-2, P.F. ≥0.95, IP-66, IK-10, CRI >80, under voltage & over voltage protection, EMI-EMC as per CISPR-15, lenses for beam angle 30 deg -120 deg as per the application & project requirement deg. suitable tilt able fitting, life time (LED, Driver & electrical circuitry) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report, CCT 3000°K / 4000°K / 5700°K / 6000°K / 6500°K (As per ANSI Bin), SDCM (Standard Deviation Color Matching) <5, Maximum power consumption should not more than the specified rating and fixture shall be of relevant BIS standard complete in all respect i/c connections with suitable size FRLS, PVC insulated copper conductor single core cable & earthing etc. as required with Minimum 5 year OEM warranty. System lumen efficacy ≥120 & <135 lm/Watt output. LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size & CCT shall be as approved by E-I-C as per requirement. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C). | 9.00 | NOS. |  | 2180.00 | 19620.00 | 1776.00 | 15984.00 | 5500.00 | 49500.00 | 3000.00 | 27000.00 | 15984.00 | ECS ENGINEERING PVT LTD
1.04 | LED Flood Light, powder coated pressure die cast aluminium (System lumen efficacy ≥120 & <135 lm/Watt) Supplying, Installation, Testing & Commissioning of 100 Watt Flood Light, powder coated pressure die cast aluminum body with built in or separate driver as per the requirement with Driver efficiency >85%, Input voltage: Input voltage: 140-270 Volt AC, freq 50/60 hz, Operating temp range -15 deg to 50 deg centigrade, internal surge protection of 5 KV L,N,E as per IEC 61000-4-5, Driver efficiency >85%,THD <10% as per IEC 61000-3-2, P.F.≥0.95, IP-66, IK-10, CRI >80, under voltage & over voltage protection, EMI-EMC as per CISPR-15, lenses for beam angle 30 deg -120 deg as per the application & the project requirement deg, suitable tilt able fitting, life time (LED, Driver & electrical circuitry) of minimum 50000 Burning Hours with 70% of initial Lumen maintained till life ends as per LM80 extrapolation IES TM-21-11 report, CCT 3000°K / 4000°K / 5700°K / 6000°K / 6500°K (As per ANSI Bin), SDCM (Standard Deviation Color Matching) <5, Maximum Power Consumption should not more than the specified rating & fixture shall be of relevant BIS standard complete in all respect i/c connections with suitable size FRLS, PVC insulated copper conductor single core cable & earthing etc. as required with Minimum 5 year OEM warranty. System lumen efficacy ≥120 & <135 lm/ Watt output. LM79 & LM80 Test report from NABL lab for all testing required for LED fixtures as per BIS shall be submitted. Shape size & CCT shall be as approved by Engineer-in-Charge as per requirement. (Thermal management: heat sink of aluminum housing such that LED junction temperature shall not rise above 90°C). | 18.00 | NOS. |  | 2760.00 | 49680.00 | 2280.00 | 41040.00 | 8250.00 | 148500.00 | 4000.00 | 72000.00 | 41040.00 | ECS ENGINEERING PVT LTD
1.05 | Supply, Installation, Testing & Commissioning of heavy duty wall mount Industrial AC Air circulators operating on single phase 240V having sweep of 750 mm having 03 blades, 03 speed control etc. and as directed by E-I-C. | 9.00 | JOB |  | 14000.00 | 126000.00 | 12950.00 | 116550.00 | 6500.00 | 58500.00 | 10000.00 | 90000.00 | 58500.00 | DY Infra & Projects Private Limited
1.06 | Supply, Installation, Testing & Commissioning of heavy duty wall mount Industrial exhaust fans operating on single phase 240V, minimum 600mm sweep, 900 rpm as directed by E-I-C. | 4.00 | JOB |  | 12500.00 | 50000.00 | 10200.00 | 40800.00 | 4800.00 | 19200.00 | 9000.00 | 36000.00 | 19200.00 | DY Infra & Projects Private Limited
1.07 | Supply, Installation, Testing & Commissioning of geyser with 25 Ltr. storage, 5 star BEE rating suitable for operating on single phase AC supply having glass coated heating element, metal body having water pressure of approx 8 bar with all safety features complete as required as directed by E-I-C. | 1.00 | JOB |  | 9000.00 | 9000.00 | 7500.00 | 7500.00 | 9800.00 | 9800.00 | 8000.00 | 8000.00 | 7500.00 | ECS ENGINEERING PVT LTD
2.00 | SITC of Split Air-Conditioning Units
2.01 | Supply of 2.0 TR BEE-5 star rating wall mounted Inverter Split type Air Conditioning Units operating on eco-refrigerant (R32 preferrably), copper condenser & copper evaporator coils suitable for operation on 220-240V, single phase, 50 Hz supply having all safety features, air filters, cordless remote for operation etc. incl. all accessories such as std. length copper pipe (not less than 3 mtrs), drain pipe, laying of power cable, control cable etc. having compressor warranty of minimum 10 years complete as required. | 11.00 | NOS. |  | 60000.00 | 660000.00 | 57800.00 | 635800.00 | 68000.00 | 748000.00 | 50000.00 | 550000.00 | 550000.00 | SYNERGY LIGHTING SOLUTIONS
2.02 | Installation, Testing & Commissioning of 2.0 TR Split AC as per site conditions & connecting the Indoor & Outdoor unit with standard copper pipe of 3 mtrs. approx, brazing, connecting the drain pipe with indoor unit etc. complete as required as directed by E-I-C. | 11.00 | JOB |  | 2500.00 | 27500.00 | 1500.00 | 16500.00 | 3500.00 | 38500.00 | 500.00 | 5500.00 | 5500.00 | SYNERGY LIGHTING SOLUTIONS
2.03 | Supplying & fixing of copper pipe (1/2", 1/4") for suction /liquid line and connecting the same with existing copper pipe, brazing etc. of indoor / outdoor unit along with insulation, fixing insulation with vinyl tape etc. complete as required as per site requirement & as directed by E-I-C. | 100.00 | MTR. |  | 1050.00 | 105000.00 | 525.00 | 52500.00 | 1050.00 | 105000.00 | 2000.00 | 200000.00 | 52500.00 | ECS ENGINEERING PVT LTD
2.04 | Supply & Fixing of Drain Pipe (wiremesh of minimum 1" dia) with insulation of suitable length to connect with existing drain pipe of AC complete as required. | 100.00 | MTR. |  | 150.00 | 15000.00 | 160.00 | 16000.00 | 240.00 | 24000.00 | 200.00 | 20000.00 | 15000.00 | NATIONAL SAFETY ENGINEERS
2.05 | Supplying & Fixing of outdoor wall brackets so as to mount the outdoor units of Split AC on wall/ floor complete as reqd. with nut, bolts etc. as directed by E-I-C. | 11.00 | JOB |  | 850.00 | 9350.00 | 800.00 | 8800.00 | 880.00 | 9680.00 | 1000.00 | 11000.00 | 8800.00 | ECS ENGINEERING PVT LTD
2.06 | Supply of following sizes FRLSH PVC insulated & PVC round sheathed Multi Core Annealed bare Copper stranded Conductor (flexible) industrial Cables for 1100 Volt grade conforming to IS 694: 2010 as & when required as directed by E-I-C:- (A) 3 C x 2.5 sqmm | 200.00 | MTR. |  | 170.00 | 34000.00 | 140.00 | 28000.00 | 160.00 | 32000.00 | 125.00 | 25000.00 | 25000.00 | SYNERGY LIGHTING SOLUTIONS
3.00 | SITC of LT Panel
3.01 | LT PANEL Supply, Installation, Testing & Commissioning of cubicle type LT panel (PTTA) indoor type, IP54 protection, 50 KA suitable for 415V, 3 Phase, 4 wire 50 Hz AC supply system fabricated in compart-mentalized design from CRCA sheet steel of 2 mm thick for frame work and covers, 3 mm thick for gland, plates i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having 4P Aluminium alloy bus bars of high conductivity, SMC bus bar supports,with short circuit withstand capacity of 50 KA for 1 sec, bottom base channel of MS section not less than 100mm x 50mm x 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common copper earth bar of size 25mm x 5mm at the rear with 2 Nos. earth stud, solid connections from main bus bar to switch gears with required size of Alu. bus bars and control wiring with suitable size of PVC insulated copper conductor, cable alleys, cable gland plates in two half i/c providing following:- (A) INCOMER i) 01 No. MCCB, 250A, 36 kA, Four Pole with Microprocessor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). MCCB above shall be provided with: i) 16 Parameter Multifunction digital meter to read A, V, KVA, KW, KVAR, KVAH, HZ, P.F & THD etc. The MFM to be duly equipped with RS-485 Port. ii) OFF / ON / Trip indicating LED lights with 2 Amp. SP MCB iii) Extended Rotary operating mechanism and terminal extension spreaders for all the MCCBs. iv) LED Phase Indicating Lights R,Y,B with 2A SP MCB for protection.
3.02 | (B) Bus Bars 4 Nos 200 A Electrolytic Aluminium Bus-Bars of equal cross-section. (C) OUTGOINGS i) 06 Nos. MCCB, 100A, 30 KA, Four Pole with Micro-processor based (LSING) release having Over Current, Short Circuit, Earth Fault Protection (Ics=Icu). Each Outgoing MCCB above shall be provided with: i) 16 Parameter Multifunction digital meter to read A, V, KVA, KW, KVAR, KVAH, HZ, P.F & THD etc. The MFM to be duly equipped with RS-485 Port. ii) OFF/ ON / Trip indicating LED lights with 2A SP MCB iii) Extended Rotary operating mechanism and terminal extension spreaders for all the MCCBs. iv) LED Phase Indicating Lights R, Y, B with 2A SP MCB for protection. | 2.00 | JOB |  | 450000.00 | 900000.00 | 410000.00 | 820000.00 | 245000.00 | 490000.00 | 300000.00 | 600000.00 | 490000.00 | DY Infra & Projects Private Limited
4.00 | DSR Item
4.01 | Execution of Items of work as per the requirement at site from the CPWD Schedule of Rate (Electrical DSR-2022) as per CPWD Specification complete as required (Total amount of Rs. 3,00,000/- (excl. GST). | 1.00 | JOB |  | 280000.00 | 280000.00 | 390000.00 | 390000.00 | 310000.00 | 310000.00 | 200000.00 | 200000.00 | 200000.00 | SYNERGY LIGHTING SOLUTIONS
5.00 | Dismantling
5.01 | Dismantling of following elecrical equipments along with shifting the same to Electricals Stores complete as required as directed by E-I-C. (i) Light Fittings (PLL Type/ Tublight fittings etc.) Ceiling Fans or any other associated electricals fittings complete as required. | 70.00 | JOB |  | 20.00 | 1400.00 | 100.00 | 7000.00 | 140.00 | 9800.00 | 20.00 | 1400.00 | 1400.00 | SYNERGY LIGHTING SOLUTIONS, NATIONAL SAFETY ENGINEERS
5.02 | Dismantling of upto 2.0 TR Split AC units installed in the existing Rooms etc. & shifting the indoor & outdoor units to AAI Store complete as required as directed by E-I-C. | 15.00 | JOB |  | 300.00 | 4500.00 | 800.00 | 12000.00 | 1750.00 | 26250.00 | 500.00 | 7500.00 | 4500.00 | NATIONAL SAFETY ENGINEERS
| Total in Figures |  |  |  |  | 2475010.00 |  | 2374218.00 |  | 2462110.00 |  | 2071400.00
Lowest Amount Quoted BY: SYNERGY LIGHTING SOLUTIONS(2071400.00)

## BOQ Summary
BOQ Summary Details Tender Title: Renovation Modification Works at MT Workshop at RHQ, NR. SH-Electrical Works Tender ID: 2026_AAI_276901_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SYNERGY LIGHTING SOLUTIONS (BID ID -1029578) | 2071400.00 | L1
| 2 | ECS ENGINEERING PVT LTD (BID ID -1029426) | 2374218.00 | L2
| 3 | DY Infra & Projects Private Limited (BID ID -1029368) | 2462110.00 | L3
| 4 | NATIONAL SAFETY ENGINEERS (BID ID -1029621) | 2475010.00 | L4