## BoQ1
Government eProcurement System Created By: Tarun Kumar Created Date/Time: 16-Jun-2026 12:21 PM Tender Title: Provision of VRF VRV System for Utility Building of New Terminal Building at Civil Enclave Jodhpur Tender ID: 2026_AAI_277667_1
Tender Inviting Authority: Senior Manager (Engg.-E.), AAI, Civil Enclave, Jodhpur.
Name of Work: Provision of VRF/VRV System for Utility Building of New Terminal Building at Civil Enclave Jodhpur.
Contract No: 2026_AAI_277667_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | SHARDA INFRA ENGINEERS PVT LTD (GSTN-07AAPCS8168P1Z7) BID ID -1028117 |  | DY Infra & Projects Private Limited (GSTN-NA) BID ID -1029348
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying, Installation, Testing & Commissioning of Modular type Variable Refrigerant Flow/Variable Refrigerant Volume air cooled Outdoor units suitable for cooling/heating having 100% hermetically sealed inverter type twin Rotary/Scroll Compressor(s), minimum two compressors (with individual separate PCB) for above 14HP modules, microprocessor based Controller, top discharge type condensing unit(s), with R-410-A Refrigerant or equivalent, vibration Isolators with suitable foundation etc. complete as required. To have better efficiency condenser fan shall be capable to operate at different speed with respect to load. The unit shall deliver the rated capacity and in confirmation as per IS 18728:2024 and CPWD Specifications and work even at 50°C ambient temperature without tripping. The system shall be able to deliver 100% of the rated capacity upto 39°C. The unit shall be suitable to work on 400V +/- 10%, 3 Phase, 50Hz AC power supply and BMS compatible. The unit shall be filled with first charge of the refrigerant and ready for use as required. The condenser should be coated with a hydrophilic film to prevent water accumulation on the surface of the heat exchanger, enhance water dispersion, and reduce the risk of degradation, thereby improving overall performance and durability. The Indian Seasonal Energy Efficiency Ratio (ISEER) of the unit shall be as per Energy Conservation and Sustainable Building Code (ECSBC) 2024 as below and complete as per CPWD specification, connections, inter connections etc. as required. (For capacity <40 kWr ISEER 5.4, Capacity > 40 and <70 ISEER 5.5, Capacity > 70 ISEER 5.6 for ECSBC Building For Cooling or Heating or Both , MS Stand with vibration isolators, necessary accessories and top up of refrigerant gas at site.
1.01 | 14 HP dual compressor Module | 1.00 | each | 0.00 | 300000.00 | 300000.00 | 331800.00 | 331800.00 | 300000.00 | SHARDA INFRA ENGINEERS PVT LTD
1.02 | 16 HP dual compressor Module | 1.00 | each | 0.00 | 325000.00 | 325000.00 | 388700.00 | 388700.00 | 325000.00 | SHARDA INFRA ENGINEERS PVT LTD
2.00 | Supplying, Installation, Testing and Commissioning of following minimum capacity 4 way Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX Copper coil, electronic expansion valve, outer cabinet, drain pump, grill, necessary supports, vibration Isolation, Corded remote control etc., suitable for operation on single phase 230 V ± 10%, 50Hz AC supply, complete, as required. The Indoor units must shut down upon receiving a singal from the BMS System/Fire Singnals. The system shall be capable to adjust air flow as per room requirement in auto mode. The cooling capacity of indoor unit will be at air inlet conditions of 27 °C DB and 19 °C WB temperature. (Make will be same as of Outdoor) (Compact Cassette= 2x2 ft.)
2.01 | 1.2 TR | 4.00 | Each | 0.00 | 36000.00 | 144000.00 | 38500.00 | 154000.00 | 144000.00 | SHARDA INFRA ENGINEERS PVT LTD
2.02 | 1.6 TR | 11.00 | Each | 0.00 | 36000.00 | 396000.00 | 40500.00 | 445500.00 | 396000.00 | SHARDA INFRA ENGINEERS PVT LTD
2.03 | 1.8 TR | 2.00 | Each | 0.00 | 40000.00 | 80000.00 | 42500.00 | 85000.00 | 80000.00 | SHARDA INFRA ENGINEERS PVT LTD
3.00 | Supplying, Installation, Testing and Commissioning of Y/T/Multi Joints for Indoor Units. Joints shall be of same Original Equipment Manufacturer (OEM) make as of ODUs and IDUs | 15.00 | Each | 0.00 | 5000.00 | 75000.00 | 5050.00 | 75750.00 | 75000.00 | SHARDA INFRA ENGINEERS PVT LTD
4.00 | Supplying, Installation, testing and commissioning including vaccumiazation and Nitrogen testing of following nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XPLE Class-O tubular insulation/with Class-O closed cell elastometric nitrile rubber tubular sleeves sections of 19 mm thick insulation as given below for Suction and Liquid lines, all accessories as per specifications etc. as required :
4.01 | 6.4 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm | 70.00 | Mtr | 0.00 | 800.00 | 56000.00 | 550.00 | 38500.00 | 38500.00 | DY Infra & Projects Private Limited
4.02 | 9.5 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm | 90.00 | Mtr | 0.00 | 800.00 | 72000.00 | 720.00 | 64800.00 | 64800.00 | DY Infra & Projects Private Limited
4.03 | 12.7 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm | 90.00 | Mtr | 0.00 | 800.00 | 72000.00 | 875.00 | 78750.00 | 72000.00 | SHARDA INFRA ENGINEERS PVT LTD
4.04 | 15.86 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm | 110.00 | Mtr | 0.00 | 800.00 | 88000.00 | 1150.00 | 126500.00 | 88000.00 | SHARDA INFRA ENGINEERS PVT LTD
4.05 | 19 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm | 25.00 | Mtr | 0.00 | 700.00 | 17500.00 | 1230.00 | 30750.00 | 17500.00 | SHARDA INFRA ENGINEERS PVT LTD
4.06 | 22.2 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm | 30.00 | Mtr | 0.00 | 700.00 | 21000.00 | 1350.00 | 40500.00 | 21000.00 | SHARDA INFRA ENGINEERS PVT LTD
4.07 | 28.58 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm | 45.00 | Mtr | 0.00 | 1600.00 | 72000.00 | 2180.00 | 98100.00 | 72000.00 | SHARDA INFRA ENGINEERS PVT LTD
4.08 | 34.9 mm dia (OD) (Hard drawn) with tube thickness 1.62 mm | 25.00 | Mtr | 0.00 | 1800.00 | 45000.00 | 2650.00 | 66250.00 | 45000.00 | SHARDA INFRA ENGINEERS PVT LTD
4.09 | 41.27 mm dia (OD) (Hard drawn) with tube thickness 1.62 mm | 20.00 | Mtr | 0.00 | 2200.00 | 44000.00 | 3700.00 | 74000.00 | 44000.00 | SHARDA INFRA ENGINEERS PVT LTD
5.00 | Supply, installation , testing and commissioning of CPVC drain piping complete with fittings, supports, valve etc. Complete as required
5.01 | 25 mm | 200.00 | Mtr | 0.00 | 200.00 | 40000.00 | 160.00 | 32000.00 | 32000.00 | DY Infra & Projects Private Limited
5.02 | 32 mm | 55.00 | Mtr | 0.00 | 300.00 | 16500.00 | 175.00 | 9625.00 | 9625.00 | DY Infra & Projects Private Limited
6.00 | Providing and Fixing transmission/control wire/Cable PVC insulated of Suitable size as recommended by OEM in 25 mm PVC Conduit between outdoor to outdoor/indoor to indoor/outdoor to indoor and remote control unit. | 306.00 | Mtr | 0.00 | 180.00 | 55080.00 | 135.00 | 41310.00 | 41310.00 | DY Infra & Projects Private Limited
7.00 | Supply and Fixing of 25 mm of Medium class PVC conduit along with accessories in Surface/recess inclusing cutting the wall and making good the same in case of recessed conduit as required. | 306.00 | Mtr | 0.00 | 100.00 | 30600.00 | 30.00 | 9180.00 | 9180.00 | DY Infra & Projects Private Limited
8.00 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as required.
8.01 | 150 mm width X 50 mm depth X 1.6 mm thickness | 200.00 | Mtr | 0.00 | 650.00 | 130000.00 | 720.00 | 144000.00 | 130000.00 | SHARDA INFRA ENGINEERS PVT LTD
8.02 | 300 mm width X 50 mm depth X 1.6 mm thickness | 200.00 | Mtr | 0.00 | 650.00 | 130000.00 | 1050.00 | 210000.00 | 130000.00 | SHARDA INFRA ENGINEERS PVT LTD
9.00 | Supply of 1.1 KV grade XLPE armoured Copper conductor cable of 4Cx16 sqmm sqmm sizes & as per IS:7098-part-I specifications i/c loading/unloading & transportation of cables etc. complete as required: | 150.00 | Mtr | 0.00 | 1200.00 | 180000.00 | 1350.00 | 202500.00 | 180000.00 | SHARDA INFRA ENGINEERS PVT LTD
10.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of Upto 35 sq. mm (clamped with 1mm thick saddle) on wall surface as required. | 150.00 | Mtr | 0.00 | 1800.00 | 270000.00 | 45.00 | 6750.00 | 6750.00 | DY Infra & Projects Private Limited
11.00 | Suppling and making end termination with brass compression gland and copper lugs according to the Copper cable size of 4Cx16 sqmm size for PVC/ XLPE insulated and PVC sheathed armoured copper conductor cable of 1.1 KV grade as required. | 2.00 | Set | 0.00 | 6000.00 | 12000.00 | 850.00 | 1700.00 | 1700.00 | DY Infra & Projects Private Limited
12.00 | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS/HFFR PVC insulated copper conductor, single core cable in surface/ recessed medium class PVC conduit as required.
12.01 | 2X1.5 sqmm + 1x 1.5 sqmm earth wire | 100.00 | Mtr | 0.00 | 160.00 | 16000.00 | 65.00 | 6500.00 | 6500.00 | DY Infra & Projects Private Limited
12.02 | 2X2.5 sqmm + 1x 2.5 sqmm earth wire | 100.00 | Mtr | 0.00 | 225.00 | 22500.00 | 122.00 | 12200.00 | 12200.00 | DY Infra & Projects Private Limited
13.00 | Supplying and fixing suitable size GI box/polycarbonate with modular plate and cover in FRLS on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 amps modular socket outlet and 15/16 amps modular switch, connection etc. as required. | 17.00 | Each | 0.00 | 800.00 | 13600.00 | 750.00 | 12750.00 | 12750.00 | DY Infra & Projects Private Limited
14.00 | Supplying and fixing of 12 way (4+36), TPN, Double door, vertical type , sheet steel, MCB distribution board, 415 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator). | 1.00 | Each | 0.00 | 9000.00 | 9000.00 | 3250.00 | 3250.00 | 3250.00 | DY Infra & Projects Private Limited
15.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
15.01 | Single pole | 17.00 | Each | 0.00 | 360.00 | 6120.00 | 450.00 | 7650.00 | 6120.00 | SHARDA INFRA ENGINEERS PVT LTD
15.02 | Triple pole and neutral | 2.00 | Each | 0.00 | 1600.00 | 3200.00 | 1380.00 | 2760.00 | 2760.00 | DY Infra & Projects Private Limited
16.00 | Supplying and fixing following rating, four pole, 415 volts, 63 Amp, 10 kA, C curve MCB in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 1.00 | Each | 0.00 | 5500.00 | 5500.00 | 2270.00 | 2270.00 | 2270.00 | DY Infra & Projects Private Limited
17.00 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | 7.00 | Each | 0.00 | 100.00 | 700.00 | 50.00 | 350.00 | 350.00 | DY Infra & Projects Private Limited
18.00 | Supply and laying of 4Cx 6 Sqmm Copper unarmoured power cable etc. complete as required. | 50.00 | Mtr | 0.00 | 350.00 | 17500.00 | 510.00 | 25500.00 | 17500.00 | SHARDA INFRA ENGINEERS PVT LTD
19.00 | Supply and laying of 3Cx 2.5 Sqmm Copper unarmoured power cable etc. complete as required. | 50.00 | Mtr | 0.00 | 180.00 | 9000.00 | 215.00 | 10750.00 | 9000.00 | SHARDA INFRA ENGINEERS PVT LTD
20.00 | SITC of 3-Pin top 16 Amp for indoor units power supply etc. complete as required. | 17.00 | Each | 0.00 | 800.00 | 13600.00 | 150.00 | 2550.00 | 2550.00 | DY Infra & Projects Private Limited
21.00 | Supply, Installation, Testing & Commissioning of Central Controller capable of centrally controlling all the outdoor and indoor units including temprature, On/Off, control wiring and connections etc. as per OEM recommandation complete as required. | 1.00 | Each | 0.00 | 45000.00 | 45000.00 | 115000.00 | 115000.00 | 45000.00 | SHARDA INFRA ENGINEERS PVT LTD
22.00 | Earthing with G.I. earth pipe 4.5 Meter long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/coke and salt as required. | 1.00 | Each | 0.00 | 14000.00 | 14000.00 | 13500.00 | 13500.00 | 13500.00 | DY Infra & Projects Private Limited
23.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 50.00 | Mtr | 0.00 | 200.00 | 10000.00 | 130.00 | 6500.00 | 6500.00 | DY Infra & Projects Private Limited
| Total in Figures |  |  |  |  | 2857400.00 |  | 2977495.00
Lowest Amount Quoted BY: SHARDA INFRA ENGINEERS PVT LTD(2857400.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of VRF VRV System for Utility Building of New Terminal Building at Civil Enclave Jodhpur Tender ID: 2026_AAI_277667_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SHARDA INFRA ENGINEERS PVT LTD (BID ID -1028117) | 2857400.00 | L1
| 2 | DY Infra & Projects Private Limited (BID ID -1029348) | 2977495.00 | L2