## BoQ1
Government eProcurement System Created By: SUNIL KUMAR GOUD Created Date/Time: 10-Jul-2026 12:48 PM Tender Title: Replacement of fire hydrant system at Lilabari Airport Tender ID: 2026_AAI_279374_1
Tender Inviting Authority: Airports Authority of India
Name of Work: Replacement of fire hydrant system at Lilabari Airport.
Contract No: 2026_AAI_279374_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | VOID FIRE CONSULTANTS (GSTN-NA) BID ID -1037590 |  | Automation Tools and Equipments (GSTN-NA) BID ID -1038112
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH: I (Electrical Works)
1.01 | Supplying, installation, testing and commissioning of Electric driven Main Fire Pump suitable for automatic operation and consisting of following, complete in all respects, as required : (a) Horizontal type, multistage, centrifugal, split casing pump of cast iron body & bronze impeller with stainless steel shaft, mechanical seal conforming to IS 1520. (b) Suitable HP Squirrel cage induction motor, TEFC,synchronous speed 1500 RPM, suitable for operation on 415 volts, 3 phase 50 Hz, AC supply with IP 55 protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS-325. (c) M.S. fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required. (d) Suitable cement concrete foundation duly plastered with anti vibration pads. 2280 Ipm at 70 m Head | 2.00 | Set | 0.00 | 410000.00 | 820000.00 | 389500.00 | 779000.00 | 779000.00 | Automation Tools and Equipments
2.00 | Supplying, installation, testing and commissioning of diesel engine driven main fire pump suitable for automatic operation and consisting of following, complete in all respects, as required : (Diesel Driven Pump) Horizontal type, multistage, centrifugal pump of cast of iron body and bronze impeller with stainless steel shaft,mechanical seal conforming to IS 1520. diesel engine conforming to relevant IS standard complete with auto starting mechanism, 12 /24 volts electric starting equipment, diesel tank, exhaust pipe extended upto 10 m outside pump house duly insulated with 50 mm thick glass wool with 1.0 mm thick aluminium sheet cladding, residential silencer,instruments and protection as per standard specification, stop solenoid for auto stop in the event of fault with audio indications, painted with post office red colour etc. as required. M.S fabricated, common base plate, coupling, coupling guard, foundation bolts etc. as required. Suitable cement concrete foundation duly plastered and with anti vibration pads. 2280 Ipm at 70 m Head | 1.00 | Set | 0.00 | 699000.00 | 699000.00 | 608000.00 | 608000.00 | 608000.00 | Automation Tools and Equipments
3.00 | Supplying, installation, testing and commissioning of electric driven pressurisation pump suitable for automatic operation and consisting of following,complete in all respects, as required : (Jockey Pump) Horizontal type, multistage, centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal conforming to IS : 1520. Suitable HP squirell cage induction motor TEFC type suitable for operation on 415 volts, 3 phase 50 Hz AC supply with IP 55 class of protection for enclosure, horizontal foot mounted type with Class-'F' insulation, conforming to IS : 325. M.S.fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required. Suitable cement concrete foundation duly plastered and with anti vibration pads. 180 Ipm at 70 m Head | 2.00 | Set | 0.00 | 125000.00 | 250000.00 | 109250.00 | 218500.00 | 218500.00 | Automation Tools and Equipments
4.00 | Fabrication, Supplying, Installation, Testing and Commissioning of electrical control panel of cubical construction, floor/wall mounted type, fabrication out of 2mm. thick CRCA sheet, compartmentalised with hinged lockable doors, dust and vermin proof, powder coated of approved shade after 7 tank treatment process, cable alley, inter-connection, having switchgear, metering instrument and accessories mounting and internal wiring, earth terminals, numbering ect. complete in all respect, suitable for operation on 415 V, 3 phase, 50 HZ. AC supply with enclosure protection class IP 42 as required. A.lncomer ( 1 set) i) 400 A MCCB, 50KA - 2 No.INCOMING with suitable rating 01 buscoupler and interlocking arrangment (Both Electrical and mechanical) 400A, 50kA 4 Pole MCCB, Ics=100% Icu rating Digital Volmeter (0-500V with selector switch Ammeter (0-400 A) with selector switch & CTs etc. LED type RYB phase indicating lamps, ON, OFF, trip indicating lamps. Set of Copper Bus Bar 500A OUTGOING (Note : All outgoing feeders for pumps should have digital Ammeter with selector switches, and LED type ON, OFF, trip indicating lamps) MAIN FIRE PUMP 200 A, 50kA TPN MCCB - 02 Nos, lcs=100% leu, with fully automatic Star/Delta starter suitable for 75 hp pump with overload protection, current sensing type single phase preventor complete with all acceessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/OFF operation. JOCKEY PUMP 100 A, 50kA TPN MCCB - 02 Nos, lcs=100% leu, with suitable HP fully automatic Star/Delta starter with overload protection, current sensing type single phase preventor complete with all acceessories and internal wiring required for automatic operation, selector switch for local/remote, auto/manual/OFF operation. 63 A, 36kA TPN MCCB - 02 Nos, lcs=100% l DIESEL ENGINE CONTROL Control for diesel engine comprising - Automatic/Manual selctor switch & 3 attempt starting device, timers and relays as required, push buttons, start/stop in manual mode Indicating lamp for high/ Low Lub. Oil pressure, High Water Temp and Engine on indication Battery charger suitbale for 12V/24 V DC with boost and trickle selector switch, 0-30 V DC volt meter, and 0-20 A DC Ammeter All standard relays and accessories for automatic operation of diesel engine SYSTEM CONTROLLER Designing, Supply, Installation, Testing and commissioning of system controller to control operation of main electric fire pump, diesel pump, Pressurization pump, Terrace pump in sequence as per specification consisting of relays, timers. Sensors, annunciation window for fault indication, complete as per specifications | 1.00 | Set | 0.00 | 599500.00 | 599500.00 | 19190.00 | 19190.00 | 19190.00 | Automation Tools and Equipments
5.00 | Providing laying, testing & commissioning of 'C' class heavy duty MS Pipe conforming to IS 1239/3589 i/c fittings like elbows, tees, flanges, tapers, nuts bolts,gaskets etc. in ground including welding, excavation & providing cement concrete blocks as supports, anticorrosive treatment with coaltar/asphalt tape as per IS 10221, refilling the trench etc. of following sizes complete as required.
5.01 | 150 mm. Dia | 150.00 | Mtr. | 0.00 | 3685.00 | 552750.00 | 2675.00 | 401250.00 | 401250.00 | Automation Tools and Equipments
5.02 | 100 mm Dia | 30.00 | Mtr. | 0.00 | 2654.00 | 79620.00 | 9878.00 | 296340.00 | 79620.00 | VOID FIRE CONSULTANTS
6.00 | Providing, laying, testing & commissioning of 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 including Welding, fittings like elbows, tees, flanges, tapers, nuts bolts, gaskets etc. and fixing the pipe on the wall/ceiling with suitable clamp/support frame and painting with two or more coats of synthetic enamel paint of required shade complete as required :
6.01 | 25 mm dia | 70.00 | Mtr. | 0.00 | 450.00 | 31500.00 | 2765.00 | 193550.00 | 31500.00 | VOID FIRE CONSULTANTS
6.02 | 80 mm dia | 70.00 | Mtr. | 0.00 | 1400.00 | 98000.00 | 896.00 | 62720.00 | 62720.00 | Automation Tools and Equipments
6.03 | 100 mm dia | 250.00 | Mtr. | 0.00 | 2100.00 | 525000.00 | 1234.00 | 308500.00 | 308500.00 | Automation Tools and Equipments
6.04 | 150 mm dia | 500.00 | Mtr. | 0.00 | 2645.00 | 1322500.00 | 2280.00 | 1140000.00 | 1140000.00 | Automation Tools and Equipments
6.05 | 200 mm dia (wall thickness 6.3 mm) | 20.00 | Mtr | 0.00 | 3500.00 | 70000.00 | 2717.00 | 54340.00 | 54340.00 | Automation Tools and Equipments
7.00 | Supplying and fixing single headed internal hydrant valve with instantaneous Gunmetal/Stainless Steel coupling of 63 mm dia with cast iron wheel ISI marked conforming to IS 5290 (Type -A) with blank Gunmetal/Stainless Steel cap and chain as required
7.01 | Single headed Stainless steel | 8.00 | Set | 0.00 | 6300.00 | 50400.00 | 3990.00 | 31920.00 | 31920.00 | Automation Tools and Equipments
8.00 | Supplying and fixing Single headed external yard hydrant valve with 1 No. 63 mm dia instantaneous FM Gunmetal/Stainless Steel coupling and cast iron wheel, ISI marked, conforming to IS 5290 (type A) with blank Gunmetal/Stainless Steel cap and chain as required
8.01 | Single headed Stainless steel | 15.00 | Set | 0.00 | 6300.00 | 94500.00 | 4580.00 | 68700.00 | 68700.00 | Automation Tools and Equipments
9.00 | Supplying, fixing, testing and commissioning of butterfly valve of PN 1.6 rating with bronze/gunmetal seat duly ISI marked complete with nuts, bolts, washers, gaskets conforming to IS 13095 of following sizes as required
9.01 | 80 mm dia | 30.00 | Set | 0.00 | 3139.00 | 94170.00 | 2890.00 | 86700.00 | 86700.00 | Automation Tools and Equipments
9.02 | 100 mm dia | 5.00 | Set | 0.00 | 4139.00 | 20695.00 | 3760.00 | 18800.00 | 18800.00 | Automation Tools and Equipments
9.03 | 150 mm dia | 5.00 | Set | 0.00 | 5762.00 | 28810.00 | 4950.00 | 24750.00 | 24750.00 | Automation Tools and Equipments
9.04 | 200 mm dia | 1.00 | Set | 0.00 | 8764.00 | 8764.00 | 6175.00 | 6175.00 | 6175.00 | Automation Tools and Equipments
10.00 | Providing, installation, testing and commissioning of non-return valve of following sizes confirming to IS: 5312 complete with rubber gasket, GI bolts, nuts, washers etc.as required
10.01 | 100mm dia | 2.00 | Set | 0.00 | 8705.00 | 17410.00 | 6510.00 | 13020.00 | 13020.00 | Automation Tools and Equipments
10.02 | 150mm dia | 2.00 | Set | 0.00 | 15879.00 | 31758.00 | 6460.00 | 12920.00 | 12920.00 | Automation Tools and Equipments
11.00 | Providing, installation, testing and commissioning of stainless steel Y-strainer fabricated out of 1.6 mm thick stainless steel, Grade 304, sheet with 3 mm dia holes with stainless steel flange
11.01 | 200mm dia | 1.00 | Each | 0.00 | 17895.00 | 17895.00 | 17098.00 | 17098.00 | 17098.00 | Automation Tools and Equipments
12.00 | Supplying and fixing 63 mm dia, 15 m long RRL hose pipe with 63 mm dia male and female couplings duly bound with GI wire, rivets etc. conforming to IS 636 (type-A) as required :
12.01 | Stainless Steel (Grade 304) | 60.00 | Each | 0.00 | 3865.00 | 231900.00 | 3670.00 | 220200.00 | 220200.00 | Automation Tools and Equipments
13.00 | Supplying and fixing first-aid Hose Reel with MS construction spray painted in post office red, conforming to IS 884 complete with the following as required. 30 mtr 20 mm nominal internal dia water hose thermoplastic (Textile reinforced) type -2 as per IS: 12585 20 mm nominal internal dia gun metal globe valve & nozzle. Drum and brackets for fixing the equipment on wall. Connections from riser with 25 mm dia stop gun metal valve & M.S. Pipe and socket. | 10.00 | Set | 0.00 | 7991.00 | 79910.00 | 4560.00 | 45600.00 | 45600.00 | Automation Tools and Equipments
14.00 | Supplying & fixing of 63 mm dia Stainless Steel (Grade 304) short branch pipe with 20 mm nominal internal diameter size nozzle conforming to IS 903 suitable for instantaneous connection to interconnect hose pipe coupling as required | 30.00 | Each | 0.00 | 1703.00 | 51090.00 | 2482.00 | 74460.00 | 51090.00 | VOID FIRE CONSULTANTS
15.00 | Supplying and fixing of fire brigade connection of cast iron body with gun metal male instantaneous inlet couplings complete with cap and chain as reqd. for suitable dia MS pipe connection conforming to IS 904 as required
15.01 | 4 way - 150 mm dia M.S. Pipe | 1.00 | Set | 0.00 | 9563.00 | 9563.00 | 9545.00 | 9545.00 | 9545.00 | Automation Tools and Equipments
16.00 | Supplying and fixing air vessel made of 250 mm dia, 8 mm thick MS sheet, 1200 mm in height with air release valve on top and flanged connection to riser, drain arrangement with 25 mm dia gun metal wheel valve with required accessories, pressure gauge and painting with synthetic enamel paint of approved shade as required. | 2.00 | Set | 0.00 | 15720.00 | 31440.00 | 16136.00 | 32272.00 | 31440.00 | VOID FIRE CONSULTANTS
17.00 | Providing & fixing of pressure switch in M.S. pipe line including connection etc. as required | 4.00 | Each | 0.00 | 1232.00 | 4928.00 | 1258.00 | 5032.00 | 4928.00 | VOID FIRE CONSULTANTS
18.00 | Providing & fixing of pressure Guage in M.S. pipe line including connection etc. as required | 10.00 | Each | 0.00 | 1848.00 | 18480.00 | 1750.00 | 17500.00 | 17500.00 | Automation Tools and Equipments
19.00 | Supply . erection & tearing of electronic level switch with all accessories. | 1.00 | Each | 0.00 | 5240.00 | 5240.00 | 4950.00 | 4950.00 | 4950.00 | Automation Tools and Equipments
20.00 | Providng & Fixing of Air Release Valve made of Gunmetal / Bronze with required fittings as required. | 4.00 | Each | 0.00 | 1022.00 | 4088.00 | 918.00 | 3672.00 | 3672.00 | Automation Tools and Equipments
21.00 | Providing & Fixing of Weather proof hose cabinets fabricated from 16 g M.S. Sheet with full glass door and locking arrangement. The cabinet shall be painted with one coat of primer and finished stove enamelled "Fire Red" (Approx 0.75m x 0.6 m x 0.3 m) Size. | 19.00 | Each | 0.00 | 4192.00 | 79648.00 | 3750.00 | 71250.00 | 71250.00 | Automation Tools and Equipments
22.00 | Supply , erecting, testing and commissioning of following size power cable from switchgear panel to motors in pipe / surface including end termination with brass compression gland complete with lugs etc.
22.01 | 3C x 120 sq.mm armoured 1.1 kv PVC insulated Aluminium conductor cable. | 100.00 | Mtr. | 0.00 | 910.00 | 91000.00 | 765.00 | 76500.00 | 76500.00 | Automation Tools and Equipments
22.02 | 3C x 16 sq. mm. armoured 1. 1 kv PVC insulated Aluminium conductor cable. | 50.00 | Mtr. | 0.00 | 210.00 | 10500.00 | 271.00 | 13550.00 | 10500.00 | VOID FIRE CONSULTANTS
23.00 | Supply, laying,testing and commissioning of control cables from various instruments in composite panel for system protection in pipe/surface i/c end termination with brass compression gland complete with lugs etc. 2C X 2.5 sqmm unarmoured 1. 1 kv, PVC copper cable | 100.00 | Mtr. | 0.00 | 323.00 | 32300.00 | 150.00 | 15000.00 | 15000.00 | Automation Tools and Equipments
24.00 | Supply , installation, testing and commissioning of Submersible Sump Pump Motor set Model 1500 CW of 1.1 KW of 2900 RPM Outlet size 65 MM having capacty 5 L/s at a total head of 15 Mtrs suitable for operations in 3 ph 410+/- 10% Volts, 50 Hz, AC supply. Materials of Construction of Pump motor set is as here under Pump Casing : Cl, Impeller : CI, Shaft : SS, Min Submergency required for continueous operation 480MM | 1.00 | Each | 0.00 | 40610.00 | 40610.00 | 38518.00 | 38518.00 | 38518.00 | Automation Tools and Equipments
25.00 | Supply of 600mm Sweep heavy duty pedestal Air- Circulation Fan,suitable for operation in 230V, 50Hz AC supply etc. as reqd. | 2.00 | Each | 0.00 | 20095.00 | 40190.00 | 9899.00 | 19798.00 | 19798.00 | Automation Tools and Equipments
26.00 | Supply of 450mm Sweep high speed Wall Mounted Air Circulator Fan, suitable for operation in 230V, 50Hz AC supplyetc. as reqd. | 4.00 | Each | 0.00 | 8810.00 | 35240.00 | 2850.00 | 11400.00 | 11400.00 | Automation Tools and Equipments
27.00 | Supply of 450mm Sweep heavy duty Exhaust Fan, suitable for operation in 230V, 50Hz AC supply etc. as reqd. | 4.00 | Each | 0.00 | 7600.00 | 30400.00 | 3620.00 | 14480.00 | 14480.00 | Automation Tools and Equipments
28.00 | Supply of 1400mm Sweep ceiling fans complete with 60 cms. down rod canopies and 100w speed regulator (electronic type) suitable for operation in 230V, 501(z AC supply etc. as reqd. | 4.00 | Each | 0.00 | 4980.00 | 19920.00 | 2750.00 | 11000.00 | 11000.00 | Automation Tools and Equipments
29.00 | Supply of surface mounted ulta slim aluminium LED lighting fixture,environmental friendly, energy efficient, ready to use pack suitable for 230 volt 50 Hz A C supply etc. as reqd. | 20.00 | Each | 0.00 | 800.00 | 16000.00 | 850.00 | 17000.00 | 16000.00 | VOID FIRE CONSULTANTS
30.00 | Supply of following sizes XLPE insulated & PVC sheathed,1.1 KV grade, aluminium conductor, armoured power cable confirming to IS: 7098, Part-1/1988 with upto date amendments
30.01 | 3.5C x 300 Sqmm | 300.00 | Mtr. | 0.00 | 2458.00 | 737400.00 | 1751.00 | 525300.00 | 525300.00 | Automation Tools and Equipments
30.02 | 3.5C x70 Sqmm | 100.00 | Mtr. | 0.00 | 615.00 | 61500.00 | 467.00 | 46700.00 | 46700.00 | Automation Tools and Equipments
30.03 | 3.5C x50 Sqmm | 200.00 | Mtr. | 0.00 | 465.00 | 93000.00 | 358.00 | 71600.00 | 71600.00 | Automation Tools and Equipments
31.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
31.01 | Above 185 sq. mm and upto 400 sq. mm | 200.00 | Mtr. | 0.00 | 220.00 | 44000.00 | 198.00 | 39600.00 | 39600.00 | Automation Tools and Equipments
31.02 | Above 35 sq. mm and upto 95 sq. mm | 230.00 | Mtr. | 0.00 | 145.00 | 33350.00 | 95.00 | 21850.00 | 21850.00 | Automation Tools and Equipments
32.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required.
32.01 | Above 185 sq. mm and upto 400 sq. mm | 30.00 | Mtr. | 0.00 | 217.00 | 6510.00 | 147.00 | 4410.00 | 4410.00 | Automation Tools and Equipments
32.02 | Above 35 sq. mm and upto 95 sq. mm | 80.00 | Mtr. | 0.00 | 145.00 | 11600.00 | 95.00 | 7600.00 | 7600.00 | Automation Tools and Equipments
33.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing masonry open duct as required
33.01 | Above 185 sq. mm and upto 400 sq. mm | 20.00 | Mtr. | 0.00 | 217.00 | 4340.00 | 138.00 | 2760.00 | 2760.00 | Automation Tools and Equipments
33.02 | Above 35 sq. mm and upto 95 sq. mm | 50.00 | Mtr. | 0.00 | 145.00 | 7250.00 | 95.00 | 4750.00 | 4750.00 | Automation Tools and Equipments
34.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV
34.01 | 3½ X 300 sq. mm (70mm) | 4.00 | Each | 0.00 | 1638.00 | 6552.00 | 285.00 | 1140.00 | 1140.00 | Automation Tools and Equipments
34.02 | 3½ X 50 sq. mm (35mm) | 4.00 | Each | 0.00 | 1376.00 | 5504.00 | 190.00 | 760.00 | 760.00 | Automation Tools and Equipments
35.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/ coke and salt as required. | 6.00 | Job | 0.00 | 11790.00 | 70740.00 | 4650.00 | 27900.00 | 27900.00 | Automation Tools and Equipments
36.00 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. (with charcoal/ coke and salt ) as required. | 8.00 | Job | 0.00 | 662.00 | 5296.00 | 5890.00 | 47120.00 | 5296.00 | VOID FIRE CONSULTANTS
37.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | 50.00 | Mtr. | 0.00 | 171.00 | 8550.00 | 175.00 | 8750.00 | 8550.00 | VOID FIRE CONSULTANTS
38.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 70.00 | Mtr. | 0.00 | 171.00 | 11970.00 | 185.00 | 12950.00 | 11970.00 | VOID FIRE CONSULTANTS
39.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 50.00 | Mtr. | 0.00 | 54.00 | 2700.00 | 49.00 | 2450.00 | 2450.00 | Automation Tools and Equipments
40.00 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing as required. | 50.00 | Mtr. | 0.00 | 54.00 | 2700.00 | 47.00 | 2350.00 | 2350.00 | Automation Tools and Equipments
41.00 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FR PVC insulated copper conductor single core cable in surface / recessed steel conduit, with piano type switch, phenolic laminated sheet, suitable size M.S. box and earthing the point with 1.5 sq.mm. FR PVC insulated copper conductor single core cable etc as required.
41.01 | Group A | 20.00 | Job | 0.00 | 44.00 | 880.00 | 39.00 | 780.00 | 780.00 | Automation Tools and Equipments
42.00 | Supplying and fixing following way, horizontal type three pole and neutral, sheet steel, MCB distribution board, 415 volts, on surface/ recess, omplete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/ RCCB/ Isolator)
42.01 | 6 way (4 + 24), Double door | 1.00 | Job | 0.00 | 1965.00 | 1965.00 | 1850.00 | 1850.00 | 1850.00 | Automation Tools and Equipments
43.00 | Supplying and fixing 63 A rating, Four Pole ,415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 1.00 | Job | 0.00 | 2607.00 | 2607.00 | 2250.00 | 2250.00 | 2250.00 | Automation Tools and Equipments
44.00 | Supplying and fixing 5 amps to 32 amps rating, 240/415 volts, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
44.01 | Single pole | 18.00 | Each | 0.00 | 773.00 | 13914.00 | 278.00 | 5004.00 | 5004.00 | Automation Tools and Equipments
45.00 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required.
45.01 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 100.00 | Mtr. | 0.00 | 460.00 | 46000.00 | 298.00 | 29800.00 | 29800.00 | Automation Tools and Equipments
45.02 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 50.00 | Mtr. | 0.00 | 393.00 | 19650.00 | 143.00 | 7150.00 | 7150.00 | Automation Tools and Equipments
46.00 | Supplying and fixing metal box of 150mm X 75mm X 60mm deep (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including providing and fixing 3 pin 5/6 A socket outlet and 5/6 A piano type switch, connections, painting etc. as required. | 15.00 | Each | 0.00 | 210.00 | 3150.00 | 198.00 | 2970.00 | 2970.00 | Automation Tools and Equipments
47.00 | Supplying and fixing metal box of 180mm X 100mm X 60mm deep (nominal size) on surface or in recess with suitable size of phenolic laminated sheet cover in front including providing and fixing 6 pin 5/6 & 15/16 A socket outlet and 15/16 A piano type switch, connections, painting etc. as required. | 20.00 | Each | 0.00 | 393.00 | 7860.00 | 354.00 | 7080.00 | 7080.00 | Automation Tools and Equipments
48.00 | Installation ,Testing, Commissioning of wall bracket /ceiling fittings of all sizes and shapes containing upto two GLS/CFL/LED lamps per fitting, complete with all accessories including connections etc. as required. | 20.00 | Job | 0.00 | 197.00 | 3940.00 | 176.00 | 3520.00 | 3520.00 | Automation Tools and Equipments
49.00 | Installation of exhaust fan/ Ventilating fans in the existing opening, including making good the damage, connection, testing, commissioning etc. as required.
49.01 | Upto 450 mm sweep | 4.00 | Job | 0.00 | 197.00 | 788.00 | 185.00 | 740.00 | 740.00 | Automation Tools and Equipments
50.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray cable tray with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required.
50.01 | 100 mm width X 50 mm depth X 1.6 mm thickness | 50.00 | Mtr | 0.00 | 314.00 | 15700.00 | 291.00 | 14550.00 | 14550.00 | Automation Tools and Equipments
50.02 | 150 mm width X 50 mm depth X 1.6 mm thickness | 30.00 | Mtr | 0.00 | 413.00 | 12390.00 | 385.00 | 11550.00 | 11550.00 | Automation Tools and Equipments
50.03 | 300 mm width X 50 mm depth X 1.6 mm thickness | 20.00 | Mtr | 0.00 | 1265.00 | 25300.00 | 865.00 | 17300.00 | 17300.00 | Automation Tools and Equipments
51.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray “bends “ ( galvanisation not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with G.I. suspenders including G.I. bolts & nuts, etc as required.
51.01 | 100 mm width X 50 mm depth X 1.6 mm thickness | 6.00 | Mtr | 0.00 | 2948.00 | 17688.00 | 1240.00 | 7440.00 | 7440.00 | Automation Tools and Equipments
51.02 | 150 mm width X 50 mm depth X 1.6 mm thickness | 6.00 | Mtr | 0.00 | 4675.00 | 28050.00 | 138.00 | 828.00 | 828.00 | Automation Tools and Equipments
51.03 | 300 mm width X 50 mm depth X 1.6 mm thickness | 3.00 | Mtr | 0.00 | 5700.00 | 17100.00 | 1860.00 | 5580.00 | 5580.00 | Automation Tools and Equipments
52.00 | Supply of 12.5 HP (9.30 KW), 3 Phase, 415 volts, 50 Hz, 2900 RPM, rating, five stage (Pump), vertical Submersible Pump Motor set, discharge capacity minimum 13000 GPH, head minimum - 32 Mtrs, Star-Delta operation etc as required as per specification and make list. | 2.00 | Each | 0.00 | 63535.00 | 127070.00 | 60855.00 | 121710.00 | 121710.00 | Automation Tools and Equipments
53.00 | ITC of existing 12.5 HP Submersible Pump Motor set, including Supply and Laying of 100mm dia. C class GI pipe with necessary sockets, bents etc upto 32Mtr, 10 mm double steel wire rope upto 75 mtr. , 4 sq.mm X 3 core copper flat cable upto 40 Mtr. including lowering with U clamp, well cover (12" X 8"), NRV and Gate valve, supporting clamps, flange, pressure gauge etc,including connection with panel/feeder pillar box for controlling as required. | 2.00 | Each | 0.00 | 90660.00 | 181320.00 | 17575.00 | 35150.00 | 35150.00 | Automation Tools and Equipments
54.00 | Design, Fabrication, supply, installation, Testing and commissioning of Floor Mounted outdoor type, suitable size control panel cum feeder pillar made of CRCA sheet steel of 2 mm thick for frame work and covers i/c cleaning and finishing complete with powder coating in approved shade, having 100 amps capacity TPN aluminium busbars, bottom base of MS channel and Legs, have a common GI earth bar with 2 nos earth stud, internal connection by suitable aluminium strip/bar or aluminium cable as per specification and control wiring with 2.5 Sq.mm PVC insulated copper conductor cable i/c providing the following switch gears and same should be fixed 2 ft. height (from ground level) on brick foundation i/c outgoing and incoming electrical connection etc as required. (a) 63 amps, 4 pole, 25 KA MCCB incoming with extended rotary handle, (b) 12.5 HP rating Star-Delta starter, (c) Single phasing preventer, (d)Time switch with sutiable power contactor, (e) Thermal Over Load relay, (f) Voltmeter and ammeter with necessary CTs and selector switches, LED type indication Lamps for incoming | 2.00 | Job | 0.00 | 163750.00 | 327500.00 | 58600.00 | 117200.00 | 117200.00 | Automation Tools and Equipments
55.00 | SH: II (Civil Works)
56.00 | Earth work in excavation by mechanical means (Hydraulic excavator)/ manual means over areas (exceeding 30 cm in depth, 1.5 m in width as well as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by Engineer-in charge. All kinds of soil | 515.00 | Cum | 0.00 | 233.00 | 119995.00 | 158.00 | 81370.00 | 81370.00 | Automation Tools and Equipments
57.00 | Extra for every additional lift of 1.5 m or part thereof in excavation / banking excavated or stacked materials.All kinds of soil | 210.00 | Cum | 0.00 | 167.00 | 35070.00 | 59.00 | 12390.00 | 12390.00 | Automation Tools and Equipments
58.00 | Construction of granular sub-base by providing close graded Material conforming to specifications, mixing in a mechanical mix plant at OMC, carriage of mixed material by tippers to work site, for all leads & lifts, spreading in uniform layers of specified thickness with motor grader on prepared surface and compacting with vibratory power roller to achieve the desired density, complete as per specifications and directions of Engineer-in-Charge. With material conforming to Grade-I (size range 75 mm to 0.075 mm) having CBR Value-30 | 35.00 | Cum | 0.00 | 3650.00 | 127750.00 | 2385.00 | 83475.00 | 83475.00 | Automation Tools and Equipments
59.00 | Centering and shuttering including strutting, propping etc. and removal of form for Foundations, footings, bases of columns, etc. for mass concrete | 32.00 | Sqm | 0.00 | 514.00 | 16448.00 | 398.00 | 12736.00 | 12736.00 | Automation Tools and Equipments
60.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:4:8 (1 Cement : 4 coarse sand (zone-III) derived from natural sources : 8 graded stone aggregate 40 mm nominal size derived from natural sources) | 25.00 | Cum | 0.00 | 8924.00 | 223100.00 | 4095.00 | 102375.00 | 102375.00 | Automation Tools and Equipments
61.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:3:6 (1 Cement : 3 coarse sand (zone-III) derived from natural sources : 6 graded stone aggregate 20 mm nominal size derived from natural sources) | 14.10 | Cum | 0.00 | 8315.00 | 117241.50 | 4275.00 | 60277.50 | 60277.50 | Automation Tools and Equipments
62.00 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:2:4 (1 cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources) | 14.00 | Cum | 0.00 | 10321.00 | 144494.00 | 5510.00 | 77140.00 | 77140.00 | Automation Tools and Equipments
63.00 | Centering and shuttering including strutting, propping etc. and removal of form for Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | 525.00 | Sqm | 0.00 | 1104.00 | 579600.00 | 2667.00 | 1400175.00 | 579600.00 | VOID FIRE CONSULTANTS
64.00 | Centering and shuttering including strutting, propping etc. and removal of form for Suspended floors, roofs, landings, balconies and access platform. | 215.00 | Sqm | 0.00 | 1215.00 | 261225.00 | 617.00 | 132655.00 | 132655.00 | Automation Tools and Equipments
65.00 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level. Thermo-Mechanically Treated bars of grade Fe-500D or more. | 11400.00 | Kg | 0.00 | 109.00 | 1242600.00 | 96.00 | 1094400.00 | 1094400.00 | Automation Tools and Equipments
66.00 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level : 1:1.5:3 (1 cement : 1.5 coarse sand (zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources) | 95.00 | Cum | 0.00 | 11849.00 | 1125655.00 | 6650.00 | 631750.00 | 631750.00 | Automation Tools and Equipments
67.00 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete above plinth level. Thermo-Mechanically Treated bars of grade Fe-500D or more. | 3480.00 | Kg | 0.00 | 112.00 | 389760.00 | 102.00 | 354960.00 | 354960.00 | Automation Tools and Equipments
68.00 | Centering and shuttering including strutting, propping etc. and removal of form for Columns, Pillars, Piers, Abutments, Posts and Struts | 50.00 | Sqm | 0.00 | 1104.00 | 55200.00 | 850.00 | 42500.00 | 42500.00 | Automation Tools and Equipments
69.00 | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. above plinth level up to floor five level, excluding cost of centering, shuttering, finishing and reinforcement : 1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources) | 4.00 | Cum | 0.00 | 14217.00 | 56868.00 | 6860.00 | 27440.00 | 27440.00 | Automation Tools and Equipments
70.00 | Centering and shuttering including strutting, propping etc. and removal of form for Lintels, beams, plinth beams, girders, bressumers and cantilevers | 100.00 | Sqm | 0.00 | 965.00 | 96500.00 | 660.00 | 66000.00 | 66000.00 | Automation Tools and Equipments
71.00 | Reinforced cement concrete work in beams, suspended floors, roofs having slope up to 15° landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases above plinth level up to floor five level, excluding the cost of centering, shuttering, finishing and reinforcement with 1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources). | 25.00 | cum | 0.00 | 15072.00 | 376800.00 | 7900.00 | 197500.00 | 197500.00 | Automation Tools and Equipments
72.00 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in : Cement mortar 1:4 (1 cement : 4 coarse sand) | 35.00 | cum | 0.00 | 5712.00 | 199920.00 | 4560.00 | 159600.00 | 159600.00 | Automation Tools and Equipments
73.00 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in: Cement mortar 1:6 (1 cement : 6 coarse sand) | 2.00 | cum | 0.00 | 8247.00 | 16494.00 | 5325.00 | 10650.00 | 10650.00 | Automation Tools and Equipments
74.00 | 12 mm cement plaster of mix : 1:4 (1 cement: 4 fine sand) | 145.00 | sqm | 0.00 | 452.00 | 65540.00 | 375.00 | 54375.00 | 54375.00 | Automation Tools and Equipments
75.00 | 15 mm cement plaster on the rough side of single or half brick wall of mix : 1:4 (1 cement: 4 fine sand) | 145.00 | sqm | 0.00 | 523.00 | 75835.00 | 485.00 | 70325.00 | 70325.00 | Automation Tools and Equipments
76.00 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/10 sqm) | 145.00 | sqm | 0.00 | 210.00 | 30450.00 | 66.00 | 9570.00 | 9570.00 | Automation Tools and Equipments
77.00 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. | 145.00 | sqm | 0.00 | 205.00 | 29725.00 | 54.00 | 7830.00 | 7830.00 | Automation Tools and Equipments
78.00 | Wall painting with acrylic emulsion paint, having VOC (Volatile Organic Compound ) content less than 50 grams/ litre, of approved brand and manufacture, including applying additional coats wherever required, to achieve even shade and colour. | 145.00 | sqm | 0.00 | 121.00 | 17545.00 | 95.00 | 13775.00 | 13775.00 | Automation Tools and Equipments
79.00 | Steel work welded in built up sections/ framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer using structural steel etc. as required. In stringers, treads, landings etc. of stair cases, including use of chequered plate wherever required, all complete | 500.00 | kg | 0.00 | 162.00 | 81000.00 | 88.00 | 44000.00 | 44000.00 | Automation Tools and Equipments
80.00 | Providing and Placing in position suitable PVC water stops conforming to IS:12200 for construction/ expansion joints between two RCC members and fixed to the reinforcement with binding wire beforevpouring concrete etc. complete : Serrated with central bulb (225 mm wide, 8-11 mm thick) | 355.00 | Mtr | 0.00 | 430.00 | 152650.00 | 195.00 | 69225.00 | 69225.00 | Automation Tools and Equipments
81.00 | Supplying and fixing rolling shutters of approved make, made of required size M.S. laths, interlocked together through their entire length and jointed together at the end by end locks, mounted on specially designed pipe shaft with brackets, side guides and arrangements for inside and outside locking with push and pull operation complete, including the cost of providing and fixing necessary 27.5 cm long wire springs manufactured from high tensile steel wire of adequate strength conforming to IS: 4454 - part 1 and M.S. top cover of required thickness for rolling shutters.80x1.25 mm M.S. laths with 1.25 mm thick top cover | 6.00 | sqm | 0.00 | 4786.00 | 28716.00 | 1250.00 | 7500.00 | 7500.00 | Automation Tools and Equipments
82.00 | Boring/drilling bore well of required dia for casing/ strainer pipe, by suitable method prescribed in IS: 2800 (part I), including collecting samples from different strata, preparing and submitting strata chart/ bore log, including hire & running charges of all equipments, tools, plants & machineries required for the job, all complete as per direction of Engineer-in-charge, upto 90 metre depth below ground level. All types of soil 300 mm dia | 90.00 | mtr | 0.00 | 927.00 | 83430.00 | 834.00 | 75060.00 | 75060.00 | Automation Tools and Equipments
83.00 | Boring/drilling bore well of required dia for casing/ strainer pipe, by suitable method prescribed in IS: 2800 (part I), including collecting samples from different strata, preparing and submitting strata chart/ bore log, including hire & running charges of all equipments, tools, plants & machineries required for the job, all complete as per direction of Engineer-in-charge, beyond 90 metre & upto 150 metre depth below ground level. All types of soil 300 mm dia | 60.00 | Mtr | 0.00 | 1081.00 | 64860.00 | 956.00 | 57360.00 | 57360.00 | Automation Tools and Equipments
84.00 | Supplying, assembling, lowering and fixing in vertical position in bore well, unplasticized PVC medium well casing (CM) pipe of required dia, conforming to IS: 12818, including required hire and labour charges, fittings & accessories etc. all complete, for all depths, as per direction of Engineer -in-charge.200 mm nominal size dia | 100.00 | Mtr | 0.00 | 1459.00 | 145900.00 | 1350.00 | 135000.00 | 135000.00 | Automation Tools and Equipments
85.00 | Supplying, assembling, lowering and fixing in vertical position in bore well unplasticized PVC medium well screen (RMS) pipes with ribs, conforming to IS: 12818, including hire & labour charges, fittings & accessories etc. all complete, for all depths, as per direction of Engineer-in-charge. | 50.00 | Mtr | 0.00 | 1459.00 | 72950.00 | 1240.00 | 62000.00 | 62000.00 | Automation Tools and Equipments
86.00 | Gravel packing in tubewell construction in accordance with IS: 4097, including providing gravel fine/ medium/ coarse, in required grading & sizes as per actual requirement, all complete as per direction of Engineer-in-charge. | 5.00 | cum | 0.00 | 2652.00 | 13260.00 | 2337.00 | 11685.00 | 11685.00 | Automation Tools and Equipments
87.00 | Development of tube well in accordance with IS : 2800 (part I) and IS: 11189, to establish maximum rate of usable water yield without sand content (beyond permissible limit), with required capacity air compressor, running the compressor for required time till well is fully developed, measuring yield of well by "V" notch method or any other approved method, measuring static level & draw down etc. by step draw down method, collecting water samples & getting tested in approved laboratory, i/c disinfection of tubewell, all complete, including hire & labour charges of air compressor, tools & accessories etc., all as per requirement and direction of Engineer-in-charge. | 20.00 | hour | 0.00 | 1422.00 | 28440.00 | 1277.00 | 25540.00 | 25540.00 | Automation Tools and Equipments
88.00 | Providing and fixing suitable size threaded mild steel cap or spot welded plate to the top of bore well housing/ casing pipe, removable as per requirement, all complete for borewell of: 200 mm dia | 1.00 | each | 0.00 | 421.00 | 421.00 | 480.00 | 480.00 | 421.00 | VOID FIRE CONSULTANTS
89.00 | Providing and fixing M.S. clamp of required dia to the top of casing/ housing pipe of tubewell as per IS: 2800 (part I), including necessary bolts & nuts of required size complete. 200 mm clamp | 4.00 | each | 0.00 | 3004.00 | 12016.00 | 950.00 | 3800.00 | 3800.00 | Automation Tools and Equipments
90.00 | Providing and fixing Bail plug/ Bottom plug of required dia to the bottom of pipe assembly of tubewell as per IS:2800 (part I). 200 mm dia | 1.00 | Each | 0.00 | 322.00 | 322.00 | 285.00 | 285.00 | 285.00 | Automation Tools and Equipments
91.00 | Extra for providing and mixing water proofing material in cement concrete work in doses by weight of cement as per manufacturer's specification. | 760.00 | 50 Kg Bag | 0.00 | 24.00 | 18240.00 | 17.00 | 12920.00 | 12920.00 | Automation Tools and Equipments
92.00 | Providing and applying integral crystalline slurry of hydrophilic in nature for waterproofing treatment to the RCC structures like retaining walls of the basement, water tanks, roof slabs, podiums, reservior, sewage & water treatment plant, tunnels / subway and bridge deck etc., prepared by mixing in the ratio of 5 : 2 (5 parts integral crystalline slurry : 2 parts water) for vertical surfaces and 3 : 1 (3 parts integral crystalline slurry : 1 part water) for horizontal surfaces and applying the same from negative (internal) side with the help of synthetic fiber brush. The material shall meet the requirements as specified in ACI- 212-3R-2010 i.e by reducing permeability of concrete by more than 90% compared with control concrete as per DIN 1048 and resistant to 16 bar hydrostatic pressure on negative side. The crystalline slurry shall be capable of self-healing of cracks up to a width of 0.50mm. The work shall be carried out all complete as per specification and the direction of the engineer-in-charge. The product performance shall carry guarantee for 10 years against any leakage. For vertical surface two coats @ 0.70 kg per sqm | 240.00 | Sqm | 0.00 | 685.00 | 164400.00 | 235.00 | 56400.00 | 56400.00 | Automation Tools and Equipments
93.00 | Providing and applying integral crystalline slurry of hydrophilic in nature for waterproofing treatment to the RCC structures like retaining walls of the basement, water tanks, roof slabs, podiums, reservior, sewage & water treatment plant, tunnels / subway and bridge deck etc., prepared by mixing in the ratio of 5 : 2 (5 parts integral crystalline slurry : 2 parts water) for vertical surfaces and 3 : 1 (3 parts integral crystalline slurry : 1 part water) for horizontal surfaces and applying the same from negative (internal) side with the help of synthetic fiber brush. The material shall meet the requirements as specified in ACI- 212-3R-2010 i.e by reducing permeability of concrete by more than 90% compared with control concrete as per DIN 1048 and resistant to 16 bar hydrostatic pressure on negative side. The crystalline slurry shall be capable of self-healing of cracks up to a width of 0.50mm. The work shall be carried out all complete as per specification and the direction of the engineer-in-charge. The product performance shall carry guarantee for 10 years against any leakage. For horizontal surface one coat @1.10 kg per sqm. | 150.00 | Sqm | 0.00 | 540.50 | 81075.00 | 334.00 | 50100.00 | 50100.00 | Automation Tools and Equipments
94.00 | Providing Engineering Consultancy Services for undergroung sump and pump house drawing, i/c associated, RCC work, RCC wall, RCC coloum and brick wall for pump house with all relevant calculation sheet and design vetted by I.I.T/NIT/Reputed Government College, issue of good for construction drawings and revision of drawing if required during execution etc. as specified in tender document and any other details related to consultancy work which are essential for successful execution of works etc complete as per direction and satisfaction of EIC. Note:- Three sets of RCC work, RCC wall, RCC coloum and brick wall drawing and Architectural drawing has to be provided by the agency at the office of E.I.C. | 1.00 | Job | 0.00 | 112040.00 | 112040.00 | 80350.00 | 80350.00 | 80350.00 | Automation Tools and Equipments
| Total in Figures |  |  |  |  | 14674088.50 |  | 11678615.50
Lowest Amount Quoted BY: Automation Tools and Equipments(11678615.50)

## BOQ Summary
BOQ Summary Details Tender Title: Replacement of fire hydrant system at Lilabari Airport Tender ID: 2026_AAI_279374_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Automation Tools and Equipments (BID ID -1038112) | 11678615.50 | L1
| 2 | VOID FIRE CONSULTANTS (BID ID -1037590) | 14674088.50 | L2