## BoQ1
Government eProcurement System Created By: Narender Kumar Created Date/Time: 30-Jun-2026 12:25 PM Tender Title: SITC of LPS at RCDU Workshop, Old Area, New Delhi. Tender ID: 2026_AAI_279869_1
Tender Inviting Authority: Sr. Mgr., Airports Authority of India, Safdarjung Airport, New Delhi-110003.
Name of Work: SITC of LPS at RCDU Workshop, Old Area, New Delhi.
Contract No: AAI/SAP/Engg(E)/LPS/RCDU/26-27
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Vrinda Nano Technologies Pvt Ltd (GSTN-06AABCV6699N1ZG) BID ID -1037728 |  | Nexpo Power Solutions Private Limited (GSTN-NA) BID ID -1037617
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SITC of Parallel Connectors for (700mm air terminal) connecting two conductors in parallel manner. Material- StSt, with clamping range- Rd / Rd 7-10 mm & Complied as per Standard EN 62561-1. | 40.00 | No. | 100.00 | 3800.00 | 152000.00 | 3500.00 | 140000.00 | 140000.00 | Nexpo Power Solutions Private Limited
2.00 | SITC of Air-termination rod having length- 2500 mm, of Material- AlMgSi, of Diameter Ø 16 / 10 mm (rod lower dia 16mm/rod upper dia 10mm), chamfered on both ends, & Complied as per Standard EN 62561-2. | 14.00 | No. | 100.00 | 27500.00 | 385000.00 | 22500.00 | 315000.00 | 315000.00 | Nexpo Power Solutions Private Limited
3.00 | SITC of FS clamp for air-termination rods of 16 mm dia, clamps for connecting air-termination rods to conductors with truss head screw, plate, nut and double clamp ,Material of clamp: Al, should have Clamping for air-termination rod: 16 mm dia & Clamping range of Round conductor: 2x 8-10 mm. | 14.00 | No. | 10.00 | 2200.00 | 30800.00 | 2565.00 | 35910.00 | 30800.00 | Vrinda Nano Technologies Pvt Ltd
4.00 | SITC of Universal connector of Material- StSt, with clamping range- 8-10mm, with truss head screw M10x35 mm & Complied as per Standard EN 62561-1., | 143.00 | No. | 10.00 | 950.00 | 135850.00 | 1050.00 | 150150.00 | 135850.00 | Vrinda Nano Technologies Pvt Ltd
5.00 | SITC of Roof Conductor of Diameter Ø- 8 mm, Cross-section- 50 mm2, of Material- AlMgSi & Complied as per Standard EN 62561-2. | 970.00 | Mtr | 10.00 | 910.00 | 882700.00 | 785.00 | 761450.00 | 761450.00 | Nexpo Power Solutions Private Limited
6.00 | SITC of Conductor holder for Parapet wall/Side wall of Material- StSt, for Rd 8-10 mm Fl 20 mm, Height- 20 mm & Complied as per Standard EN 62561-4.With accessories Screw and Gitty, Material SS (M5 x 50mm) | 370.00 | No. | 10.00 | 1025.00 | 379250.00 | 930.00 | 344100.00 | 344100.00 | Nexpo Power Solutions Private Limited
7.00 | SITC of Roof conductor holder for installing rigid conductor running on the corrugated sheet roof having profile height range from 5 mm and 8 mm, Material of conductor holder: SS,the clamp shall support Round counder of 8-10 mm dia. | 500.00 | No. | 10.00 | 1405.00 | 702500.00 | 1390.00 | 695000.00 | 695000.00 | Nexpo Power Solutions Private Limited
8.00 | SITC of Conductor holder for downpipes for installing down conductors with fixed conductor routing Type PV, adjustable, with M8 clamping screw, suitable to be clampled on pipe: 50-120 mm dia , clamp shall hold round Conductor of 6-8 mm dia Material of conductor holder: SS | 2.00 | No. | 10.00 | 2400.00 | 4800.00 | 2350.00 | 4700.00 | 4700.00 | Nexpo Power Solutions Private Limited
9.00 | SITC of Lightning strike counter 3 Digit LCD Impulse real Date time Counter for recording discharge currents.For recording lightning and impulse Max. countable impulse current (10/350 µs) (Iimp )100 kA Min. countable impulse current (10/350 µs) (Iimp )1 kA currents in down conductors (including HVI Conductors), earthing und equipotential bonding systemsLightning strike counter as per GB/T 33588.6 and IEC 62561-6: Type 1 + type 2 CE, GB, UKCA | 4.00 | No. | 10.00 | 58300.00 | 233200.00 | 60000.00 | 240000.00 | 233200.00 | Vrinda Nano Technologies Pvt Ltd
10.00 | SITC of Copper insulated Conductor (CUI), 3500 mm long CUI Conductor for avoiding touch voltages on down conductors. Material of conductor: Cu, Material of insulation: XLPE, overall Diameter of conductor: 20 mm , cross-section of core: 50 mm2,Colour of conductor: light grey Standard: EN 62561-2. | 16.00 | No. | 10.00 | 66000.00 | 1056000.00 | 65300.00 | 1044800.00 | 1044800.00 | Nexpo Power Solutions Private Limited
11.00 | SITC of Conductor holder for the CUI Conductor for mounting the CUI conductor (black) or HVI light Conductor, e.g. for wall mounting Material of conductor holder: StSt Conductor support Rd: 20-21 mm Fixing : 6.5 x 16 mm Screw: M6 x 14 Standard: EN 62561-4 | 64.00 | No. | 10.00 | 4000.00 | 256000.00 | 4100.00 | 262400.00 | 256000.00 | Vrinda Nano Technologies Pvt Ltd
12.00 | SITC of Isolating spark gap for equipotential bonding according to IEC 62305-3,particularly for use in potentially explosive atmospheres. Power frequency sparkover voltage (50Hz): <= 0.5 kV Rated power frequency withstand voltage (50 Hz): <= 250 V Rated discharge current (50 Hz): 500 A / 0.2 sec. (Tu <= 45°C) Degree of protection: IP67 Enclosure: M10 x 25 screw and spring washer on both ends Approvals CE UL. | 2.00 | No. | 10.00 | 35000.00 | 70000.00 | 35650.00 | 71300.00 | 70000.00 | Vrinda Nano Technologies Pvt Ltd
13.00 | SITC of 3 Phase / Type1+2 Lightning current & Surge Protection Device at mains LT panel (3 phase, 415 V variation of 10%) for (L-N) Single-pole combined digital with 3 Digit LCD Impulse real Date time Counter , lightning current and surge arrester, Type 1 SPD -the device shall be non-exhausting metal encapsulated, spark gap based technology and tested as per latest and valid IEC 61643-11:2011 or EN 61643-11:2012 standards. It shall be capable to discharge Lightning current (10/350µs) of 25kA (L-N) and 100kA(N-E) and voltage protection level of device shall be ≤ 1.5 KV. The device shall have inbuilt fuse for L-N. Follow current extinguishing capability [L-N]/[N-PE] : 100kArms / 100Arms. The short circuit with stand capability of the device shall be 100 KArms for L-N SPD. The device shall have mechanical indication for both the states (green for ‘healthy’ and red for failure) on L-N and N-PE. The device shall be certified by KEMA /VDE or NABL lab as per IEC 61643-11:2011 or or EN 61643-11:2012 for testing of all parameter at 10/350 µs and 8/20 µs .The complete system shall be in transparent enclosure IP65. | 2.00 | No. | 10.00 | 250000.00 | 500000.00 | 265000.00 | 530000.00 | 500000.00 | Vrinda Nano Technologies Pvt Ltd
14.00 | SITC of UNI Disconnecting Clamps with intermediate plate for round and flat conductor, of Material- SS, Material thickness- 2.5 mm, with clamping range for round conductor of 8-10 mm dia & for flat 30 mm width, & Complied as per Standard EN 62561-1. | 16.00 | No. | 10.00 | 925.00 | 14800.00 | 950.00 | 15200.00 | 14800.00 | Vrinda Nano Technologies Pvt Ltd
15.00 | SITC of GI flat (25x6mm) Strip. Having width- 25mm, Thickness- 6mm, Material- Hot dipped Galvanized Iron, Cross Section- 150mm2, & Complied as per IEC 62561-2., | 240.00 | Mtr | 10.00 | 600.00 | 144000.00 | 650.00 | 156000.00 | 144000.00 | Vrinda Nano Technologies Pvt Ltd
16.00 | SITC of GI strip holder of material- Dow moulded compound, having height- 19mm, Slot Size- 25x6 mm. | 36.00 | No. | 10.00 | 810.00 | 29160.00 | 830.00 | 29880.00 | 29160.00 | Vrinda Nano Technologies Pvt Ltd
17.00 | SITC of Copper bonded rod with Low carbon steel, high tensile strength copper bonded rod with min 250 microns of copper plating, UL listed with company name marked on rod. Diameter of rod- 17.2 mm, Length- 3 meters, Material- Copper Bonded, Coating thickness- 250 microns, min, Approvals- Tested acc. IEC / EN 62561-2, UL 467., 20 kg backfilled compound, Material- Carbon based backfill/earthing compound, Fulgurite formation test at direct lightning (10/350 μs), lightning long duration test at 100 degree Celcius- No fulgurites test Pass, Environmentally Friendly ROHS certified, Resistivity< 0.12 ΩM, Complying Standard- IEC 62561-7 , Testing Approvals Certified from- NABL accredited Laboratories, SS-316 grade clamp to terminate the load on earth electrode, Poly plastic pit cover of material- Polymer Body & Cover. | 16.00 | No. | 10.00 | 61000.00 | 976000.00 | 58250.00 | 932000.00 | 932000.00 | Nexpo Power Solutions Private Limited
18.00 | SITC of Anti-corrosion tape( Length of roll-10 Mtr) (width: 50 mm) Anti-corrosion tape For wrapping underground and above ground connections for use in the soil , UV-stabilised Material: petrolatum. | 4.00 | No. | 10.00 | 4000.00 | 16000.00 | 3500.00 | 14000.00 | 14000.00 | Nexpo Power Solutions Private Limited
19.00 | SITC of advanced Earthing Monitoring System with Local HMI, IoT Cloud, and Mobile App support. It is DIN rail mountable (35mm, EN60715) and supports Wi-Fi, RS-485, and Ethernet connectivity. Measures Earthing Resistance (0.31–30 Ω) using the Fall of Potential (3-pole) method, Earth Leakage (0.010–30A), and N-E Voltage (0.5–15V) across up to 3 channels. Provides fault indication via LED, display, web interface, and 2 potential-free contacts for alarms. Operates on 110–415V AC, 45–55Hz. | 1.00 | No. | 10.00 | 315000.00 | 315000.00 | 325000.00 | 325000.00 | 315000.00 | Vrinda Nano Technologies Pvt Ltd
20.00 | SITC of Expansion piece, round Expansion piece For temperature-related length compensation of long conductors (provided that the conductor routing in the holders is loose) Material: Al Dimensions: Ø8 mm Length: approx. 395 mm, Standard: EN 62561-2. | 34.00 | No. | 10.00 | 1500.00 | 51000.00 | 1385.00 | 47090.00 | 47090.00 | Nexpo Power Solutions Private Limited
21.00 | SITC of Concrete block 17 kg (Approx.) suitable for fixing air termination of rod having length of 2500 mm. | 28.00 | No. | 10.00 | 2200.00 | 61600.00 | 1625.00 | 45500.00 | 45500.00 | Nexpo Power Solutions Private Limited
22.00 | SITC of adhesive Cartage for fixing metal to plastic (lord glue). | 3.00 | No. | 10.00 | 20000.00 | 60000.00 | 16500.00 | 49500.00 | 49500.00 | Nexpo Power Solutions Private Limited
23.00 | SITC of MV clamp with hexagon screw, StSt (V4A) MV clamp Multipurpose connecting clamp for universal use as a cross clamp, T clamp and parallel clamp, for round conductors capable of carrying lightning current tested according to EN 62561-1 with hexagon screw and threaded base part Material of clamp: StSt (V4A) Clamping range Rd: 8-10 mm Connection (solid / stranded): 35-70 mm2 Material thickness: 2.5 mm Material No.: 1.4571 / 1.4404 / 1.4401 ASTM / AISI:: 316Ti / 316L / 316 Standard: EN 62561-1. | 16.00 | No. | 10.00 | 1300.00 | 20800.00 | 1150.00 | 18400.00 | 18400.00 | Nexpo Power Solutions Private Limited
24.00 | SITC of Bridging cable, 500 mm long Bridging cable for connecting or bridging metal cladding. Suitable for use outdoors. Length: 500 mm Material of cable lug: Al Material of cable: Cu Cross-section: 16 mm2 Fixing : [4x] Ø6.5 / [2x] Ø10.5 mm Insulation: rubber EM5 black. | 4.00 | No. | 10.00 | 3500.00 | 14000.00 | 3370.00 | 13480.00 | 13480.00 | Nexpo Power Solutions Private Limited
25.00 | SITC of Roof conductor holder FB2 for flat roofs with concrete block-C35/45 with double conductor holder- Rd 8 mm fixed, Dimension- 141 x 86 x 70 mm | 122.00 | No. | 10.00 | 1000.00 | 122000.00 | 950.00 | 115900.00 | 115900.00 | Nexpo Power Solutions Private Limited
26.00 | SITC of 1000 mm air termination rod. Diameter Ø- 10 mm of Material- AlMgSi. | 10.00 | No. | 10.00 | 5000.00 | 50000.00 | 5500.00 | 55000.00 | 50000.00 | Vrinda Nano Technologies Pvt Ltd
27.00 | SITC of protecting sheet under the concrete base(17 kg.) for protectin of roof. The Diameter Ø outside 370 mm, Diameter Ø inside 360 mm and Material EVA. | 28.00 | No. | 10.00 | 4000.00 | 112000.00 | 3850.00 | 107800.00 | 107800.00 | Nexpo Power Solutions Private Limited
28.00 | Supply, Installation, Testing & Commissioning of Low Impedance Digital Grounding System 240kA Single Phase three wire LIDGS 4th Generation equipment Grounding & bonding system with built in 100% Lightning and Surges, static charge, Noises, ESD, EPR and abnormal electrical characteristics eliminator which enter from power and other service lines and ensuring clear bonding potential (earth to Neutral voltage) less than 1.0V, a digital 3 Digit LCD Impulse real Date time Counter with threshold of 1KA, self health visual status indicator, built Zero leakage Current based solution. Lightning Impulse Current Discharge Capability up to 12 KA (10/350μsec) Surge Discharge Current Capability up to 40KA (8/20μsec) 7 Modes of Protection (L1-N, N?PE, L1- PE) total surge handling capacity 240KA Shortcircuit extinguishing and limiting capabilities up to 25KArms without tripping of Let-through-energy of less than 01 Joule in a Pre-wired pulverulent body painted metal enclosure to be connected in parallel to the power supply circuit, Conforming solution CE NABL IEC 61643-11 -2011. | 2.00 | No. | 10.00 | 395000.00 | 790000.00 | 450000.00 | 900000.00 | 790000.00 | Vrinda Nano Technologies Pvt Ltd
| Total in Figures |  |  |  |  | 7564460.00 |  | 7419560.00
Lowest Amount Quoted BY: Nexpo Power Solutions Private Limited(7419560.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of LPS at RCDU Workshop, Old Area, New Delhi. Tender ID: 2026_AAI_279869_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Nexpo Power Solutions Private Limited (BID ID -1037617) | 7419560.00 | L1
| 2 | Vrinda Nano Technologies Pvt Ltd (BID ID -1037728) | 7564460.00 | L2