## BoQ1
Government eProcurement System Created By: Sunil Waghmare Created Date/Time: 11-Sep-2026 03:50 PM Tender Title: SITC of Fire Fighting Fire Alarm and Detection System for New Terminal Building and New Office Block at Juhu Airport Mumbai Tender ID: 2026_AAI_280396_1
Tender Inviting Authority: AAI
Name of work: SITC of Fire Fighting, Fire Alarm & Detection System for New Terminal Building & New Office Block at Juhu Airport, Mumbai.
Tender ID : 2026_AAI_280396_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Universal Fire And Safety Services (GSTN-27AACCU2212P1Z7) BID ID -1058672 |  | CENTRE TAP ENGINEERING (GSTN-24AGPPP8172K1ZP) BID ID -1061611 |  | Krishsons International Engineers And Consultants (I) Pvt. Ltd (GSTN-NA) BID ID -1062976 |  | ARC SERVICESS (GSTN-NA) BID ID -1063075 |  | Luminosity Infra Projects Pvt Ltd (GSTN-NA) BID ID -1062656
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.10 | Supplying, installation, testing and commissioning of micro processor based intelligent addressable main fire alarm panel, central processing unit with the following loop modules and capable of supporting not less than 240 devices (including detectors) and minimum 120 detectors per loop and loop length up to 2 km, network communication card, minimum 320 character graphics/ LCD display with touch screen or other keypad and minimum 4000 events history log in the non volatile memory (EPROM), power supply unit (230 ± 5 % V, 50 hz), 48 hrs back-up with 24 volt sealed maintenance free batteries with automatic charger. The panel shall have facility to connect printer to printout log and acility to have seamless integration with analog/digital voice evacuation system (which is part of the schedule of work under SH: PA System) and shall be complete with all accessories . The panel shall be compatible for IBMS system with open protocol BACnet/ Modbus over IP complete as per specifications. Make :- AAI Preferred make
1.20 | Two Loop Panel | 2.00 | Each |  | 168390.00 | 336780.00 | 200000.00 | 400000.00 | 175000.00 | 350000.00 | 220000.00 | 440000.00 | 148500.00 | 297000.00 | 297000.00 | Luminosity Infra Projects Pvt Ltd
1.30 | Supplying, installation, testing & commissioning of repeater panel with 320 character/ Touch screen LCD display with inbuilt reset, acknowledge and silence switches complete as required. Make :- AAI Preferred make | 1.00 | Each |  | 83145.00 | 83145.00 | 60000.00 | 60000.00 | 90000.00 | 90000.00 | 125000.00 | 125000.00 | 62600.00 | 62600.00 | 60000.00 | CENTRE TAP ENGINEERING
1.40 | Supplying, installation, testing & commissioning of addressable manual call point complete as required. Make :- AAI Preferred make | 7.00 | Each |  | 6140.00 | 42980.00 | 4500.00 | 31500.00 | 5000.00 | 35000.00 | 2450.00 | 17150.00 | 2900.00 | 20300.00 | 17150.00 | ARC SERVICESS
1.50 | Supplying, installation, testing & commissioning intelligent addressable multi criteria detector (Smoke + heat) (base included) with inbuilt fault isolator base and with unique optical sensing chamber, visible LED, fully coated circuit board, superior RF/Transient protection suitable for 2 wires loop connectionn, complete with plug into common separate base & housing contructed of LEXAN (or plycarbonate) complete with connections etc. as required and to be installed on cilling etc. complete as required. Make :- AAI Preferred make | 65.00 | Each |  | 3195.00 | 207675.00 | 3500.00 | 227500.00 | 3000.00 | 195000.00 | 2450.00 | 159250.00 | 3500.00 | 227500.00 | 159250.00 | ARC SERVICESS
1.60 | Supply, Installation, testing & commissioning of Electronic Hooter with volume control unit giving output of 65 db maximum or 5db above any noise tends to exit. The hooter shall be of wall mounted type. The rate shall include for mounting accessories, etc. complete as required. Make :- AAI Preferred make | 7.00 | Each |  | 7645.00 | 53515.00 | 4500.00 | 31500.00 | 10000.00 | 70000.00 | 2450.00 | 17150.00 | 6200.00 | 43400.00 | 17150.00 | ARC SERVICESS
1.70 | Supplying & laying of 2x1.5 sqmm fire survival armoured cable, 600/1000V rated with annealed copper conductor having glass mica fire barrier tape covered by an extruded layer of Cross Linkable Ethylene Propylene Rubber (EPR) insulation and LSZH inner bedding, steel wire armouring & LSZH outer sheath complete as required. Make: AAI Preferred make | 800.00 | Mtr |  | 199.00 | 159200.00 | 200.00 | 160000.00 | 200.00 | 160000.00 | 230.00 | 184000.00 | 140.00 | 112000.00 | 112000.00 | Luminosity Infra Projects Pvt Ltd
1.80 | Supply & installation of 4 Nos. mild steel sand buckets of 9 liter capacity painted "Red Color" with nomenclature "FIRE" white in English and black in hindi filed with sand complete with stand & canopy duly painted "Red Color" of suitable height to hang 4 Buckets etc complete as required. Make :- AAI Preferred make | 3.00 | Set |  | 5805.00 | 17415.00 | 20000.00 | 60000.00 | 500.00 | 1500.00 | 1000.00 | 3000.00 | 3500.00 | 10500.00 | 1500.00 | Krishsons International Engineers And Consultants (I) Pvt. Ltd
| Total in Figures |  |  |  |  | 900710.00 |  | 970500.00 |  | 901500.00 |  | 945550.00 |  | 773300.00
Lowest Amount Quoted BY: Luminosity Infra Projects Pvt Ltd(773300.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of Fire Fighting Fire Alarm and Detection System for New Terminal Building and New Office Block at Juhu Airport Mumbai Tender ID: 2026_AAI_280396_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Luminosity Infra Projects Pvt Ltd (BID ID -1062656) | 773300.00 | L1
| 2 | Universal Fire And Safety Services (BID ID -1058672) | 900710.00 | L2
| 3 | Krishsons International Engineers And Consultants (I) Pvt. Ltd (BID ID -1062976) | 901500.00 | L3
| 4 | ARC SERVICESS (BID ID -1063075) | 945550.00 | L4
| 5 | CENTRE TAP ENGINEERING (BID ID -1061611) | 970500.00 | L5