## BoQ1
Government eProcurement System Created By: RAVI KUMAR VANKUDOTHU Created Date/Time: 27-Jul-2026 03:37 PM Tender Title: SITC of Fire Suppression for DVOR, ILS and Unmanned CNS Installations at Rajahmundry Airport Tender ID: 2026_AAI_281783_1
Tender Inviting Authority: ASST. GENERAL MANAGER (ENGG-ELECT), AIRPORTS AUTHORITY OF INDIA, RAJAHMUNDRY AIRPORT, RAJAHMUNDRY
Name of Work:SITC of Fire Suppression System for DVOR, ILS, Unmanned CNS Installations at Rajahmundry Airport
Tender ID No: 2026_AAI_281783_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | Nexus Fire And Security Systems (GSTN-07AAKFN7125K1ZY) BID ID -1037921 |  | DOSHI ELECTRIC ENGG. CO. (GSTN-24AAEFD3355K1ZI) BID ID -1042837 |  | CENTRE TAP ENGINEERING (GSTN-24AGPPP8172K1ZP) BID ID -1043685 |  | advent electric technologies pvt. ltd. (GSTN-07AAJCA2055K1ZN) BID ID -1043811 |  | DSS Electric Corporation LLP (GSTN-NA) BID ID -1043267 |  | Nexpo Power Solutions Private Limited (GSTN-NA) BID ID -1043680
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Installation, Testing & Commissioning of Aerosol-based fire suppression system for protection of critical areas that shall be electrically actuated including supply of UL/EN approved aerosol generators. The housing shall be constructed of stainless steel shell and sealed with non-permiable membrane. The units shall have passed salt spray corrosion testing as per NFPA/UL/EN/KIWA/UL2775 as part of their listing. The aerosol generator shall be potassium-based, non-toxic and providing effective fire suppression while being environmental friendly with zero Ozone Depletion Potential and Zero Global Warming potential, CFC & HFC-Free. Agent shall be listed by the US EPA under the SNAP program, that shall be non- toxic and marked with the green label. Aerosol generators shall be listed by Underwriter's Laboratory (UL)/EN subject to UL-2775 covering Fixed Condensed Aerosol System as per NFPA 2010. The room flooding must be designed as per UL/EN density of Aerosol less than 110 g/cu. mtr. for Class A, B & C fires as per NFPA 2010. The aerosol generator should have self life of atleast 15 years. The system shall comply with relevant standards including NBC 2016, NFPA 2010, complete with all necessary accessories and works required for satisfactory operation. Note : Number of Aerosol uni, design software for a given dimension of room duly approved by manufacturer (OEM) shall be submitted prior to starting of the works. Fire Suppression System for following rooms and given approximate volume.The gas Supression should be integrated with the Exsisting Conventioanl Type Fire detection and Alarm system of Ravel make with Fire Alarm panel of Model RE-102.
1.10 | DVOR- EQUIPMENT ROOM (Approx Room volume 81 cum.) | 1.00 | Job |  | 308357.00 | 308357.00 | 473630.00 | 473630.00 | 350000.00 | 350000.00 | 402781.20 | 402781.20 | 171000.00 | 171000.00 | 260700.00 | 260700.00 | 171000.00 | DSS Electric Corporation LLP
1.20 | DVOR- UPS ROOM (Approx Room Volume 20 cum.) | 1.00 | Job |  | 127127.00 | 127127.00 | 104600.00 | 104600.00 | 150000.00 | 150000.00 | 186145.00 | 186145.00 | 75000.00 | 75000.00 | 132750.00 | 132750.00 | 75000.00 | DSS Electric Corporation LLP
1.30 | DVOR- ELECTRICAL ROOM (Approx Room Volume 20 cum.) | 1.00 | Job |  | 127127.00 | 127127.00 | 104600.00 | 104600.00 | 150000.00 | 150000.00 | 186145.00 | 186145.00 | 75000.00 | 75000.00 | 132750.00 | 132750.00 | 75000.00 | DSS Electric Corporation LLP
1.40 | DVOR- WORK AREA (Approx Room Volume 56 cum.) | 1.00 | Job |  | 224308.00 | 224308.00 | 292880.00 | 292880.00 | 250000.00 | 250000.00 | 297643.20 | 297643.20 | 112750.00 | 112750.00 | 284850.00 | 284850.00 | 112750.00 | DSS Electric Corporation LLP
1.50 | LOCALIZER- EQUIPMENT ROOM (Approx Room Volume 70 cum.) | 1.00 | Job |  | 404223.00 | 404223.00 | 366100.00 | 366100.00 | 350000.00 | 350000.00 | 361634.60 | 361634.60 | 171000.00 | 171000.00 | 364800.00 | 364800.00 | 171000.00 | DSS Electric Corporation LLP
1.60 | LOCALIZER- ELECTRICAL CUM UPS ROOM (Approx Room Volume 65 cum.) | 1.00 | Job |  | 333308.00 | 333308.00 | 339950.00 | 339950.00 | 350000.00 | 350000.00 | 361634.60 | 361634.60 | 171000.00 | 171000.00 | 345600.00 | 345600.00 | 171000.00 | DSS Electric Corporation LLP
1.70 | GLIDE PATH- EQUIPMENT ROOM (Approx Room Volume 70 cum.) | 1.00 | Job |  | 372705.00 | 372705.00 | 366100.00 | 366100.00 | 350000.00 | 350000.00 | 361634.60 | 361634.60 | 171000.00 | 171000.00 | 364800.00 | 364800.00 | 171000.00 | DSS Electric Corporation LLP
1.80 | GLIDE PATH- ELECTRICAL CUM UPS ROOM (Approx Room Volume 65 cum.) | 1.00 | Job |  | 333308.00 | 333308.00 | 339950.00 | 339950.00 | 350000.00 | 350000.00 | 361634.60 | 361634.60 | 171000.00 | 171000.00 | 345600.00 | 345600.00 | 171000.00 | DSS Electric Corporation LLP
2.00 | Supply, installation testing & commissioning of Conventional agent release control panel with battery back up for 30 minutes in alarm condition having UL/EN/CE Certified approval. Panel shall be of 02 zones with necessary manual release switch, zone indication, fault indication, alarm display. Quoted rate shall include necessary battery & interconnections. | 8.00 | Nos |  | 36705.00 | 293640.00 | 80000.00 | 640000.00 | 30000.00 | 240000.00 | 24000.00 | 192000.00 | 95000.00 | 760000.00 | 35000.00 | 280000.00 | 192000.00 | advent electric technologies pvt. ltd.
3.00 | Supply, installation, testing & commissioning of "DO NOT ENTER/ GAS RELEASED" identification signage. | 8.00 | Nos. |  | 7585.00 | 60680.00 | 9000.00 | 72000.00 | 5000.00 | 40000.00 | 400.00 | 3200.00 | 5000.00 | 40000.00 | 5500.00 | 44000.00 | 3200.00 | advent electric technologies pvt. ltd.
| Total in Figures |  |  |  |  | 2584783.00 |  | 3099810.00 |  | 2580000.00 |  | 2714452.80 |  | 1917750.00 |  | 2555850.00
Lowest Amount Quoted BY: DSS Electric Corporation LLP(1917750.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of Fire Suppression for DVOR, ILS and Unmanned CNS Installations at Rajahmundry Airport Tender ID: 2026_AAI_281783_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | DSS Electric Corporation LLP (BID ID -1043267) | 1917750.00 | L1
| 2 | Nexpo Power Solutions Private Limited (BID ID -1043680) | 2555850.00 | L2
| 3 | CENTRE TAP ENGINEERING (BID ID -1043685) | 2580000.00 | L3
| 4 | Nexus Fire And Security Systems (BID ID -1037921) | 2584783.00 | L4
| 5 | advent electric technologies pvt. ltd. (BID ID -1043811) | 2714452.80 | L5
| 6 | DOSHI ELECTRIC ENGG. CO. (BID ID -1042837) | 3099810.00 | L6