## BoQ1
Government eProcurement System Created By: Preeti Beniwal Created Date/Time: 05-Aug-2026 01:43 PM Tender Title: Construction of Glide Path and Localizer Building and other associated works inside Airforce Area at Chandigarh Airport. SH- SITC of LT panel, Split AC and internal wiring works Tender ID: 2026_AAI_282923_1
Tender Inviting Authority: AGM (Engg. Elect.), AAI, OTB, Chandigarh- 160003.
Name of Work: Construction of Glide Path & Localizer Building and other associated works inside Airforce Area at Chandigarh Airport. SH- SITC of LT panel, Split AC & internal wiring works.
Contract No: 0172-2242404
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ECS ENGINEERING PVT LTD (GSTN-09AABCE5944P1Z1) BID ID -1049086 |  | Awasthi Electric Works (GSTN-09ABAPA1866D1Z5) BID ID -1049168 |  | Yash Energy Pvt. Ltd (GSTN-24AAACY3771H1ZA) BID ID -1049182 |  | ARNAV ENGINEERING CONSULTANCY SERVICES (GSTN-07ABKFA7102Q1Z4) BID ID -1049189
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | SH I :- Internal Electrical Works Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS/HFFR PVC insulated copper conductor single core cable in surface/ recessed steel conduit, with modular switch, modularplate, suitable GI box and earthing the point with 1.5 sq.mm FRLS/HFFR PVC insulated copper conductor single core cable etc. as required.. Group C | 24.00 | Point |  | 2900.00 | 69600.00 | 1700.00 | 40800.00 | 1944.00 | 46656.00 | 1250.00 | 30000.00 | 30000.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
2.00 | Wiring for group controlled (looped) light point/fan point/exhaust fan point/ call bell point (without independent switch etc.) with 1.5 sq. mm FRLS/HFFR PVC insulated copper conductor single core cable in surface/ recessed steel conduit, and earthing the point with 1.5 sq. mm FRLS/HFFR PVC insulated copper conductor single core cable etc. as required.
2.10 | Group A | 26.00 | Point |  | 1250.00 | 32500.00 | 750.00 | 19500.00 | 918.00 | 23868.00 | 750.00 | 19500.00 | 19500.00 | Awasthi Electric Works, ARNAV ENGINEERING CONSULTANCY SERVICES
2.20 | Group C | 8.00 | Point |  | 1800.00 | 14400.00 | 1000.00 | 8000.00 | 918.00 | 7344.00 | 850.00 | 6800.00 | 6800.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
3.00 | Wiring for circuit/ submain wiring along with earth wire with the following sizes of FRLS/HFFR PVC insulated copper conductor, single core cable in surface/ recessed steel conduit as required.
3.10 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | 200.00 | Mtrs. |  | 370.00 | 74000.00 | 250.00 | 50000.00 | 297.00 | 59400.00 | 210.00 | 42000.00 | 42000.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
3.20 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | 500.00 | Mtrs. |  | 461.00 | 230500.00 | 300.00 | 150000.00 | 415.00 | 207500.00 | 385.00 | 192500.00 | 150000.00 | Awasthi Electric Works
3.30 | 2 X 16 sq. mm + 1 X 6 sq. mm earth wire | 60.00 | Mtrs. |  | 1070.00 | 64200.00 | 800.00 | 48000.00 | 961.00 | 57660.00 | 550.00 | 33000.00 | 33000.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
3.40 | 4 X 10 sq. mm + 2 X 6 sq. mm earth wire | 30.00 | Mtrs. |  | 1467.00 | 44010.00 | 1000.00 | 30000.00 | 1328.00 | 39840.00 | 650.00 | 19500.00 | 19500.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
4.00 | Supplying and drawing following sizes of FRLS/HFFR PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
4.10 | 3 x 1.5 sq. mm | 60.00 | Mtrs. |  | 135.00 | 8100.00 | 105.00 | 6300.00 | 162.00 | 9720.00 | 110.00 | 6600.00 | 6300.00 | Awasthi Electric Works
4.20 | 3 x 2.5 sq. mm | 60.00 | Mtrs. |  | 175.00 | 10500.00 | 170.00 | 10200.00 | 226.00 | 13560.00 | 205.00 | 12300.00 | 10200.00 | Awasthi Electric Works
4.30 | 3 x 4 sq. mm | 100.00 | Mtrs. |  | 260.00 | 26000.00 | 265.00 | 26500.00 | 313.00 | 31300.00 | 257.00 | 25700.00 | 25700.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
5.00 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required.
5.10 | 20 mm | 30.00 | Mtrs. |  | 90.00 | 2700.00 | 190.00 | 5700.00 | 48.00 | 1440.00 | 20.00 | 600.00 | 600.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
5.20 | 25 mm | 30.00 | Mtrs. |  | 110.00 | 3300.00 | 220.00 | 6600.00 | 54.00 | 1620.00 | 25.00 | 750.00 | 750.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
5.30 | 32 mm | 30.00 | Mtrs. |  | 140.00 | 4200.00 | 280.00 | 8400.00 | 81.00 | 2430.00 | 30.00 | 900.00 | 900.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
6.00 | Supplying and fixing suitable size GI box with modular plate and cover in front on surface or in recess, including providing and fixing 6 pin 5/6 & 15/16 A modular socket outlet and 15/16 A modular switch, connections etc. as required. | 66.00 | Each |  | 1200.00 | 79200.00 | 600.00 | 39600.00 | 783.00 | 51678.00 | 255.00 | 16830.00 | 16830.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
7.00 | Supplying and fixing of following ways surface/ recess mounting, vertical type, 415 V, TPN MCB distribution board of sheet steel, dust protected, duly powder painted, inclusive of 200 A tinned copper bus bar, common neutral link, earth bar, din bar for mounting MCBs (but without MCBs and incomer ) as required . 8 way (4 + 24), Double door | 2.00 | Each |  | 5375.00 | 10750.00 | 11500.00 | 23000.00 | 6480.00 | 12960.00 | 9500.00 | 19000.00 | 10750.00 | ECS ENGINEERING PVT LTD
8.00 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/Isolator) 12 way, Double door | 4.00 | Each |  | 7190.00 | 28760.00 | 1950.00 | 7800.00 | 3456.00 | 13824.00 | 5500.00 | 22000.00 | 7800.00 | Awasthi Electric Works
9.00 | Supplying and fixing TP sheet steel enclosure on surface/ recess along with 16/25/32 A 415 V "C" curve TP MCB complete with connections, testing and commissioning etc. as required. | 4.00 | Each |  | 1400.00 | 5600.00 | 1350.00 | 5400.00 | 1944.00 | 7776.00 | 1500.00 | 6000.00 | 5400.00 | Awasthi Electric Works
10.00 | Supplying and fixing 5 A to 32 A rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
10.10 | Single Pole | 40.00 | Each |  | 170.00 | 6800.00 | 190.00 | 7600.00 | 302.00 | 12080.00 | 250.00 | 10000.00 | 6800.00 | ECS ENGINEERING PVT LTD
10.20 | Double pole | 40.00 | Each |  | 585.00 | 23400.00 | 600.00 | 24000.00 | 756.00 | 30240.00 | 670.00 | 26800.00 | 23400.00 | ECS ENGINEERING PVT LTD
10.30 | Triple pole and neutral | 4.00 | Each |  | 1287.00 | 5148.00 | 1050.00 | 4200.00 | 1296.00 | 5184.00 | 1450.00 | 5800.00 | 4200.00 | Awasthi Electric Works
11.00 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual current circuit breaker (RCCB), having a sensitivity current 30 mA in the existing MCB DB complete with connections, testing and commissioning etc. as required. 63 A | 2.00 | Each |  | 2956.00 | 5912.00 | 1950.00 | 3900.00 | 3510.00 | 7020.00 | 3500.00 | 7000.00 | 3900.00 | Awasthi Electric Works
12.00 | Supplying and fixing 20 A, 240 V, SPN Industrial type socket outlet, with 2 pole and earth, metal enclosed plug top along with 20 A "C" curve, SP, MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning etc. as required. | 12.00 | Each |  | 2000.00 | 24000.00 | 1600.00 | 19200.00 | 1890.00 | 22680.00 | 440.00 | 5280.00 | 5280.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
13.00 | Supply of following size of 1.1KV grade multicore stranded aluminium conductor XLPE insulated & PVC sheathed armoured cable (FRLS Type) as per IS: 7098 (Part-1) 1988 complete as required & as per enclosed specification. (3.5 x 35 Sqmm) | 200.00 | Meter |  | 300.00 | 60000.00 | 350.00 | 70000.00 | 459.00 | 91800.00 | 375.00 | 75000.00 | 60000.00 | ECS ENGINEERING PVT LTD
14.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL pipe as required. Upto 35 sq. mm | 160.00 | Meter |  | 40.00 | 6400.00 | 55.00 | 8800.00 | 54.00 | 8640.00 | 55.00 | 8800.00 | 6400.00 | ECS ENGINEERING PVT LTD
15.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface as required. Upto 35 sq. mm (clamped with 1mm thick saddle) | 20.00 | Meter |  | 70.00 | 1400.00 | 60.00 | 1200.00 | 59.00 | 1180.00 | 45.00 | 900.00 | 900.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
16.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade as required. 2 X 35 sq. mm (25mm) | 8.00 | Each |  | 300.00 | 2400.00 | 300.00 | 2400.00 | 810.00 | 6480.00 | 450.00 | 3600.00 | 2400.00 | ECS ENGINEERING PVT LTD, Awasthi Electric Works
17.00 | Supply, Installation, Testing and Commissioning of ceiling fan with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. metal( Aluminium alloy) blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, steel/Al body Power Factor not less than 0.9, Service Value 1200mm, service value ≥ 6.0 CM/Min/Watt, air delivery 210 CM/Min (Minimum) | 2.00 | Each |  | 3500.00 | 7000.00 | 3000.00 | 6000.00 | 2593.00 | 5186.00 | 3500.00 | 7000.00 | 5186.00 | Yash Energy Pvt. Ltd
18.00 | Earthing with G.I. earth pipe 4.5 Meter long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 4.00 | Set |  | 12000.00 | 48000.00 | 14500.00 | 58000.00 | 9180.00 | 36720.00 | 6500.00 | 26000.00 | 26000.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
19.00 | Supplying and laying 6 SWG G.I. wire at 0.50 Meter below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | 60.00 | Mtr. |  | 110.00 | 6600.00 | 55.00 | 3300.00 | 97.00 | 5820.00 | 55.00 | 3300.00 | 3300.00 | Awasthi Electric Works, ARNAV ENGINEERING CONSULTANCY SERVICES
20.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode including connection with G.I. thimble excavation and re-filling as required. | 30.00 | Mtr. |  | 210.00 | 6300.00 | 250.00 | 7500.00 | 118.00 | 3540.00 | 60.00 | 1800.00 | 1800.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
21.00 | Supply, Installation, Testing and Commissioning of min. 18-22 W LED Batten light fixture having Extruded aluminium housing with LED's of preferred Make, having THD less than 10%, Efficacy Min 100 lumens/watt, having IP > 20, including driver/control gear, all accessories as required suitable for fixing on existing structure/surface, complying technical specification. | 30.00 | Each |  | 650.00 | 19500.00 | 450.00 | 13500.00 | 810.00 | 24300.00 | 350.00 | 10500.00 | 10500.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
22.00 | Supply, Installation, Testing and Commissioning of 5700 K or more, pressure die cast aluminium housing, LED Street light fixture of 45 W of preferred Make, having THD less than 10%, Efficacy Min 110 lumens/watt, IP more than equal to 65, including driver/control gear, with arrangement for mounting i/c all accessories as required as per site requirement. | 8.00 | Each |  | 2250.00 | 18000.00 | 1850.00 | 14800.00 | 2862.00 | 22896.00 | 4500.00 | 36000.00 | 14800.00 | Awasthi Electric Works
23.00 | SH II:- External Electrical works Outdoor LT Panel:- SITC of PTTA dust & vermin proof outdoor floor mounted distribution electric panel of suitable size on cement concrete foundations generally conforming to IS 5039 and to withstand rough usage and weather. The panel shall be fabricated with 14 SWG M.S. sheet with suitable flat iron frame work complete with hinged door on front with locking arrangement, doors/ covers for individual inside compartments, suitable angle/ channels frame in the bottom, legs for grouting in foundation, painting etc. including supplying and fixing of following accessories and making inter connections, earth connection etc. as required as per attached SLD in TS- 27 of Tender document. (A) INCOMER (1) MCCB,FP, 100 A, 415 V, 36 KA Breaking Capacity, TM release with O/L & S/C Protection - 3 Set ( 02 Nos. for incomer, 01 no common after changeover switch) (B) Automatic Transfer switch :- (1)100A FP Automatic Transfer switch for Source Changeover :- 01 Set (2) ON indication lamp for both source with control MCB :- 01 Set (C) INCOMER from 30 KVA DG set:- (1) MCCB,FP, 63 A, 415 V, 25 KA Breaking Capacity, TM release with O/L & S/C Protection - 1 Set (D) 30 KVA DG AMF START STOP control Part with sutable relay, contctors, MCB, Push bottons, LED indication Lamp etc. required to ON DG set in case of Power failure from output of Auto transfer Switch. :- 1 set alongwith necessary electrical interlocking with incomer 100 A. (E) OUTGOING (1) MCCB,FP, 63 A, 415 V, 25 KA Breaking Capacity, TM release with O/L & S/C Protection - 2 Set (2) MCCB,FP, 32 A, 415 V, 25 KA Breaking Capacity, TM release with O/L & S/C Protection - 2 Set (3) SURGE PROTECTION DEVICE 40KA, TYPE 2- 02 Set (4) DIGITAL Timer Switch :- 1 Set (5) 40 A DP MCB, 10 KA C curve for R-Y-B Phase - 01 set (F) 125 A 4 Pole Aluminium Bus Bar :- 01 Set (G) Suitable size GI Strip throughout the Panel :- 01 set Note :- 1. All Incomming MCCB ( 2+1 ) should be provided with spreader set, Auxillary contacts, rotary handle, Phase, ON, OFF Indication lamps with SP MCB, Digital Multifuntion meter with suitable size of CT, and with Energy meter CL 1 2. All out going MCCB shouuld be be provided with spreader set, Auxillary contacts, rotary handle, ON, OFF Indication lamps with SP MCB. | 2.00 | Job |  | 540000.00 | 1080000.00 | 485000.00 | 970000.00 | 378000.00 | 756000.00 | 355000.00 | 710000.00 | 710000.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
24.00 | SITC of 50 kVA, 3 Phase Air cooled Servo Controlled Automatic Voltage Stabilizer, suitable for operation on 415V, 50Hz AC supply. The stabilizer shall be equiped with Suitable size of Input MCCB, Bypass Switch, Single phase preventer, Over Load and Short circuit Protection etc complete as per site requirement. | 2.00 | Each |  | 180000.00 | 360000.00 | 145000.00 | 290000.00 | 313200.00 | 626400.00 | 95000.00 | 190000.00 | 190000.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
25.00 | SH III:- Split AC Works Supplying , Installation, Testing and Commissioning of Air Cooled Hi Wall 1.5 TR with 5 Star BEE Rating split type Air conditioners complete with Indoor unit(IDU), Out door unit (ODU), surface / concealed copper Refrigerant piping with insulation (closed cell elastomeric nitrile rubber tubular pipe section) upto 3 Mtr (IDU to ODU), copper power cable upto 3.5 Mtr (IDU to ODU) i/c drain pipe R-32/R-410/ R-407 Green Refrigerant, wireless Remote control, suitable for working between 180-260V with low & high voltage cutoff and 50 hz ,1 phase AC supply capable of performing cooling, dehumidification, air circulation of following capacity with Inverter rotary compressor (Variable Speed). The system shall be able to deliver 100% of the rated capacity upto 42 °C. Min 5 year Original Equipment Manufacturer (OEM) warranty both compressor and Printed Circuit Board (PCB). Must comply : Electrical cable IS 694 or IS 9968 temperature sensing control IS /International Electrotechnical Commission (IEC) 60730, hermetic compressor IS 10617, heat exchanger IS 11329, capacitor IS 2993 and motor IS 12615. Complete as per CPWD specification and IS : 1391 Part II 2023. The system shall be able to operate up to 50 °C (out door ambient temperature). This include Provision of plyboard, or a suitable sheet or structure, for the installation of IDUs on frangible hut structures and MS stand for installation of ODU on ground as per site requirement. | 12.00 | Each |  | 58000.00 | 696000.00 | 43000.00 | 516000.00 | 52380.00 | 628560.00 | 48700.00 | 584400.00 | 516000.00 | Awasthi Electric Works
26.00 | SITC of metal-based 5 KVA Automatic Voltage Stabilizer of suitable capacity with high / low cut off complete as reqd. suitable for input voltage range from 150 to 285 volt giving output 175-255 volt at 50 Hz A.C. Supply. The stabilisers should be suitable for 1.5/2 TR ACs as per BOQ Item No. 25. | 12.00 | Each |  | 5000.00 | 60000.00 | 8000.00 | 96000.00 | 12960.00 | 155520.00 | 4800.00 | 57600.00 | 57600.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
27.00 | SITC of Smart AC timer switch for switching power alternatively between two ACs supplied as per BOQ Item No. 25. Timer will be programmable type which is adjustable over 24 hrs with 4-6- 8 hours intervals. This Item include suitable size wiring in between two AC to timer, mounting bracket, painting, sealing, civil finishing etc., complete as required at site. | 6.00 | Each |  | 7000.00 | 42000.00 | 4800.00 | 28800.00 | 8640.00 | 51840.00 | 3200.00 | 19200.00 | 19200.00 | ARNAV ENGINEERING CONSULTANCY SERVICES
| Total in Figures |  |  |  |  | 3187180.00 |  | 2631000.00 |  | 3090662.00 |  | 2242960.00
Lowest Amount Quoted BY: ARNAV ENGINEERING CONSULTANCY SERVICES(2242960.00)

## BOQ Summary
BOQ Summary Details Tender Title: Construction of Glide Path and Localizer Building and other associated works inside Airforce Area at Chandigarh Airport. SH- SITC of LT panel, Split AC and internal wiring works Tender ID: 2026_AAI_282923_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | ARNAV ENGINEERING CONSULTANCY SERVICES (BID ID -1049189) | 2242960.00 | L1
| 2 | Awasthi Electric Works (BID ID -1049168) | 2631000.00 | L2
| 3 | Yash Energy Pvt. Ltd (BID ID -1049182) | 3090662.00 | L3
| 4 | ECS ENGINEERING PVT LTD (BID ID -1049086) | 3187180.00 | L4