## BoQ1
Government eProcurement System Created By: RAVI KUMAR VANKUDOTHU Created Date/Time: 11-Aug-2026 05:55 PM Tender Title: Provision of Apron High Mast Lighting at New Helicopter Apron at Rajahmundry Airport Tender ID: 2026_AAI_283087_1
Tender Inviting Authority: ASST. GENERAL MANAGER (ENGG-ELECT), AIRPORTS AUTHORITY OF INDIA, RAJAHMUNDRY AIRPORT, RAJAHMUNDRY
Name of Work:Provision of Apron Highmast Lighting at New Helicopter Apron at Rajhamundry Airport.
Tender ID No: 2026_AAI_283087_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | HDC Power Systems Pvt Ltd (GSTN-33AABCH1022K1Z4) BID ID -1048655 |  | DOSHI ELECTRIC ENGG. CO. (GSTN-24AAEFD3355K1ZI) BID ID -1049883 |  | BR Power Control and Automation Services (GSTN-06AREPS4024K1ZP) BID ID -1050636 |  | SARASWAT ENGINEERING SERVICES (GSTN-27AAZFS6239C1ZO) BID ID -1050832 |  | TECH-MASTERS (GSTN-NA) BID ID -1049869
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, Fabrication, Supply, Installation, Testing and commissioning of High mast shaft of 12 mtrs in single sections hot galvanized Steel plates confirming to BSEN 10025:1993 suitable for wind speed as per IS:875,part 3 with raising lowering system comprising, head frame, lantern carriage suitable to install Minimum 6 Nos. 250 W LED luminaries in asymmetrical arrangement, double drum winch, 6 mm diameter SS wire rope, Two number 5C X 2.5 Sq.mm tinned unarmoured copper conductor EPR insulated & PVC sheathed trailing cable from Junction Box of lantern carriage to control panel, one number 3CX4 Sq.mm, PVC insulated, PVC sheathed unarmoured Copper conductor cable for Power tool from control panel, connectors, 415 V, 32 A, 3P+N+E Plug & Sockets, integral power tool motor with mechanically tripping facility & manual handle, terminations Junction Box, lightening finial including the followings. High mast tower shall conform to tender specification & as required complete in all respects. Supply of foundation bolts manufactured from special steel along with nuts, washers, anchor plate and common template. Construction of shallow foundation with M25 grade concrete for the highmast considering the safe soil bearing capacity at site as 10 T/sqmtr at 2 meterdepth with all materials and labour. Erection of the high mast including all accessories with the help of suitable tools and plants. Installation, testing and commissioning of 250 W LED Flood lights upto 6No's or as per site requirements and 01 No.Omni directional single Type aviation obstruction light on the existing lantern carriage including wiring of all luminaires with all wiring materials like PVC insulated PVC sheathed flexible cable of suitable copper conductor cores of 2.5 sq. mm from Junction Box of Lantern Carriage to individual light fittings, lugs, mounting accessories and all labour etc. | 3.00 | Job |  | 349000.00 | 1047000.00 | 265000.00 | 795000.00 | 211000.00 | 633000.00 | 262387.00 | 787161.00 | 195650.00 | 586950.00 | 586950.00 | TECH-MASTERS
2.00 | Supply of LED flood light luminaire with secondary optical lens having minimum output of 20000 lm and rated power not exceeding 250 watts with 5 years warranty designed with Powder coated Pressure Die Cast aluminum housing, frame , MS mounting bracket, integral driver with Surge protection, heat resistant toughned glass, Conforming to IP 65/IP66 protection etc. complete as required. (LED & Power Drive Should meet the AAI Specifications) | 40.00 | Each |  | 11000.00 | 440000.00 | 7750.00 | 310000.00 | 6150.00 | 246000.00 | 7260.00 | 290400.00 | 11130.00 | 445200.00 | 246000.00 | BR Power Control and Automation Services
3.00 | Supply of Omni directional single type aviation dome obstruction LED light fitting comprising of aluminum housing and polycarbinate diffuser suitable for operation on 230V;50Hz AC single phase power supply etc. complete as required. | 10.00 | Each |  | 4350.00 | 43500.00 | 4500.00 | 45000.00 | 3521.00 | 35210.00 | 6563.00 | 65630.00 | 4465.00 | 44650.00 | 35210.00 | BR Power Control and Automation Services
4.00 | Design, Fabrication, Supply, Installation, Testing & Commissioning of cubicle type, Totally enclosed, double door with sloped roof, Outdoor type (IP55 or higher), floor mounted, fully CRCA steel built feeder pillar fabricated in compartmentalised design made out of 2.0 mm thick CRCA sheet, duly powder coated in approved shade suitable for operation on 415 V, 3 phase , 4 wire, 50 Hz AC supply, TPN aluminum busbars of high conductivity, DMC/SMC busbar supports with bottom base channel with mounting legs made out of steel section of not less than 3mm thickness, entire panel shall have a common copper earthbar of size 20mm X 3 mm at the rear with 2 Nos. earth studs, solid connection from main busbar to switchgears with required size of aluminum busbar, suitable cement concrete foundation, control wiring with FRLS insulated copper conductor cables, cable alleys , cable gland plates, neoprene gaskets, terminal blocks etc to accommodate the following accessories etc. complete as required. I) Incomer MCCBs : 63 A, FP, Breaking capacity of 25kA at 415 Volts MCCB (Ics= 100% Icu) with Thermal magnetic release having O/L & S/C protection - 1 Set II) LED Phase Indication (R,Y,B) lamps ON&OFF indication lamps with control MCBs & 1.5 Sq.mm FRLS Copper wiring - 01 Set III)Ougoing MCBs : 32 A, 10 KA, 4P, C Series MCB - 4 Nos ( two lighting circuit, one motor circuit & one spare) IV) Common 4 Pole,100A capacity aluminum Busbar. V) Single dial time switch with 32A FP contactor with 2NO+2NC auxiliary contacts for the automatic switching of Highmast flood lighting - 01 Set VI) 32A FP contactor with 2NO+2NC auxiliary contacts for the automatic switching of Highmast flood lighting - 01 Set VII) Power tool Motor control with Two number 32 A, FP contactors with 2NO+2NC auxiliary contacts, Over load protection and Raise & lower push buttons - 0 1Set (for raising lowering system of Highmast). VIII) Remote /Manual operation Selector Switch -01 No. (In Remote Mode, Highmast lighting control from ATC Tower and Manual Mode, highmast Lighting control through manual operation ). IX) Necessary Internal control wiring & earthing strip as per specifications. I/C providing & fixing of suitable Rail Mounted Terminal Connectors etc. | 3.00 | Job |  | 99000.00 | 297000.00 | 90000.00 | 270000.00 | 87280.00 | 261840.00 | 79511.00 | 238533.00 | 170660.00 | 511980.00 | 238533.00 | SARASWAT ENGINEERING SERVICES
5.00 | Design, Supply, Installation, Testing and commissioning of weather proof, vermin proof, powder coated, free floor standing, fully compartmentalised , bottom entry double door type , outdoor canopy type , MV cubicle Electrical Outdoor panel generally conforming to IP-55 and higher , fabricated from 2 mm. thick CRCA sheet , treated through seven tank process along with detachable 3mm thick gland plate suitable for operation on 415 V, 3 phase , 4 wire, 50 Hz AC supply, TPN aluminum busbars of high conductivity, DMC/SMC busbar supports with bottom base channel made out of MS section not less than 100 mm x50 mm x 5 mm thick, entire panel shall have a common copper earthbar of size 20mm X 3 mm at the rear with 2 Nos. earth studs ,solid connection from main busbar to switchgears with required size of aluminum busbar & control wiring with FRLS insulated copper conductor cable, cable alleys, lifting hooks including swapping, recoiling and handling of all incoming and outgoing cables, Civil work for CC foundation, cutting , fixing, grouting, painting and sign writing etc. complete as required. Incomer : 125A, FP,25kA MCCB (Ics=100%Icu) with with O/L and S/C fault Protection with Thermal magnetic release with front operated rotary handle - 01 nos Busbar:150A, Al - Bus bar, Four pole with Fibre glass insulated support & pvc sleave etc-1set Out goings 63A, FP, 25kA MCCB (Ics=100%Icu) with Thermal magnetic release having O/L & S/C protection with rotary handle - 05 Nos Metering: Digital Multifunction meter, 3 phase, 5A, class -1 with CTs (100/5) = 01 set(for incomer). ON-OFF indication lamps (LED type) with Control Fuse/MCB's -6sets LED Phase Indication lamp with control MCBs - 1 Set. | 1.00 | Job |  | 149000.00 | 149000.00 | 185000.00 | 185000.00 | 142500.00 | 142500.00 | 313094.00 | 313094.00 | 272330.00 | 272330.00 | 142500.00 | BR Power Control and Automation Services
6.00 | Supply of following size XLPE insulated PVC sheathed aluminum conductor armoured power cable of 1.1KV grade confirming to IS 7098 (PART-I) with upto date amendments as required. 3.5C X 240 Sq.mm | 500.00 | Mtr. |  | 1450.00 | 725000.00 | 1450.00 | 725000.00 | 1398.00 | 699000.00 | 1471.00 | 735500.00 | 1800.00 | 900000.00 | 699000.00 | BR Power Control and Automation Services
7.00 | Supply of following copper conductor control cable of 1.1 KV grade, XLPE insulated PVC sheathed armoured cable confirming to IS7098, Part-I, 1980 with up to date amendments complete as required. 19 Core X 2.5 Sq.mm (Control Cable) | 500.00 | Mtr. |  | 900.00 | 450000.00 | 800.00 | 400000.00 | 829.00 | 414500.00 | 887.00 | 443500.00 | 1100.00 | 550000.00 | 400000.00 | DOSHI ELECTRIC ENGG. CO.
8.00 | Supply of following copper conductor control cable of 1.1 KV grade, XLPE insulated PVC sheathed armoured cable confirming to IS7098, Part-I, 1980 with up to date amendments complete as required. 8 Core X 2.5 Sq.mm (Control Cable) | 150.00 | Mtr. |  | 450.00 | 67500.00 | 350.00 | 52500.00 | 410.00 | 61500.00 | 406.00 | 60900.00 | 520.00 | 78000.00 | 52500.00 | DOSHI ELECTRIC ENGG. CO.
9.00 | Supply of following size cables of grade 1.1 KV, XLPE insulated, PVC sheathed, armoured aluminum conductor conforming to IS 7098 (Part 1) amended upto date. 4C X 35 Sq mm | 600.00 | Mtr |  | 350.00 | 210000.00 | 300.00 | 180000.00 | 345.00 | 207000.00 | 308.00 | 184800.00 | 380.00 | 228000.00 | 180000.00 | DOSHI ELECTRIC ENGG. CO.
10.00 | Supply and making end termination with brass compression gland and aluminum lugs for XLPE Insulated and PVC sheathed aluminum conductor cable of 1.1 KV grade and sizes as required for the following: 4 C X 35 Sq mm | 12.00 | Set |  | 2500.00 | 30000.00 | 500.00 | 6000.00 | 1510.00 | 18120.00 | 604.00 | 7248.00 | 1730.00 | 20760.00 | 6000.00 | DOSHI ELECTRIC ENGG. CO.
11.00 | Supply and laying of 120 mm dia.(Outer) size, DWC HDPE pipe, ISI marked conforming to IS 14930 Part II with upto date amendments etc as required. | 300.00 | Mtr. |  | 200.00 | 60000.00 | 150.00 | 45000.00 | 252.00 | 75600.00 | 318.00 | 95400.00 | 265.00 | 79500.00 | 45000.00 | DOSHI ELECTRIC ENGG. CO.
12.00 | Supplying of 50 mm dia.(Outer) size, DWC HDPE pipe, ISI marked conforming to IS 14930 Part II with upto date amendments etc as required. | 500.00 | Mtr. |  | 150.00 | 75000.00 | 75.00 | 37500.00 | 69.00 | 34500.00 | 54.00 | 27000.00 | 110.00 | 55000.00 | 27000.00 | SARASWAT ENGINEERING SERVICES
13.00 | Supplying of following size , DWC HDPE pipe, ISI marked conforming to IS 14930 Part II with upto date amendments etc.complete as required. 63mm dia(outer)/50 mm Dia(inner) | 240.00 | Mtr |  | 100.00 | 24000.00 | 90.00 | 21600.00 | 64.00 | 15360.00 | 72.00 | 17280.00 | 115.00 | 27600.00 | 15360.00 | BR Power Control and Automation Services
14.00 | Laying of following size DWC HDPE pipe Complete with all fitting & couplers direct in ground (75 cm below ground level) including excavation and refilling the trench after laying Pipe etc., complete as required. Upto 63mm Dia(outer) | 240.00 | Mtr |  | 100.00 | 24000.00 | 90.00 | 21600.00 | 130.00 | 31200.00 | 149.00 | 35760.00 | 295.00 | 70800.00 | 21600.00 | DOSHI ELECTRIC ENGG. CO.
15.00 | Laying of following size DWC HDPE pipe Complete with all fitting & couplers direct in ground (75 cm below ground level) including excavation and refilling the trench after laying Pipe etc., complete as required. Upto 50mm Dia(outer) | 500.00 | Mtr |  | 100.00 | 50000.00 | 80.00 | 40000.00 | 132.00 | 66000.00 | 149.00 | 74500.00 | 260.00 | 130000.00 | 40000.00 | DOSHI ELECTRIC ENGG. CO.
16.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as reqd. Upto 35 sq. mm | 750.00 | Mtr |  | 100.00 | 75000.00 | 40.00 | 30000.00 | 60.00 | 45000.00 | 45.00 | 33750.00 | 50.00 | 37500.00 | 30000.00 | DOSHI ELECTRIC ENGG. CO.
17.00 | Earthing with G.I. earth pipe of 4 meterlong, 40 mm dia including accessories, and providing 300x300x450(H) mm RCC earth pit chamber suitable to receive 6mm thick MS chequered plate with handle, strengthening & compaction of soil below the earth pit chamber including providing suitable ratio PCC, providing & laying Plain Cement Concrete (PCC) (1:2:4) of depth 100mm surrounding the earth pit chamber covering surface area of 01 SqMeter,including providing and fixing of reducer, water funnel with wire mesh arrangement for watering etc. with charcoal/coke and salt as required. | 14.00 | Job |  | 14000.00 | 196000.00 | 8000.00 | 112000.00 | 12400.00 | 173600.00 | 15551.00 | 217714.00 | 20000.00 | 280000.00 | 112000.00 | DOSHI ELECTRIC ENGG. CO.
18.00 | Providing and fixing 25mm x 5mm GI strip on surface or in recess from earth electrode to electrical panel/Highmast as required. | 20.00 | Mtrs |  | 222.00 | 4440.00 | 175.00 | 3500.00 | 179.00 | 3580.00 | 173.00 | 3460.00 | 165.00 | 3300.00 | 3300.00 | TECH-MASTERS
19.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 Sets of G.I. nut bolt & spring washer spaced at 50mm) | 150.00 | Mtrs |  | 320.00 | 48000.00 | 200.00 | 30000.00 | 215.00 | 32250.00 | 253.00 | 37950.00 | 225.00 | 33750.00 | 30000.00 | DOSHI ELECTRIC ENGG. CO.
20.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing RCC/ HUME/ METAL/HDPE pipe as required. Above 185 sq.mm upto 400Sq.mm | 100.00 | Mtrs |  | 150.00 | 15000.00 | 80.00 | 8000.00 | 140.00 | 14000.00 | 118.00 | 11800.00 | 285.00 | 28500.00 | 8000.00 | DOSHI ELECTRIC ENGG. CO.
21.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size in the existing masonry open duct as required. Above 185 sq.mm upto 400Sq.mm | 200.00 | Mtrs |  | 150.00 | 30000.00 | 60.00 | 12000.00 | 129.00 | 25800.00 | 137.00 | 27400.00 | 295.00 | 59000.00 | 12000.00 | DOSHI ELECTRIC ENGG. CO.
22.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following size on wall surface/Cable Tray as required. as required. Above 185 sq.mm upto 400Sq.mm | 200.00 | Mtrs |  | 150.00 | 30000.00 | 100.00 | 20000.00 | 127.00 | 25400.00 | 160.00 | 32000.00 | 265.00 | 53000.00 | 20000.00 | DOSHI ELECTRIC ENGG. CO.
23.00 | Supply and making end termination with brass compression gland and aluminum lugs for XLPE Insulated and PVC sheathed aluminum conductor cable of 1.1 KV grade and sizes as required for the following. 3.5 C X 240 Sq mm | 2.00 | Set |  | 4000.00 | 8000.00 | 1800.00 | 3600.00 | 2500.00 | 5000.00 | 1916.00 | 3832.00 | 4950.00 | 9900.00 | 3600.00 | DOSHI ELECTRIC ENGG. CO.
24.00 | Supply and making end termination with brass compression gland and aluminum lugs for XLPE Insulated and PVC sheathed aluminum conductor cable of 1.1 KV grade and sizes as required for the following. 4 C X 16 Sq mm | 6.00 | Set |  | 2000.00 | 12000.00 | 300.00 | 1800.00 | 610.00 | 3660.00 | 452.00 | 2712.00 | 1350.00 | 8100.00 | 1800.00 | DOSHI ELECTRIC ENGG. CO.
25.00 | Supply and making end termination with brass compression gland and aluminum lugs for XLPE Insulated and PVC sheathed aluminum conductor cable of 1.1 KV grade and sizes as required for the following. 4 C X 25 Sq mm | 2.00 | Set |  | 2000.00 | 4000.00 | 400.00 | 800.00 | 725.00 | 1450.00 | 499.00 | 998.00 | 950.00 | 1900.00 | 800.00 | DOSHI ELECTRIC ENGG. CO.
| Total in Figures |  |  |  |  | 4114440.00 |  | 3355900.00 |  | 3271070.00 |  | 3748322.00 |  | 4515720.00
Lowest Amount Quoted BY: BR Power Control and Automation Services(3271070.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Apron High Mast Lighting at New Helicopter Apron at Rajahmundry Airport Tender ID: 2026_AAI_283087_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | BR Power Control and Automation Services (BID ID -1050636) | 3271070.00 | L1
| 2 | DOSHI ELECTRIC ENGG. CO. (BID ID -1049883) | 3355900.00 | L2
| 3 | SARASWAT ENGINEERING SERVICES (BID ID -1050832) | 3748322.00 | L3
| 4 | HDC Power Systems Pvt Ltd (BID ID -1048655) | 4114440.00 | L4
| 5 | TECH-MASTERS (BID ID -1049869) | 4515720.00 | L5