## BoQ1
Government eProcurement System Created By: Prabhash Baleshwar Created Date/Time: 18-Aug-2026 01:13 PM Tender Title: SITC of DG Sets and Replacement of old and Conventional AC units and Other Miscellaneous Works at ACS Pratapgarh. Tender ID: 2026_AAI_284370_1
Tender Inviting Authority: AGM (Engg.-Elect.), AAI, M.P. Airport, Udaipur
Name of Work: SITC of DG Sets and Replacement of old & Conventional AC units and Other Miscellaneous Works at ACS Pratapgarh.
Contract No: AAI/UDR/ENGG(E)/2026-27/PG/DG/AC
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | ECS ENGINEERING PVT LTD (GSTN-09AABCE5944P1Z1) BID ID -1054140 |  | Yash Energy Pvt. Ltd (GSTN-24AAACY3771H1ZA) BID ID -1054786
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supplying, Installation, Testing & Commissioning of ‘Silent Type Diesel Generating set as per CPCB IV + or better norms along with having Prime Power Rating of 30 KVA , 415 volts at 1500 RPM, 0.8 lagging power factor at 415 V suitable for 50 Hz, 3 phase system & for 0.85 Load Factor, including testing at factory and site with fuel, load for test and other necessary arrangements Complete as per CPWD specifications, should have QR code which should contain drawing, test report OEM manual, Geo- Tag of manufacturing location, rating plate as per relevant IS Code etc. and consisting of the followings:
1.10 | (A) Diesel Engine: Tourbo charged Diesel engine 4 stroke water cooled, multi cylinder, dynamically balanced fly wheel, electric start of suitable BHP at 1500 RPM suitable for above output of alternator at 40 °C, 50% RH & at 1000 Meter MSL , capable of taking 10% over loading for one hour after 12 hours of continuous operation. The engine will be with Electronic governor, Dry type Air filter with service indicator, first filling of engine fuel (after commissioning) lubricating Oil, Coolant and other consumables complete with all the required accessories, the Electronic governor shall be as per ISO 8528.The engine shall comply to the latest CPCB norms (CPCB IV + or better) and Conforming to BS 5514, BS 649, IS 10000, IS 10002, IS 13018 and as per CPWD specifications. (B) Engine mounted Instrument Panel fitted with and having digital display for following: (i) Start-stop switch with key (ii) Water temperature indication (iii) Lubrication oil pressure indication (iv) Lubrication oil temperature indication (v) Battery charging indication and Voltage indication (vi) RPM indication(vii) Over speed indication (viii) Low lubricantion Oil trip indication(ix) Engine Running Hours indication (x) Fuel Level.
1.20 | (C) Alternator: Synchronous alternator rated at 30 KVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at 40 Degree C, 50% RH & at 1000 Meter MSL. The alternator shall be having Screen Protected Drip Proof (SPDP) enclosure IP23, brushless, continuous duty, dynamically balanced rotor, capable of taking 10% over loading for one hour after 12 hours of continuous operation, self cooled,self-excited and self-regulated through AVR conforming to IS13364(Part 2)/IS: 4722/BS 2613 suitable for tropical conditions and with class- H insulation. (D) Base Frame & Foundation: Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement and vibration isolation arrangement as per recommendations of manufacturer. (E) FUEL TANK :Daily service fuel tank of suitable liters capacity as per CPWD Specifications, fabricated out of 3 mm thick M.S. sheet complete with all standard accessories and fuel piping between fuel tank and diesel engine with MS class ‘C’ pipes of suitable dia. Complete with valves, level indications & accessories as required as per specifications. (F) Exhaust System:Dry exhaust manifold with hospital type exhaust silencer and catalytic convertor.
1.30 | (G) Starting System:12V/24V DC starting system comprising of starter motors: voltage regulator and arrangement for initial excitation complete with suitable numbers of batteries and charger as required as per specifications. The battery shall be housed inside the acoustic enclosure of DG Set. (H) Acoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere and the temperature rise inside the enclosure, noise level outside enclosure. The acoustic enclosure should be suitable for cable connection/connection through bus-trunking. Such arrangements on acoustic enclosure should be water proof & dust-proof conforming to IP-65 protection. The enclosure shall be as per CPCB IV + or better norms etc. and as per CPWD specifications.
1.40 | 30 KVA | 2.00 | No. | 0.00 | 531000.00 | 1062000.00 | 530200.00 | 1060400.00 | 1060400.00 | Yash Energy Pvt. Ltd
2.00 | Providing, installing, testing and commissioning of floor mounted, dust and vermin proof Automatic Mains Failure (AMF) panel for 30 KVA DG Set, fabricated out of 14 SWG CRCA MS sheet, powder coated, complete with gland plate, earthing studs, internal wiring, suitable supports and accessories, comprising of the following: 1. 2 Nos. 4 Pole 63 Amp MCCBs having minimum 25/36 kA breaking capacity, one for mains incomer and one for DG incomer. 2. 2 Nos. 4 Pole 63 Amp AC-3 duty power contactors, one each for mains and DG supply, complete with electrical interlocking arrangement to prevent parallel operation. 3. Copper busbars with heat shrinkable sleeves. 4. Microprocessor based AMF controller for automatic start/stop of DG set, automatic load transfer and restoration, fault monitoring and shutdown. 5. Multifunction digital energy meter for indication of voltage (L-L & L-N), current, frequency, kW, kVA, power factor and kWh complete with 3 Nos. CTs of 75/5A ratio, class-1 accuracy. 6. LED indication lamps for mains available, DG ON, load on mains and load on DG. 7. Auto/Manual/Test/OFF selector switch. 8. Push buttons for start, stop, reset and emergency stop operations. | 2.00 | Each | 0.00 | 217000.00 | 434000.00 | 75000.00 | 150000.00 | 150000.00 | Yash Energy Pvt. Ltd
2.10 | 9. Reverse power relay. 10. Suitable relays, timers, control wiring, control MCBs/fuses and accessories required for automatic operation of DG set. 11. Protection system for over/under voltage, over/under frequency, overload, short circuit, phase failure/reversal, DG fail to start/stop and battery charger failure conditions. 12. Audio visual annunciation for high engine temperature, low lube oil pressure, engine over speed, overload and DG fail to start conditions. 13. Mains failure timer, DG start delay timer, load transfer delay timer, restoration timer and engine cool down timer. 14. RS485/Modbus communication facility with provision for BMS integration and event logging. 15. Complete internal wiring, ferruling, cable termination, interconnection with DG set and LT panel, testing, commissioning and all accessories required for satisfactory operation complete as required.
3.00 | Dismantling & shifting of existing silent type Cummins make 25 KVA DG set assembly including dismantling of canopy (enclosure), cable terminations, batteries, earth strips, silencer , exhaust piping, insulation, cladding of exhaust piping, MS support structure of exhaust pipe etc. using suitable machinery, cutting as required & shifting to new location i.e. Store ( approx distance within 200 mtr) by using sufficient size Hydra Machines i/c loading and unloading at designated place with all the required suitable tools/machinery, without any damages to component & equipment as required. The dismantling is to be done in such a way so the same equipments can be installed at New Location for proper utilization. | 2.00 | Job | 0.00 | 15000.00 | 30000.00 | 11500.00 | 23000.00 | 23000.00 | Yash Energy Pvt. Ltd
4.00 | Excavation in hard rock not exceeding 3 meters in width, and lift upto 3 meters, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 meters. | 20.00 | Cum | 0.00 | 1250.00 | 25000.00 | 1500.00 | 30000.00 | 25000.00 | ECS ENGINEERING PVT LTD
5.00 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 Meter long etc. with charcoal/ coke and salt and refilling with soft soil etc. complete as required. (Excluding Excavation) | 4.00 | Each | 0.00 | 11000.00 | 44000.00 | 7200.00 | 28800.00 | 28800.00 | Yash Energy Pvt. Ltd
6.00 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 Meter long etc. with charcoal/ coke and salt and refilling with soft soil etc. complete as required. (Excluding Excavation) | 4.00 | Set | 0.00 | 27900.00 | 111600.00 | 21810.00 | 87240.00 | 87240.00 | Yash Energy Pvt. Ltd
7.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Meter | 0.00 | 550.00 | 11000.00 | 610.00 | 12200.00 | 11000.00 | ECS ENGINEERING PVT LTD
8.00 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections etc. as required. | 30.00 | Meter | 0.00 | 2100.00 | 63000.00 | 1950.00 | 58500.00 | 58500.00 | Yash Energy Pvt. Ltd
9.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 30.00 | Meter | 0.00 | 215.00 | 6450.00 | 167.00 | 5010.00 | 5010.00 | Yash Energy Pvt. Ltd
10.00 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode including connection with brass nut, bolt, spring, washer excavation and re-filling etc. as required. | 20.00 | Meter | 0.00 | 2950.00 | 59000.00 | 2380.00 | 47600.00 | 47600.00 | Yash Energy Pvt. Ltd
11.00 | Supply and making end termination with brass compression glade and aluminium lugs for PVC insulated and PVC sheathed/XLPE AI. Conductor cable of 1.1 KV grade of size 3.5 X 50 Sqmm as required | 12.00 | Set | 0.00 | 600.00 | 7200.00 | 2565.00 | 30780.00 | 7200.00 | ECS ENGINEERING PVT LTD
12.00 | Supply and fixing exhaust gas piping of 80mm dia. Welded black MS, B class pipe conforming to IS: 3589 cut to required lengths and installed with necessary bends, supports and clamps, insulation of exhaust system with mineral wool/ Rockwool density not lessthen 48 kg per Cu.mtr. & thickness 50 mm with thick wire mesh & aluminum cladding etc., as required as per specifications. | 12.00 | Meter | 0.00 | 3000.00 | 36000.00 | 5165.00 | 61980.00 | 36000.00 | ECS ENGINEERING PVT LTD
13.00 | Supply of Power/Control Copper Cables, Stranded Copper, XLPE Insulated, cores laid up, PVC Innersheathed, Armoured, extruded PVC Type ST2 Outer Sheathed, 650/1100 V grade as per IS 7098 Part-I 1988.
13.10 | 12 C X 1.5 Sq.mm. | 20.00 | Meter | 0.00 | 360.00 | 7200.00 | 800.00 | 16000.00 | 7200.00 | ECS ENGINEERING PVT LTD
14.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV grade of following on existing cable tray as required.
14.10 | Up to 35 Sq. mm (clamped with 1 mm thick saddle). | 20.00 | Meter | 0.00 | 75.00 | 1500.00 | 75.00 | 1500.00 | 1500.00 | ECS ENGINEERING PVT LTD, Yash Energy Pvt. Ltd
15.00 | Supply of 5 Star BEE Rated Air Cooled Hi-Wall Split Inverter Type Air Conditioner of 1.5 TR capacity, complete with indoor unit, outdoor unit, wireless remote control, suitable for operation on 180-260 volts, 50 Hz, single phase supply, capable of cooling, dehumidification and air circulation, fitted with rotary/scroll compressor and suitable for operation up to 50°C ambient temperature, delivering rated capacity up to 42°C. The unit shall comply with IS 1391 (Part-II):2023 and relevant IS/IEC standards for compressor, motor, capacitor, temperature control and associated components, with minimum 5 years OEM warranty on compressor and PCB. | 6.00 | Each | 0.00 | 51000.00 | 306000.00 | 41310.00 | 247860.00 | 247860.00 | Yash Energy Pvt. Ltd
16.00 | ITC of 1.5 TR Split airconditioners including surface/concealed copper refrigerant piping with closed cell elastomeric nitrile rubber insulation up to 3 metre, copper power cable up to 3.5 metre, drain pipe, R-32 refrigerant as per site requirement between condenser and evaporator unit etc. as required related civil works and including first charge of refrigerant &providing & fixing of Iron stand for outdoor unit etc. complete as required. | 6.00 | Each | 0.00 | 2500.00 | 15000.00 | 2870.00 | 17220.00 | 15000.00 | ECS ENGINEERING PVT LTD
17.00 | SITC of extra length of copper pipe for quantity in excess of 3 metres which is already taken in item no.16 (suction & discharge together)as per design of OEM between condenser and evaporator unit enclosing in with nitrile rubber insulation including wrapping in white vinyl tape etc. as required | 30.00 | Meter | 0.00 | 820.00 | 24600.00 | 300.00 | 9000.00 | 9000.00 | Yash Energy Pvt. Ltd
18.00 | SITC of extra length of drain pipe for quantity in excess of 3 metres from evaporator to a suitable location as per design of OEM etc as required. | 30.00 | Meter | 0.00 | 210.00 | 6300.00 | 242.00 | 7260.00 | 6300.00 | ECS ENGINEERING PVT LTD
19.00 | Supply and fixing of cyclic timers for 1.5 Tr Split Air conditioners for single phase 230 volt, 50Hz AC supply. | 3.00 | Each | 0.00 | 4850.00 | 14550.00 | 4000.00 | 12000.00 | 12000.00 | Yash Energy Pvt. Ltd
20.00 | SITC of voltage stablizer for Inverter type AC units with operating AC voltage range of 160V to 280V with low/high voltage cut off, fail safe protection, built - in thermal overload protection etc. complete as required. (Make: Vguard model : i4 Dura 2040 Stabilizer or equivalent) | 6.00 | Each | 0.00 | 4450.00 | 26700.00 | 3900.00 | 23400.00 | 23400.00 | Yash Energy Pvt. Ltd
21.00 | Dismantling of existing old 1.5 TR Split AC Units alongwith refrigerant piping ,mounting arrangements with all accessories, fitting etc. i/c shifting of the dismantled AC units to AAI store complete as required as per the direction of EIC. | 6.00 | Job | 0.00 | 2000.00 | 12000.00 | 700.00 | 4200.00 | 4200.00 | Yash Energy Pvt. Ltd
22.00 | SITC of Floor Mounted self contained, storage type drinking water cooler suitable for operation on 230V, 50 Hz AC supply confirming to IS 1475 (Part 1): 2001 with amendment and having nominal cooling capacities of 40 Litre / Hour at ambient temperature of 35 C complete with hermitically sealed compressors of reputed brand, thermostat, fan motor, PUF insulated water storage tank of capacity - 80 Litre made of stainless steel body (SS-304) etc. complete as required. | 2.00 | Each | 0.00 | 45000.00 | 90000.00 | 49500.00 | 99000.00 | 90000.00 | ECS ENGINEERING PVT LTD
23.00 | SITC of 50 LPH capacity Reverse Osmosis (RO) system having 50 LPH flow rate with sediment filter , activated carbon filter,micron filters, pressure pump etc. complete with high & low pressure safety, pre-piped, pre-wired and housed in a well-designed cabin modeled mild steel epoxy painted or P U coated / stainless steel skid i/c attachment with existing water cooler complete as required. | 1.00 | Each | 0.00 | 34500.00 | 34500.00 | 45500.00 | 45500.00 | 34500.00 | ECS ENGINEERING PVT LTD
24.00 | SITC of 10 KVA, Single-Phase Automatic Voltage Stabilizer (AVR) with the following Capacity: 10 KVA, Cooling: Air-cooled , Input Voltage Range: 140V– 270V, Output Voltage: Stable 230V ±1%, Technology: Servo-controlled with Overload, short circuit and surge protection, Digital display , MS (CRCA) Powder Coated Sheet Steel Cabinet, Servo motor-controlled variable transformer, Ventilated with fans complete as required. | 2.00 | Each | 0.00 | 54000.00 | 108000.00 | 34500.00 | 69000.00 | 69000.00 | Yash Energy Pvt. Ltd
| Total in Figures |  |  |  |  | 2535600.00 |  | 2147450.00
Lowest Amount Quoted BY: Yash Energy Pvt. Ltd(2147450.00)

## BOQ Summary
BOQ Summary Details Tender Title: SITC of DG Sets and Replacement of old and Conventional AC units and Other Miscellaneous Works at ACS Pratapgarh. Tender ID: 2026_AAI_284370_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | Yash Energy Pvt. Ltd (BID ID -1054786) | 2147450.00 | L1
| 2 | ECS ENGINEERING PVT LTD (BID ID -1054140) | 2535600.00 | L2