## BoQ1
Government eProcurement System Created By: Ved Bhushan Created Date/Time: 10-Sep-2026 02:36 PM Tender Title: Provision of Apron Flood Light and associated works at Civil Airport, Jaisalmer. Tender ID: 2026_AAI_284371_1
Tender Inviting Authority: Sr. Manager (Engg.-Elect.)
Name of Work: Provision of Apron Flood Light and associated works at Civil Airport, Jaisalmer.
Contract No: 2026_AAI_284371_1
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | R S ELECTRICALS (GSTN-09AALFR7080G1ZS) BID ID -1053810 |  | BR Power Control and Automation Services (GSTN-06AREPS4024K1ZP) BID ID -1053986 |  | METRO ENGINEERS SERVICES (GSTN-08AUHPK7216R1ZT) BID ID -1054120 |  | SYNERGY LIGHTING SOLUTIONS (GSTN-NA) BID ID -1053778 |  | M/s MANNU ENTERPRISES (GSTN-NA) BID ID -1053951
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Design, fabrication & Supply of 11 Mtr height High mast system complete with all accessories, as per the specificaitons. Mast shall be in two sections, hot dip galvanised and suitable for wind velocity as per IS 875 part 3. It shall also include accessories for high mast including head frame, suitable suspension system with steel wire rope 6mm dia (7/19 construction), multicore trailing cable, double drum winch, Galvanised Lantern carriage arrangement suitable for upto 05 luminaries (250 W LED) as per detailed design and lightning finial. The mast shall have an integral electrically operated power tool installed inside the base compartment with raising and lowering mechanism for lantern carraige etc.complete as required as per specifications of the contract. | 3.00 | Each | 2487.00 | 140000.00 | 420000.00 | 108611.00 | 325833.00 | 135000.00 | 405000.00 | 200000.00 | 600000.00 | 156000.00 | 468000.00 | 325833.00 | BR Power Control and Automation Services
2.00 | Design, fabrication & Supply of 12 Mtr height High mast system complete with all accessories, as per the specificaitons. Mast shall be in two sections, hot dip galvanised and suitable for wind velocity as per IS 875 part 3. It shall also include accessories for high mast including head frame, suitable suspension system with steel wire rope 6mm dia (7/19 construction), multicore trailing cable, double drum winch, Galvanised Lantern carriage arrangement suitable for upto 07 luminaries (250 W LED) as per detailed design and lightning finial. The mast shall have an integral electrically operated power tool installed inside the base compartment with raising and lowering mechanism for lantern carraige etc.complete as required as per specifications of the contract. | 3.00 | Each | 3047.00 | 150000.00 | 450000.00 | 117276.00 | 351828.00 | 145000.00 | 435000.00 | 225000.00 | 675000.00 | 167000.00 | 501000.00 | 351828.00 | BR Power Control and Automation Services
3.00 | Design and construction of suitable shallow RCC foundation with 1:1.5:3 (1 cement,1.5 coarse sand,3 graded stone aggregate) concrete for the high masts mentioned in item No.1 & 2 considering the safe soil bearing capacity at site as 10 T/sq mtr. 2 meters depth, with foundation bolts of suitable size as per approved design and manufactured from special steel alongwith nuts, washers, suitable size anchor plates and templates etc.complete as required. 11 Mtr height | 3.00 | Job | 3357.00 | 70000.00 | 210000.00 | 111075.00 | 333225.00 | 45000.00 | 135000.00 | 10000.00 | 30000.00 | 69000.00 | 207000.00 | 30000.00 | SYNERGY LIGHTING SOLUTIONS
4.00 | Design and construction of suitable shallow RCC foundation with 1:1.5:3 (1 cement,1.5 coarse sand,3 graded stone aggregate) concrete for the high masts mentioned in item No.1 & 2 considering the safe soil bearing capacity at site as 10 T/sq mtr. 2 meters depth, with foundation bolts of suitable size as per approved design and manufactured from special steel alongwith nuts, washers, suitable size anchor plates and templates etc.complete as required. 12 Mtr height | 3.00 | Job | 27080.00 | 70000.00 | 210000.00 | 114834.00 | 344502.00 | 55000.00 | 165000.00 | 10000.00 | 30000.00 | 75600.00 | 226800.00 | 30000.00 | SYNERGY LIGHTING SOLUTIONS
5.00 | Erection, testing and commissioning of following high mast system along with all accessories, flood light fittings, lightning finial and necessary cablings, wirings and junction boxes etc.complete as required on the existing foundation. 11 Mtr height in two section | 3.00 | Job | 3037.00 | 30000.00 | 90000.00 | 23000.00 | 69000.00 | 25000.00 | 75000.00 | 10000.00 | 30000.00 | 16500.00 | 49500.00 | 30000.00 | SYNERGY LIGHTING SOLUTIONS
6.00 | Erection, testing and commissioning of following high mast system along with all accessories, flood light fittings, lightning finial and necessary cablings, wirings and junction boxes etc.complete as required on the existing foundation. 12 Mtr height in two section | 3.00 | Job | 3171.00 | 30000.00 | 90000.00 | 25300.00 | 75900.00 | 25000.00 | 75000.00 | 10000.00 | 30000.00 | 16800.00 | 50400.00 | 30000.00 | SYNERGY LIGHTING SOLUTIONS
7.00 | Supply, installation, testing & commissioning of Nominal 250 W outdoor LED luminaries having > 120 Lumen/Watt light output with IP-66 pressure die cast aluminium alloy housing with impact resistance of IK08 and heat resistant toughened glass cover suitable for High Mast with LED lamp, drivers, connectors as per design criteria mentioned in technical specifications of contract etc.complete as required. | 88.00 | Each | 3109.00 | 10500.00 | 924000.00 | 8693.00 | 764984.00 | 15500.00 | 1364000.00 | 6900.00 | 607200.00 | 8200.00 | 721600.00 | 607200.00 | SYNERGY LIGHTING SOLUTIONS
8.00 | Supply, installation, testing & commissioning of LED type single dome aviation obstruction light complete in all aspect as required. | 6.00 | Each | 106.00 | 6500.00 | 39000.00 | 7067.00 | 42402.00 | 4500.00 | 27000.00 | 4000.00 | 24000.00 | 2870.00 | 17220.00 | 17220.00 | M/s MANNU ENTERPRISES
9.00 | Design, Fabrication, Supply, Installation, Testing & Commissioning of floor mounting, totally enclosed , compartmentalized, cubical, vermin proof, outdoor type panel (IP 66) suitable for 415V, 3 phase, 4 wire, 50Hz AC supply system fabricated from CRCA steel sheet of 2mm thick for frame work & 3mm for cable gland plate, entire panel shall have a common GI earth bar of size 25 mm X 5mm at the rear with 2 nos earth stud, finishing complete with power coating in approved shade, bottom base channel of MS section not less than 50mm x 50mm x 5mm thick, solid connections from main bus bar to switch gears with required suitable size of Aluminium busbars and control wiring with 2.5 sqmm FRLSH PVC insulated copper conductor cable, cable alleys, cable gland plates including providing folling switch gears etc. complete as required. This will include erection of the panel on suiable size MS frame foundation duly grouted in ground with cement and concrete. Complete in all respect as per CPWD specification with following in coming and Outgoings as required : INCOMER: a) 200A, 4P, 36kA, MCCBs (Ics=100%Icu),with thermal magnetic release, O/L, S/C & E/F protection along with incomer bus coupler with extendable ON/OFF rotary handle: 02 nos. b) Bus Coupler 200A, 4P, MCCBs (Ics=100%Icu), 36 kA with extendable ON/OFF rotary handle - 01 No. c) ON/ OFF indication Lamp - 2 Set d) (0-500 V) Digital Voltmeter with selector switch - 2 Set e) (0-200 A) Digital Ammeter with selector switch & CTs - 2 Set f) Indication lamp R/Y/B with backup MCB - 2 Set of Three Bus Bar: a) 4-Pole Aluminium Bus bar of 200 A rating of high conductivity with heat shrinkable, coloured sleeves, required intervals complete for cross section, size supports and their spacing etc as per specification. OUTGOING: a) 63A, 4P, 25kA, MCCBs (Ics=100%Icu), with Thermal Magnetic release, O/L, S/C protection etc. : 02 nos. b) 32A, 4 Pole, 10 kA, C curve, MCBs with all acceessories and internal wiring etc as required: 10 nos. (including spares) (Note : All outgoings should have LED type ON, OFF, trip indicating lamps) | 1.00 | Job | 44.00 | 210000.00 | 210000.00 | 261000.00 | 261000.00 | 455000.00 | 455000.00 | 195000.00 | 195000.00 | 119900.00 | 119900.00 | 119900.00 | M/s MANNU ENTERPRISES
10.00 | Design, manufacturing, supply, installation, testing and commissioning of cubical type totally enclosed free standing, dust free, damp and vermin proof and water proof double door outdoor (IP 66) feeder pillar fabricated out of 2mm thick CRCA sheet duly powder coated and including supply and fixing of the following items and interconnections,wiring with suitable sizes wires/cables and including mounting legs, all civil works (feeder pillar foundation) like excavation, PCC,brick work pedestal, plastering, refilling etc. and as per specification as required. a) 01 No. 32 Amps, TPN MCCB (Ics=Icu=25 kA) with rotary operating mechanism b) 01 No 32 Amps TP Contactor c) 01 No. Timer (24 hrs) d) 01 No. Auto/mannual selector switch e) 04 Set RYB, ON LED Indication lamp f) 02 Nos 12A (AC 3 rating) Contactor with overload relay for motor g) 02 Nos UP/Down push button h) 02 Nos 16A DP MCB i) 01 No. Digital Voltmeter (0-500 Volts) Class 1 with in built selector switch j) 01 No. Digital Ammeter alongwith suitable range CT's k) Control MCB, Connector strips, Potential free contact for remote operation, Dinbar etc as per requirement. | 6.00 | Job | 10372.00 | 70000.00 | 420000.00 | 100686.00 | 604116.00 | 38000.00 | 228000.00 | 25000.00 | 150000.00 | 79000.00 | 474000.00 | 150000.00 | SYNERGY LIGHTING SOLUTIONS
11.00 | Supply of following sizes of XLPE insulated PVC sheathed, Aluminium conductor armoured electric cable of 1.1 KV grade confirming to IS 7098 PART-I with upto date amended. 4 C x 16 Sq. mm | 50.00 | Mtr. | 5863.00 | 260.00 | 13000.00 | 196.00 | 9800.00 | 205.00 | 10250.00 | 300.00 | 15000.00 | 179.00 | 8950.00 | 8950.00 | M/s MANNU ENTERPRISES
12.00 | Supply of following sizes of XLPE insulated PVC sheathed, Aluminium conductor armoured electric cable of 1.1 KV grade confirming to IS 7098 PART-I with upto date amended. 3.5 C x 25 Sq. mm | 1752.00 | Mtr. | 33907.00 | 290.00 | 508080.00 | 202.00 | 353904.00 | 225.00 | 394200.00 | 400.00 | 700800.00 | 245.00 | 429240.00 | 353904.00 | BR Power Control and Automation Services
13.00 | Supply of following sizes of XLPE insulated PVC sheathed, Aluminium conductor armoured electric cable of 1.1 KV grade confirming to IS 7098 PART-I with upto date amended. 3.5 C x 50 Sq. mm | 350.00 | Mtr. | 11478.00 | 490.00 | 171500.00 | 350.00 | 122500.00 | 335.00 | 117250.00 | 670.00 | 234500.00 | 410.00 | 143500.00 | 117250.00 | METRO ENGINEERS SERVICES
14.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. 4 C x 16 Sq. mm | 12.00 | Set | 14389.00 | 250.00 | 3000.00 | 818.00 | 9816.00 | 85.00 | 1020.00 | 100.00 | 1200.00 | 245.00 | 2940.00 | 1020.00 | METRO ENGINEERS SERVICES
15.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. 3.5 C x 25 Sq. mm | 12.00 | Set | 205.00 | 300.00 | 3600.00 | 1026.00 | 12312.00 | 85.00 | 1020.00 | 150.00 | 1800.00 | 325.00 | 3900.00 | 1020.00 | METRO ENGINEERS SERVICES
16.00 | Supplying and making end termination with brass compression gland and aluminium lugs for following size of PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 kV grade as required. 3.5 C x 50 Sq. mm | 2.00 | Set | 1769.00 | 350.00 | 700.00 | 1210.00 | 2420.00 | 85.00 | 170.00 | 200.00 | 400.00 | 378.00 | 756.00 | 170.00 | METRO ENGINEERS SERVICES
17.00 | Supplying and laying of 63 mm dia (OD-63 mm & ID-51 mm nominal) size DWC HDPE pipe ISI marked along with all accessories like socket, bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc. in the existing trench, complete as required. | 2152.00 | Mtr. | 102.00 | 140.00 | 301280.00 | 194.00 | 417488.00 | 96.00 | 206592.00 | 140.00 | 301280.00 | 80.00 | 172160.00 | 172160.00 | M/s MANNU ENTERPRISES
18.00 | Excavation of the cable trenches in hard rock not exceeding 1.5 meters in width, and lift upto 1.5 meters, including getting out the excavated soil and disposal of excavated soil as directed within a lead of 50 meters. | 404.00 | Cum | 226.00 | 1100.00 | 444400.00 | 1438.00 | 580952.00 | 550.00 | 222200.00 | 120.00 | 48480.00 | 6250.00 | 2525000.00 | 48480.00 | SYNERGY LIGHTING SOLUTIONS
19.00 | Breaking/demolishing of hard concrete surface at apron area using hammer/stone breaker and making removing of debris and cleaning to form rectagular shaped groove/chamber/ trench getting out the excavated soil, disposal of surplus excavated debris soil as directed, within a lead of 50 metres. per the direction of EIC. | 6.75 | Cum | 441.00 | 900.00 | 6075.00 | 17825.00 | 120318.75 | 5500.00 | 37125.00 | 5000.00 | 33750.00 | 6450.00 | 43537.50 | 6075.00 | R S ELECTRICALS
20.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC/ HUME/ METAL/DWC pipe as required. Upto 35 sq. mm | 1442.00 | Mtr. | 154.00 | 40.00 | 57680.00 | 75.00 | 108150.00 | 150.00 | 216300.00 | 10.00 | 14420.00 | 133.00 | 191786.00 | 14420.00 | SYNERGY LIGHTING SOLUTIONS
21.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 kV grade of following size in the existing RCC/ HUME/ METAL/DWC pipe as required. Above 35 sq. mm and upto 95 sq. mm | 280.00 | Mtr. | 129.00 | 50.00 | 14000.00 | 92.00 | 25760.00 | 150.00 | 42000.00 | 15.00 | 4200.00 | 168.00 | 47040.00 | 4200.00 | SYNERGY LIGHTING SOLUTIONS
22.00 | Earthing with G.I. earth pipe 4.5 Meter long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal/ coke and salt as required. | 14.00 | Each | 241.00 | 7000.00 | 98000.00 | 15507.00 | 217098.00 | 5500.00 | 77000.00 | 3000.00 | 42000.00 | 4700.00 | 65800.00 | 42000.00 | SYNERGY LIGHTING SOLUTIONS
23.00 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 Eachs of G.I. nut bolt & spring washer spaced at 50mm) | 35.00 | Meter | 203.00 | 350.00 | 12250.00 | 233.00 | 8155.00 | 155.00 | 5425.00 | 250.00 | 8750.00 | 250.00 | 8750.00 | 5425.00 | METRO ENGINEERS SERVICES
24.00 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, spring, washer excavation and re-filling etc. as required. | 70.00 | Meter | 348.00 | 900.00 | 63000.00 | 279.00 | 19530.00 | 205.00 | 14350.00 | 600.00 | 42000.00 | 560.00 | 39200.00 | 14350.00 | METRO ENGINEERS SERVICES
25.00 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I wire in 15 mm dia G.I pipe from earth electrode including connection with G.I thimble excavation and refilling as required. | 50.00 | Meter | 57.00 | 250.00 | 12500.00 | 53.00 | 2650.00 | 55.00 | 2750.00 | 150.00 | 7500.00 | 37.00 | 1850.00 | 1850.00 | M/s MANNU ENTERPRISES
26.00 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections etc. as required. | 50.00 | Meter | 1015.00 | 300.00 | 15000.00 | 241.00 | 12050.00 | 205.00 | 10250.00 | 120.00 | 6000.00 | 220.00 | 11000.00 | 6000.00 | SYNERGY LIGHTING SOLUTIONS
27.00 | Design and construction of RCC foundation with 1:1.5:3 (1 cement,1.5 coarse sand,3 graded stone aggregate) concrete for the existing 23 mtr height high mast including excavation and refilling etc. along with supply of foundation bolts, nuts, washers, suitable size anchor plates and templates etc.complete in all aspect as required as per instruction of Engg. In Charge. | 1.00 | Job | 3285.00 | 125000.00 | 125000.00 | 138000.00 | 138000.00 | 105000.00 | 105000.00 | 15000.00 | 15000.00 | 135000.00 | 135000.00 | 15000.00 | SYNERGY LIGHTING SOLUTIONS
28.00 | Erection, testing and commissioning of existing 23mtr height high mast system along with all accessories, all flood light fittings, lightning finial, aviation lights and necessary cablings, wirings and junction boxes etc.complete at desired location complete as required on the foundation complete in all aspect as required as per instruction of Engg. In Charge. | 1.00 | Job | 8006.00 | 50000.00 | 50000.00 | 143750.00 | 143750.00 | 85000.00 | 85000.00 | 15000.00 | 15000.00 | 22000.00 | 22000.00 | 15000.00 | SYNERGY LIGHTING SOLUTIONS
29.00 | Installation, connection, testing, commissioning of existing outdoor feeder piller of high mast including replacement of digital timer, contactor, pair of push button, A/M switch etc for smooth and efficient auto and manual operation of high mast system up to satisfaction of Engg. In Charge. | 1.00 | Job | 17656.00 | 20000.00 | 20000.00 | 27025.00 | 27025.00 | 10000.00 | 10000.00 | 2000.00 | 2000.00 | 7800.00 | 7800.00 | 2000.00 | SYNERGY LIGHTING SOLUTIONS
30.00 | Supply of following rating, 415 V, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Four Pole, 25 A | 15.00 | Each | 20529.00 | 1500.00 | 22500.00 | 1792.00 | 26880.00 | 2500.00 | 37500.00 | 1500.00 | 22500.00 | 870.00 | 13050.00 | 13050.00 | M/s MANNU ENTERPRISES
31.00 | Supply of following rating, 415 V, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Four Pole, 40 A | 20.00 | Each | 360.00 | 2000.00 | 40000.00 | 2247.00 | 44940.00 | 3000.00 | 60000.00 | 1600.00 | 32000.00 | 1600.00 | 32000.00 | 32000.00 | SYNERGY LIGHTING SOLUTIONS, M/s MANNU ENTERPRISES
32.00 | Supply of following rating, 415 V, 10 kA, “C” curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. Four Pole, 63 A | 10.00 | Each | 360.00 | 2000.00 | 20000.00 | 2482.00 | 24820.00 | 3000.00 | 30000.00 | 1700.00 | 17000.00 | 1887.00 | 18870.00 | 17000.00 | SYNERGY LIGHTING SOLUTIONS
33.00 | Supply of 40 A rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current 30 milli amperes in the existing MCB DB complete with connections, testing and commissioning etc. as required. | 30.00 | Each | 743.00 | 3000.00 | 90000.00 | 2723.00 | 81690.00 | 3500.00 | 105000.00 | 2100.00 | 63000.00 | 2430.00 | 72900.00 | 63000.00 | SYNERGY LIGHTING SOLUTIONS
34.00 | Supply of indoor type glare free surface mount 3600 (minimum) lumens, efficacy of 100 lumens/watt (min) LED Batten Tube light fixture (T5), 4 feet length of approved make LED light fixtures with LED Drivers. LED shall be of Mini. of impact resistance of IK04 rating, THD less than 10% complete with all fixing accessories suitable for operation on 230 volts, 50 Hz, single phase, A.C. supply complete in all respects as required as per site conditions. | 40.00 | Each | 30000.00 | 800.00 | 32000.00 | 1662.00 | 66480.00 | 1500.00 | 60000.00 | 600.00 | 24000.00 | 545.00 | 21800.00 | 21800.00 | M/s MANNU ENTERPRISES
35.00 | Supply of outdoor type LED street light made up of pressure die cast aluminium housing with high efficiency LED as lighting source and lens embedded PC cover having Bottom Opening seperate driver compartment with IP66 protection and impact resistance of IK08 supplied along with 1.5 mtr GI bracket. LED light fitting shall be of 70 Watt with luminaire efficacy of not less than 120 lm/W and lumen maintainence ot 70% at the end of 50000 burning hours with constant current driver output, operating range 150V - 270V, 50Hz AC supply, CCT of 5700K-6500K with PF>0.95 and THD must be <10% & surge protection of > 2.5 kV complete in all respects as required as per site conditions. | 25.00 | Each | 15750.00 | 4800.00 | 120000.00 | 6404.00 | 160100.00 | 3500.00 | 87500.00 | 3500.00 | 87500.00 | 2870.00 | 71750.00 | 71750.00 | M/s MANNU ENTERPRISES
36.00 | Supply, installation, testing and commissioning of industrial type heavy duty 380 mm dia, 1400 RPM, 3250 CMH Air flow capacity, Epoxy Powder Coated MS body exhaust fan with provision of suitable rustproof heavy duty GI louvers (powder-coated CRCA steel frames and galvanized iron flaps) and all accessories suitable for operation on 230 V, 50 Hz single phase AC supply etc. complete as required in all respect and as per directions of EIC. | 18.00 | Each | 15750.00 | 6000.00 | 108000.00 | 6699.00 | 120582.00 | 4500.00 | 81000.00 | 3500.00 | 63000.00 | 1876.00 | 33768.00 | 33768.00 | M/s MANNU ENTERPRISES
37.00 | Supply of handheld digital lux meter having range 0 to 200000 lux with resolution of 0.1 lux powered by 9 Volt battery (Similar to Meco make - Digital lux meter 930P or equivalent). | 1.00 | Each | 28770.00 | 5000.00 | 5000.00 | 5698.00 | 5698.00 | 15000.00 | 15000.00 | 4000.00 | 4000.00 | 1760.00 | 1760.00 | 1760.00 | M/s MANNU ENTERPRISES
| Total in Figures |  |  |  |  | 5419565.00 |  | 6035658.75 |  | 5397902.00 |  | 4178280.00 |  | 6961527.50
Lowest Amount Quoted BY: SYNERGY LIGHTING SOLUTIONS(4178280.00)

## BOQ Summary
BOQ Summary Details Tender Title: Provision of Apron Flood Light and associated works at Civil Airport, Jaisalmer. Tender ID: 2026_AAI_284371_1
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | SYNERGY LIGHTING SOLUTIONS (BID ID -1053778) | 4178280.00 | L1
| 2 | METRO ENGINEERS SERVICES (BID ID -1054120) | 5397902.00 | L2
| 3 | R S ELECTRICALS (BID ID -1053810) | 5419565.00 | L3
| 4 | BR Power Control and Automation Services (BID ID -1053986) | 6035658.75 | L4
| 5 | M/s MANNU ENTERPRISES (BID ID -1053951) | 6961527.50 | L5