## BoQ1
Government eProcurement System Created By: Naresh Kumar Created Date/Time: 28-Aug-2026 04:39 PM Tender Title: Shifting of CCRs to New Substation at New ATC Tower at Dibrugarh Airport Tender ID: 2026_AAI_285354_2
Tender Inviting Authority: Sr. Manager (E-E), AAI, Dibrugarh Airport
Name of Work: Shifting of CCR's to New Substation a at New ATC Tower at Dibrugarh Airport
Contract No: 2026_AAI_285354_2
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | NASU SYSTEMS (GSTN-27ABAPS2566G1ZK) BID ID -1055455 |  | DOSHI ELECTRIC ENGG. CO. (GSTN-24AAEFD3355K1ZI) BID ID -1057491 |  | REWINDER TECHNO ELECTRICALS (GSTN-18AAFFR7457K1ZL) BID ID -1058639 |  | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED (GSTN-NA) BID ID -1059403
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Supply,installation, testing and Commissioning of 30 kW capacity Indoor Type Air Cooled Constant Current Regulator (CCR) of Micro Processor Controlled, Thyristor Type ((static type) suitable for operation on 2-phase 415V AC + PE ± 10%, 50 Hz input AC supply with 5 steps variation of current output as per ICAO and able to communicate with PC or PLC controlled system with digital output ammeter (0-20 Amps), over current, over voltage, open circuit and earth fault protection and earth leakage meter, two stage earth leakage detector, positive back indication equipments, hours run counter, LCD display complete as required and confirm to specifications enclosed and suitable for operation on the existing Airfield Lighting Control and Monitoring System (ALCMS) with communication, local and remote control and monitoring even and data recording and history keeping etc complete as required. Note - The above CCR should be compliance with ICAO Aerodrome design Manaul part5,IEC61822 & faa ac 150/5345-10,L829 | 3.00 | Each | 0.00 | 470000.00 | 1410000.00 | 540000.00 | 1620000.00 | 350000.00 | 1050000.00 | 511175.00 | 1533525.00 | 1050000.00 | REWINDER TECHNO ELECTRICALS
2.00 | Supply,installation, testing and Commissioning of 20 kW capacity Indoor Type Air Cooled Constant Current Regulator (CCR) of Micro Processor Controlled , Thyristor Type ((static type) suitable for operation on 2-phase 415V AC + PE ± 10%, 52-100Amp. 50 Hz input AC supply with 5 steps (2.8,3.4,4.1,5.2&6.6) variation of current output as per ICAO and able to communicate with PC or PLC controlled system with digital output ammeter (0 to 6.6 Amps), over current, over voltage, open circuit and earth fault protection and earth leakage meter, two stage earth leakage detector, positive back indication equipments, hours run counter, LCD display complete as required and confirm to specifications enclosed and suitable for operation on the existing Airfield Lighting Control and Monitoring System (ALCMS) with communication, local and remote control and monitoring even and data recording and history keeping etc complete as required. Note - The above CCR should be compliance with ICAO Aerodrome design Manaul part5,IEC61822 & faa ac 150/5345-10,L829 | 2.00 | Each | 0.00 | 390000.00 | 780000.00 | 468000.00 | 936000.00 | 250000.00 | 500000.00 | 447925.00 | 895850.00 | 500000.00 | REWINDER TECHNO ELECTRICALS
3.00 | Supply of following size 5 KV grade Airfield Lighting Cable copper conductor XLPE insulated, PVC sheathed, unshielded, anti-termite and rodent treated, UG airfield lighting cable generally confirming to IS:7098 (Part-I) with up to date amendments and particular specifications of the following sizes as required:
3.10 | 2C X 6sqmm | 2500.00 | Meter | 0.00 | 316.00 | 790000.00 | 370.00 | 925000.00 | 450.00 | 1125000.00 | 266.00 | 665000.00 | 665000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
3.20 | 2C X16sqmm | 2430.00 | Meter | 0.00 | 719.00 | 1747170.00 | 765.00 | 1858950.00 | 800.00 | 1944000.00 | 683.00 | 1659690.00 | 1659690.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
3.30 | 1C X 6sqmm | 2500.00 | Meter | 0.00 | 147.00 | 367500.00 | 175.00 | 437500.00 | 200.00 | 500000.00 | 130.00 | 325000.00 | 325000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
3.40 | 1C X 16sqmm | 2500.00 | Meter | 0.00 | 377.00 | 942500.00 | 370.00 | 925000.00 | 450.00 | 1125000.00 | 322.00 | 805000.00 | 805000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
4.00 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable of 5 KV/1.1KV grade of following size in the existing RCC/HUME/STONE WARE/METAL/DWC-HDPE pipe as required. Above 35 sq. mm and upto 95 sq. mm | 170.00 | Meter | 0.00 | 52.00 | 8840.00 | 54.00 | 9180.00 | 10.00 | 1700.00 | 58.00 | 9860.00 | 1700.00 | REWINDER TECHNO ELECTRICALS
5.00 | Laying of one number PVC insulated and PVC sheathed/ XLPE power cable of 5 KV/1.1KV grade of following size in the existing RCC/HUME/STONE WARE/METAL/DWC-HDPE pipe as required. upto 35 sqmm | 7500.00 | Meter | 0.00 | 33.00 | 247500.00 | 30.00 | 225000.00 | 10.00 | 75000.00 | 10.00 | 75000.00 | 75000.00 | REWINDER TECHNO ELECTRICALS, YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
6.00 | Laying of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV/5 KVgrade of following size in the existing masonry open duct as required. upto 35 sqmm | 1500.00 | Meter | 0.00 | 26.00 | 39000.00 | 40.00 | 60000.00 | 10.00 | 15000.00 | 10.00 | 15000.00 | 15000.00 | REWINDER TECHNO ELECTRICALS, YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
7.00 | Laying and fixing of one number PVC insulated and PVC sheathed / XLPE power cable of 1.1 KV/5kV grade of following size on cable tray/surface as required. upto 35 sqmm | 500.00 | Meter | 0.00 | 47.00 | 23500.00 | 75.00 | 37500.00 | 10.00 | 5000.00 | 10.00 | 5000.00 | 5000.00 | REWINDER TECHNO ELECTRICALS, YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
8.00 | Earthing with G.I. earth plate 600 mm x 600 mm x 6 mm thick including accessories and providing masonry enclosure with cover plate having locking arrangement and watering pipe of 2.7 metre long etc. with charcoal/coke and salt as required. | 8.00 | Set | 0.00 | 5500.00 | 44000.00 | 6750.00 | 54000.00 | 5000.00 | 40000.00 | 10350.00 | 82800.00 | 40000.00 | REWINDER TECHNO ELECTRICALS
9.00 | Providing and fixing 25mm x 5mm G.I. strip in 40mm dia G.I. pipe from earth electrode including connection with G.I. nut, bolt, stpring washer excavation and re-filling etc. as required. | 50.00 | Meter | 0.00 | 250.00 | 12500.00 | 450.00 | 22500.00 | 500.00 | 25000.00 | 725.00 | 36250.00 | 12500.00 | NASU SYSTEMS
10.00 | Providing & fixing 25 mm x 5 mm G.I. strip on surface or in recess for connections etc. as required. | 112.00 | Meter | 0.00 | 200.00 | 22400.00 | 150.00 | 16800.00 | 200.00 | 22400.00 | 253.00 | 28336.00 | 16800.00 | DOSHI ELECTRIC ENGG. CO.
11.00 | Supplying and laying 25 mm x 5 mm G.I. strip at 0.50 meter below ground as strip electrode, including connection / terminating with G.I. nut, bolt, spring washer etc. as required. (joining shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50 mm) | 18.00 | Meter | 0.00 | 190.00 | 3420.00 | 175.00 | 3150.00 | 200.00 | 3600.00 | 322.00 | 5796.00 | 3150.00 | DOSHI ELECTRIC ENGG. CO.
12.00 | Supply of following size 5 KV grade dry type Plug and Receptacle of type I, class 'B' primary connector kit with field attachment and suitable for 5 KV grade single core copper conductor, copper braided, XLPE insulated PE outer sheathed shielded cable, complete as required confirming to the technical specification.
12.10 | 16 sqmm | 70.00 | Set | 0.00 | 780.00 | 54600.00 | 585.00 | 40950.00 | 600.00 | 42000.00 | 690.00 | 48300.00 | 40950.00 | DOSHI ELECTRIC ENGG. CO.
12.20 | 6 sqmm | 70.00 | Set | 0.00 | 780.00 | 54600.00 | 585.00 | 40950.00 | 550.00 | 38500.00 | 633.00 | 44310.00 | 38500.00 | REWINDER TECHNO ELECTRICALS
13.00 | Making field connections by crimping of 6/16 sq.mm plug & receptacle with suitable existing size single core PVC cu. Conductor cable of 5 KV grade Airfield cable including filling the gap with water sealant material applying PVC insulation tape etc. complete as required. | 140.00 | Job | 0.00 | 40.00 | 5600.00 | 225.00 | 31500.00 | 50.00 | 7000.00 | 100.00 | 14000.00 | 5600.00 | NASU SYSTEMS
14.00 | Supplying and making end termination with brass compression gland and aluminium Ring type lugs for following size of PVC insulated and PVC sheathed / XLPE Copper conductor cable of 5 KV grade as required.
14.10 | 2C X 6 sqmm | 8.00 | Set | 0.00 | 240.00 | 1920.00 | 270.00 | 2160.00 | 100.00 | 800.00 | 316.00 | 2528.00 | 800.00 | REWINDER TECHNO ELECTRICALS
14.20 | 2C X 16 sqmm | 8.00 | Set | 0.00 | 240.00 | 1920.00 | 450.00 | 3600.00 | 100.00 | 800.00 | 423.00 | 3384.00 | 800.00 | REWINDER TECHNO ELECTRICALS
14.30 | 1C X 6 sqmm | 8.00 | Set | 0.00 | 240.00 | 1920.00 | 225.00 | 1800.00 | 100.00 | 800.00 | 311.00 | 2488.00 | 800.00 | REWINDER TECHNO ELECTRICALS
14.40 | 1C X 16 sqmm | 8.00 | Set | 0.00 | 240.00 | 1920.00 | 270.00 | 2160.00 | 100.00 | 800.00 | 416.00 | 3328.00 | 800.00 | REWINDER TECHNO ELECTRICALS
15.00 | Supplying and laying of following size DWC HDPEpipe ISI marked along with all accessories like socket,bend, couplers etc. conforming to IS 14930, Part II complete with fitting and cutting, jointing etc.direct in ground (75 cm below ground level) including excavation and refilling the trench but excluding sand cushioning and protective covering etc., complete as required. i. 63 mm dia (OD-63 mm & ID-51 mm nominal) | 2600.00 | Meter | 0.00 | 250.00 | 650000.00 | 200.00 | 520000.00 | 275.00 | 715000.00 | 110.00 | 286000.00 | 286000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
16.00 | Supplying and installaton following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with two numbers MS/GI Suspenders i/c base of suitable size MS/GI angle, bolts & nuts, painting suspenders, fastener etc as required. 4.1.1-100 mm width X 50 mm depth X 1.6 mm thickness | 110.00 | Meter | 0.00 | 375.00 | 41250.00 | 600.00 | 66000.00 | 800.00 | 88000.00 | 810.00 | 89100.00 | 41250.00 | NASU SYSTEMS
17.00 | Supply, Installation, Testing and Commissioning of ceiling fan with Brush Less Direct Current (BLDC) Motor BEE 5star rating, class of insulation: B, 3 nos. metal(Aluminium alloy) blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, steel/Al body. Power Factor not less than 0.9, Service Value (CM/M/W) minimum as below, 350 RPM (tolerance as per IS : 374-2019), THD (Total Harmonic Distortion) less than 10%, remote (preferably mobile app based) for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75 0C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase AC supply Ceiling Fan compliant to IS 374:2019 fan i/c external connections with 1.5 sq.mm FRLS/HFFR, PVC insulated copper conductor single core cableand earthing etc. as required. i. 1400mm, service value ≥ 6.0 CM/Min/Watt, air delivery 245 CM/Min (Minimum | 30.00 | Each | 0.00 | 2600.00 | 78000.00 | 3150.00 | 94500.00 | 4000.00 | 120000.00 | 3738.00 | 112140.00 | 78000.00 | NASU SYSTEMS
18.00 | Supply of following rating 5000V, 50 Hz Series Isolating Transformers encapsulated in polyester resin, finally moulded in neoprene type rubber and with primary and secondary connections suitable to be operated via ALCMS System confirming to specification as required suitable for above mentioned fittings for following applications and compatible to use on ALCMS 18.1.- 15W, 6.6/6.6A | 80.00 | Each | 0.00 | 2880.00 | 230400.00 | 3600.00 | 288000.00 | 3500.00 | 280000.00 | 2760.00 | 220800.00 | 220800.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
19.00 | Supplying and installing following size of perforated Hot Dipped Galvanised Iron cable tray (Galvanisation thickness not less than 50 microns) with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with two numbers GI Suspenders i/c base of suitable size GI angle, GI bolts & nuts, fastner etc as required. 4.1.4-300 mm width X 50 mm depth X 1.6 mm thickness | 100.00 | Meter | 0.00 | 500.00 | 50000.00 | 750.00 | 75000.00 | 1200.00 | 120000.00 | 1206.00 | 120600.00 | 50000.00 | NASU SYSTEMS
20.00 | Supply of 14 CX2.5sq.mm PVC insulated and FR PVC sheathed, copper conductor (solid bar Conductor ) industrial cable, 1100Volt, conforming to IS 694 with upto date amendments complete as required. | 2500.00 | Meter | 0.00 | 780.00 | 1950000.00 | 630.00 | 1575000.00 | 650.00 | 1625000.00 | 616.00 | 1540000.00 | 1540000.00 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED
21.00 | Providing and fixing 6 SWG G.I. wire etc.. complete as required. | 500.00 | Meter | 0.00 | 41.00 | 20500.00 | 15.00 | 7500.00 | 40.00 | 20000.00 | 31.00 | 15500.00 | 7500.00 | DOSHI ELECTRIC ENGG. CO.
22.00 | Supply and fixing of CPRI tested ISI marked Class A Electrical insulation mat having minimum thickness of 2 mm for working voltage upto 3.3kV confirming to IS 15652-2006, infront of LT panels as per direction of E-I-C. | 180.00 | sq.m | 0.00 | 70.00 | 12600.00 | 720.00 | 129600.00 | 900.00 | 162000.00 | 897.00 | 161460.00 | 12600.00 | NASU SYSTEMS
23.00 | Shifting of existing following various type rating and models Microprocessor Constatnt Current Regulators (CCR's) and H landing control desk from old CCR hall to New Substation ATS including dismantling,disconnection of cable and ALCMS control cables along with PLC Panel-01 , transportation, loading, unloading etc., as required .
23.10 | 30 Kw CCR ,415 volt, 50Hz, Input current 84.21 +_10% * output current - 20Amps) , Make - Nasu/Hirect | 3.00 | Job | 0.00 | 2000.00 | 6000.00 | 1800.00 | 5400.00 | 2000.00 | 6000.00 | 2500.00 | 7500.00 | 5400.00 | DOSHI ELECTRIC ENGG. CO.
23.20 | 20 Kw CCR ,415 volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps) , Make- Nasu | 3.00 | Job | 0.00 | 2000.00 | 6000.00 | 1600.00 | 4800.00 | 2000.00 | 6000.00 | 2500.00 | 7500.00 | 4800.00 | DOSHI ELECTRIC ENGG. CO.
23.30 | 15 Kw CCR ,415 volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps) Make- Nasu | 3.00 | Job | 0.00 | 2000.00 | 6000.00 | 1350.00 | 4050.00 | 2000.00 | 6000.00 | 2500.00 | 7500.00 | 4050.00 | DOSHI ELECTRIC ENGG. CO.
23.40 | 7.5 Kw CCR ,240volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps) Make- Nasu | 3.00 | Job | 0.00 | 2000.00 | 6000.00 | 1250.00 | 3750.00 | 2000.00 | 6000.00 | 2500.00 | 7500.00 | 3750.00 | DOSHI ELECTRIC ENGG. CO.
23.50 | 4.0 Kw CCR ,240volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps) Make- Nasu | 4.00 | Job | 0.00 | 2000.00 | 8000.00 | 1100.00 | 4400.00 | 2000.00 | 8000.00 | 2500.00 | 10000.00 | 4400.00 | DOSHI ELECTRIC ENGG. CO.
23.60 | 2.5 Kw CCR ,240volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps) Make- Nasu | 8.00 | Job | 0.00 | 2000.00 | 16000.00 | 1000.00 | 8000.00 | 2000.00 | 16000.00 | 2500.00 | 20000.00 | 8000.00 | DOSHI ELECTRIC ENGG. CO.
23.70 | H landing control desk -02 nos. | 2.00 | Job | 0.00 | 2000.00 | 4000.00 | 900.00 | 1800.00 | 2000.00 | 4000.00 | 2500.00 | 5000.00 | 1800.00 | DOSHI ELECTRIC ENGG. CO.
24.00 | Re-installation of following various type rating and models Constatnt Current Regulators (CCR's) and H landing control desk including Installation, testing and commissioning of CCRs & making ckts between Constant Current Regulators and Airfield Lighting Control and Monitoring System (ALCMS) alongwith Existing PLC Panel and shall be suitable working on AC Supply etc., as required as per direction of E-I-C and submission of testing parameters to AAI. Note:- ITC Report to be submiitted to Engineer Incharge.
24.10 | 30 Kw CCR ,415 volt, 50Hz, 84.21 +_10%/20Amps) Make- Nasu | 3.00 | Job | 0.00 | 2000.00 | 6000.00 | 2250.00 | 6750.00 | 2000.00 | 6000.00 | 4000.00 | 12000.00 | 6000.00 | NASU SYSTEMS, REWINDER TECHNO ELECTRICALS
24.20 | 20 Kw CCR ,415 volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps) , Make- Nasu | 3.00 | Job | 0.00 | 2000.00 | 6000.00 | 2000.00 | 6000.00 | 2000.00 | 6000.00 | 4000.00 | 12000.00 | 6000.00 | NASU SYSTEMS, DOSHI ELECTRIC ENGG. CO., REWINDER TECHNO ELECTRICALS
24.30 | 15 Kw CCR ,415 volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps) Make- Nasu | 3.00 | Job | 0.00 | 2000.00 | 6000.00 | 1800.00 | 5400.00 | 2000.00 | 6000.00 | 4000.00 | 12000.00 | 5400.00 | DOSHI ELECTRIC ENGG. CO.
24.40 | 7.5 Kw CCR ,415volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps) , Make- Nasu | 3.00 | Job | 0.00 | 2000.00 | 6000.00 | 1700.00 | 5100.00 | 2000.00 | 6000.00 | 4000.00 | 12000.00 | 5100.00 | DOSHI ELECTRIC ENGG. CO.
24.50 | 4.0 Kw CCR ,240volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps), Make- Nasu | 4.00 | Job | 0.00 | 2000.00 | 8000.00 | 1600.00 | 6400.00 | 2000.00 | 8000.00 | 4000.00 | 16000.00 | 6400.00 | DOSHI ELECTRIC ENGG. CO.
24.60 | 2.5 Kw CCR ,240volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps) , Make- Nasu | 8.00 | Job | 0.00 | 2000.00 | 16000.00 | 1450.00 | 11600.00 | 2000.00 | 16000.00 | 4000.00 | 32000.00 | 11600.00 | DOSHI ELECTRIC ENGG. CO.
24.70 | H landing control desk -02 nos. | 2.00 | Job | 0.00 | 2000.00 | 4000.00 | 900.00 | 1800.00 | 2000.00 | 4000.00 | 4000.00 | 8000.00 | 1800.00 | DOSHI ELECTRIC ENGG. CO.
25.00 | Shifting, reinstallation of the existing 01 no. ALCMS alongwith Existing PLC Panel from old power house to new Power house ATS Building including Modification in Airfield Lighting Control and Monitoring System (ALCMS)/ PLC Ckts, installtion, testing ,Commissioning of existing ALCMS & PLC Panel, making automatic & manaul ckts amoung the existing various ration of CCRS-26 Nos. through Copper Control wire and making parrallel connection with new ATC Airfield Lighting Control and Monitoring System (ALCMS) through fibre optic cable etc. etc., as required as per direction of E-I-C and submission of testing parameters to AAI. the following Ckts to incorporated with existing ALCMS & PLC Panel etc. as required. 1.30 Kw CCR ,415 volt, 50Hz, 84.21 +_10%/20Amps) -03 Nos. 2. 20 Kw CCR ,415 volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps) -03 Nos 3. 15 Kw CCR ,415 volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps) -03 Nos 4. 7.5 Kw CCR ,240volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps) -03 Nos 5. 4.0 Kw CCR ,240volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps) -04 Nos(Threshhold +end lights) 6. 2.5 Kw CCR ,240volt, 50Hz,2.8,3.4,4.1,5.2 &6.6 amps) -08 Nos 7. H landing control desk -02 nos. 8. Apron High Mast (HM)-11 Nos. 9. Beacon-01 no. 10. Crash Bell-01 No. 11. WTI- 02 Nos. 12. Guard Light-08 Nos. 13. Spares-04 Nos. Note:- ITC Report to be submiitted to Engineer Incharge. | 1.00 | Job | 0.00 | 30000.00 | 30000.00 | 200000.00 | 200000.00 | 15000.00 | 15000.00 | 172500.00 | 172500.00 | 15000.00 | REWINDER TECHNO ELECTRICALS
26.00 | Shifting and re-installation and commissioning of existing CCRs LT Panel to new ATS Power house including transportation from old CCR buiding to new ATS power house CCR Room ,determination of existing connected LT Power cable of the following: i. 3.5x 95 sqmm LT Cable de- termination-02 Set. Ii. 3.5c x 35 sq. mm LT Cablede- termination- 10 set Iii. 3.5c x 25 sq. mm LT Cablede- termination- 4 set etc. as comlete as required. Note:- ITC Report to be submiitted to Engineer Incharge. | 1.00 | Job | 0.00 | 10000.00 | 10000.00 | 15000.00 | 15000.00 | 10000.00 | 10000.00 | 30000.00 | 30000.00 | 10000.00 | NASU SYSTEMS, REWINDER TECHNO ELECTRICALS
27.00 | Shifting of existing 2 nos.x 120 KVA UPS to new ATS Power house CCR Building including transportation from old CCR buiding to new ATS power house CCR Room , disconnected the existing 3.5cx 95 ( 4 sets) and 3.5 c x 35 ( 04 sets) sq. mm sqmm LT cables etc. as comlete as required. Make- EATON | 1.00 | Job | 0.00 | 25000.00 | 25000.00 | 9000.00 | 9000.00 | 10000.00 | 10000.00 | 23000.00 | 23000.00 | 9000.00 | DOSHI ELECTRIC ENGG. CO.
28.00 | Installation, Testing and commissioning of existing 2 nos.x 120 KVA UPS in new ATS Power house CCR Building through OEM including end termination the 3.5cx 95 ( 4 sets) and 3.5 c x 35 ( 04 sets) sq. mm sqmm LT cables etc. as comlete as required. Note:- ITC Report to be submiitted to Engineer Incharge. | 1.00 | Job | 0.00 | 25000.00 | 25000.00 | 10000.00 | 10000.00 | 25000.00 | 25000.00 | 34500.00 | 34500.00 | 10000.00 | DOSHI ELECTRIC ENGG. CO.
29.00 | Shifting and re-installation and commissioning of existing 2 nos.x 1600 AH Battery bank sets for 2 nos.x 150 KVA UPS including transportation from CCR buiding to new ATS power house building , determination & end termination connection between UPS to battery bank etc. as comlete as required. Note:- ITC Report to be submiitted to Engineer Incharge. | 2.00 | Job | 0.00 | 15000.00 | 30000.00 | 10000.00 | 20000.00 | 15000.00 | 30000.00 | 34500.00 | 69000.00 | 20000.00 | DOSHI ELECTRIC ENGG. CO.
30.00 | Shifting , Installation, Testing and Commissioning of Control Desk of High Mast to New ATC Power house CCR room including disconnection of Control cable ckts of 10 Nos HM from control desk and existing ALCMS System/PLC and re connection of control ckts of HM with Control desk and connection with existing ALCMS installed in new ATS Power house building etc. compleate as required . | 1.00 | Job. | 0.00 | 5000.00 | 5000.00 | 8500.00 | 8500.00 | 20000.00 | 20000.00 | 115000.00 | 115000.00 | 5000.00 | NASU SYSTEMS
31.00 | Providing and fixing pre cast RCC Chamber of Size 120 X 120 X 100 cm inside and RCC top cover to covering chamber as per engineer incharge direction. | 5.00 | Job | 0.00 | 50000.00 | 250000.00 | 22500.00 | 112500.00 | 10000.00 | 50000.00 | 23000.00 | 115000.00 | 50000.00 | REWINDER TECHNO ELECTRICALS
| Total in Figures |  |  |  |  | 10072560.00 |  | 10459550.00 |  | 9916400.00 |  | 9534045.00
Lowest Amount Quoted BY: YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED(9534045.00)

## BOQ Summary
BOQ Summary Details Tender Title: Shifting of CCRs to New Substation at New ATC Tower at Dibrugarh Airport Tender ID: 2026_AAI_285354_2
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | YPR ENGINEERING AND SOLUTIONS PRIVATE LIMITED (BID ID -1059403) | 9534045.00 | L1
| 2 | REWINDER TECHNO ELECTRICALS (BID ID -1058639) | 9916400.00 | L2
| 3 | NASU SYSTEMS (BID ID -1055455) | 10072560.00 | L3
| 4 | DOSHI ELECTRIC ENGG. CO. (BID ID -1057491) | 10459550.00 | L4